## Volume 4.2.3
Contract title: Construction of the Building for Emergency Service in Novi Pazar Health Centre Location: Novi Pazar, Republic of Serbia TENDER REF.: EuropeAid/138746/ID/WKS/RS
VOLUME 4.2.3 –BREAKDOWN OF THE LUMP-SUM PRICE
Item | Technical Spec. Reference | Description | Unit | Firm Quantities | Unit price | Lump-sum price EUR
0 |  | GENERAL ITEMS
1 | N/A | Performance Bond | LS | 1 |  | 0
2 | N/A | Insurance of the Works | LS | 1 |  | 0
3 | N/A | Third party insurance | LS | 1 |  | 0
4 | 2.1.3 | Accomodation for Supervisor's staff as specified in the Technical Specification for fixed Site Office | LS | 1 |  | 0
5 | 2.1.3 | Services for the Supervisor's staff, incl. maintenance, cleaning, utility charges, etc. as specified in Technical Specification | LS | 1 |  | 0
6 | 1.8; 1.5; 1.8.1 | Preparation of a Quality Assurance Manual, EMP, TMP and H&S Plan, photo documentation | LS | 1 |  | 0
7 | 1.8.2; 1.9; 1.10 | Preparation and production of design for execution, detail design, As-built drawings and operating manuals. | LS | 1 |  | 0
8 | 2.1.2 | Preparation, Installation and Maintenance of site and visibility Signboards, comemmorative plaques | LS | 1 |  | 0
|  | TOTAL GENERAL ITEMS |  |  |  | 0
A |  | CONSTRUCTION AND CONSTRUCTION-CRAFT WORKS
I |  | EARTHWORKS
1 | 2.3.1 & 2.4.1.1 | Clearing the site, cutting the existing metal fence (about 120 m), marking the facility, implementation of bench marks, which will remain on the site until the technical acceptance of the building. | LS | 1 |  | 0
2 | 2.5.1 | Removal of the surface layer - topsoil d=20 cm in the bulk excavation using heavy machinery, and transport to the construction site landfill. Calculation per m² of removed topsoil in undisturbed condition. | m² | 1106 |  | 0
3 | 2.4.1.2 | Breaking the existing asphalt on a part of the newly designed facility mechanically, with loading into a vehicle and transport to the city landfill. Calculation per m² of the excavation. | m² | 40 |  | 0
4 | 2.5.2 & 2.5.4 & 2.5.6 | Bulk excavation of III category soil. Excavated material shall be loaded onto a vehicle and transported to the landfill. The quantity is calculated per m³ of the undisturbed soil. | m³ | 1840 |  | 0
5 | 2.5.2 & 2.5.4 & 2.5.6 | Excavation for the foundation slab of the elevator pit and foundations of the retaining wall outside the building, with loading onto a vehicle and transport to the city landfill. The quantity is calculated per m³ of the undisturbed soil. | m³ | 12 |  | 0
6 | 2.8.1 | Subsoil compaction after the excavation for the foundation slab of the building to the achieved compactness of min. Md=20 MPa, along with the compactness testing and issuing the test results by the authorized company. Calculation is done per m² of the compacted area. | m² | 810 |  | 0
7 | 2.9 | Supply and filling of the base layer of gravel under the foundation slab in a layer of 15 cm, along with compacting of the same layer using machinery to achieve the projected compactness of min. Md=30 MPa, of which a proof certificate should be provided. The quantity is calculated per m³ of the installed base in compacted condition. | m³ | 120 |  | 0
8 | 2.9 | Filling the base layer of gravel between the building and the surrounding area, after concreting the basement wall surfaces in layers of 30 cm each, with compacting of the same layer using machinery. The quantity is calculated per m³ of the installed base in compacted condition. | m³ | 232 |  | 0
|  | TOTAL: |  |  |  | 0
II |  | CONCRETE AND REINFORCED CONCRETE WORKS
Non-reinforced concrete
1 | 2.11.1 | Concreting of the base under the foundation slab and foundation of the retaining wall of the ramp, over the base layer of gravel, with non-reinforced concrete MB-15, thickness 5 cm. Calculation per m² of the base. | m² | 1085 |  | 0
2 | 2.11.1 | Concreting of the part of the plateau and the sidewalks as well as the area beside the ramp, intended for passenger vehicles parking, thickness d=12 cm, different widths, using concrete MB30 in appropriate formwork with dilatations at length of 2,0 m, over previously prepared base layer, which is paid separately. Dilatations shall be filled with sand to a height of h=10 cm, and the remainder with bitumen. Calculation per m² of completed sidewalks and plateau. | m² | 210 |  | 0
Reinforced concrete
3 | 2.11.2 | Concreting of the reinforced concrete foundation slab of the building and strip foundations of the retaining walls by the ramp, d=40 cm, using the MB30 concrete in appropriate formwork. Calculation per m³ of the installed concrete. | m³ | 256 |  | 0
4 | 2.11.7 | Installation of the formwork and concreting of the reinforced concrete wall surfaces in the basement and of the elevator core d=25 cm, using the MB30 concrete in smooth formwork, all in accordance with design details. Calculation per m³ of installed concrete. | m³ | 110 |  | 0
5 | 2.11.5 | Installation of formwork and concreting of the reinforced concrete columns, using the MB-30 concrete in smooth formwork, all in accordance with design details. Calculation per m³ of completed columns. | m³ | 40 |  | 0
6 | 2.11.6 & 2.11.5 | Installation of formwork and concreting of the reinforced beams, girders, door and window lintels of the building structure, using the MB-30 concrete in smooth formwork, all in accordance with design details. Calculation per m³. | m³ | 125 |  | 0
7 | 2.11.3 | Installation of formwork and concreting of the reinforced concrete flat full plate floors of d=16 cm, using the MB-30 concrete in smooth formwork. Ensure to leave all the necessary openings for installation verticals and other penetrations through the plate floors. Calculation per m² of the completed plate. | m² | 990 |  | 0
8 | 2.11.4 | Concreting of reinforced concrete internal double-flight inclined staircase slabs, d=15 cm, using the MB-30 concrete in smooth formwork. Calculation per m² of the completed inclined staircase slab. | m² | 27.2 |  | 0
9 | 2.11.4 | Concreting of the stair flight risers and treads, dimensions 16/30 cm, using the MB-30 concrete in smooth formwork. Calculation per m of completed stair risers and stair treads. | m | 90 |  | 0
10 | 2.11.4 | Concreting of the reinforced concrete full ramp slab at the embankment, and partially in the formwork above the area intended for containers and generator (exit part of the ramp in length of approximately 12 m) d= 16 cm, using the MB-30 concrete in smooth formwork. Calculation per m² of completed slab. | m² | 42 |  | 0
11 | 2.11.6 | Installation of the formwork and concreting of the reinforced concrete roof cornice - eaves, height h=40 cm, thickness 10 cm, using the MB-30 concrete in smooth formwork. Calculation per m of the cornice. | m | 94 |  | 0
12 | 2.11.6 | Installation of the formwork and concreting of the reinforced concrete fence cornice - protective garage wall on the ground floor, height h=100 cm, thickness 12 cm, reinforced using 2xQ-257, MB-30 concrete in smooth formwork. Calculation per m of the completed described item. | m | 24 |  | 0
13 | 2.11.4 | Installation of formwork and concreting of the reinforced concrete planter boxes in the entry canopy using concrete d=10 cm, reinforced with 2xQ-257 - which is included in the item price, using the MB-30 concrete in smooth formwork. Dimensions of the planter boxes are 60x270x60 cm. Calculation per peace of the complete described item. | pcs | 7 |  | 0
14 | 2.11.3 | Supply of material and work on the improvement of the ramp for vehicle entry to the intended parking lot on the ground floor, which will beformed so as to allow the unobstructed entry to and exit from the parking spaces. The ramp shall be made of interlocking concrete blocks of smaller dimensions, which provide warping of the surface on the well rolled base layer with filling gaps with sand. Price shall include the supply of the required number of kerbs. All complete listed above is paid per m² of the constructed ramp. | m² | 170 |  | 0
15 | 2.11.0 | Supply of material and construction of the "island" - the lawn area in front of the entrance ramp, which consists of kerbs that are circumferentially placed in a layer of concrete and filled with soil and humus. Price shall include seeding and planting evergreen undergrowth - a total of 10 pieces by choice of the Supervisor. All complete listed above is paid per m² of the constructed ramp. | m² | 38 |  | 0
|  | T O T A L: |  |  |  | 0
III |  | REINFORCEMENT WORKS
GENERAL DESCRIPTION
1 | 2.12 | Supply, cutting, bending, binding and positioning of the reinforcement RA 400/500 and Ga 240/360 in the building structure. Calculation per kg of the installed reinforcement. | kg | 41200 |  | 0
2 | 2.12 | Supply, preparation and installation of the wire-mesh reinforcement MA 500/600 in the building structure. Calculation per kg of the installed reinforcement. | kg | 19550 |  | 0
|  | TOTAL: |  |  |  | 0
IV |  | MASONRY AND BRICKLAYING WORKS
Brickwork
1 | 2.13.2 &2.13.3 | Construction of walls d=25 cm and 20 cm using hollow clay blocks MO-150 in cement lime mortar 1:2:6 with use of working scaffolds, which is included in the price. Calculation per m³ of completed walls. | m³ | 141 |  | 0
2 | 2.13.4 | Construction of partition walls d=12 cm using partition blocks d=12 cm in cement-lime mortar 1:2:6. Simultaneously build the necessary horizontal and vertical a/b ring beams with dimensions 12/25 cm.
Ring beams should be placed along the entire length of the wall at the height of the door lintel, made of concrete MB-20 and reinforced with +/-2 bars of 10 mm diameter with stirrups of 6 mm, at 20 cm in the necessary formwork.
|  | Connect walls with reinforced concrete walls or columns according to general description. Calculation per m² with ring beams. | m² | 93 |  | 0
3 | 2.13.4 | Construction of parapet bounding walls d=12 cm, 100 cm high, with construction of vertical ring beams, dimensions 12x20 cm at every 3.00 m and a final horizontal ring beam, dimensions 12x20 cm, using hollow clay bricks in cement mortar 1:3. Ring beams shall be reinforced with ±2f10 , stirrups f6 at 20 cm, which is included in the price of the wall and is not paid extra. Price shall include working scaffold, installation of reinforcement 2f10 and concrete with anchorage in columns and vertical ring beams of the structure. Calculation per m of completed wall as described above. | m | 86 |  | 0
Plastering works
4 | 2.13.5 | Plastering ceilings, walls, columns and beams with cement-lime mortar in the ratio 1:2:6, in two layers using the necessary working scaffold. Spray surfaces with lean cement mortar first. Openings up to 3.0 m² are not deducted. Calculation per m² of plastered surface as described above. | m² | 2960 |  | 0
Other masonry work
5 | 2.13.6 | Construction of a dip layer in sanitary blocks on the floor, using cement mortar, average thickness of 3-5 cm. Calculation per m² of the completed dip layer. | m² | 130 |  | 0
6 | 2.13.6 | Construction of cement screed in the rooms, average thickness d=5 cm, . On the outer edge to the wall, install the termo silent tape 100/5 mm. Insulation materials, extruded polystyrene panels with closed cells (XPS) and minimum compressive strength 300 kPa, and termo silent tape are paid separately. Reinforce the cement screed with wire lath Ø3,2 mm/5 cm in both directions. Calculation per m² of the fully completed works as described above. | m² | 540 |  | 0
7 | 2.13.6 | Construction of cement screed, average thickness d=4 cm, in the area where parking spaces are planned, as a dip layer, for vehicles, as well as on the passable part of the incoming road . Calculation per m² of the fully completed works as described above. | m² | 300 |  | 0
8 | 2.13.6 | Construction of cement screed, d=4 cm, lightly reinforced in the roof area, over the previously prepared thermal insulation made of mineral wool d=12 cm, which is paid separately. Reinforce the cement screed with wire lath Ø3,2 mm/5 cm in both directions. Calculation per m² of completed cement screed. | m² | 490 |  | 0
|  | TOTAL: |  |  |  | 0
V |  | CARPENTRY AND ROOFING WORKS
The roof structure
1 | 2.14.1 & 2.14.3 | Construction and installation of the wooden roof structure of dry fir timber II class, all according to the static calculation and drawings, with supply of the entire material, hardware and fire-resistant coating or coating against fungi and wormholes. Roof lathing and boarding is paid separately. Calculation per m² of the horizontal projection as measured by the outer edges of the roof. | m² | 430 |  | 0
2 | 2.14.1 & 2.14.3 | Roof boarding using boards 24 mm, up to 15 cm wide, made of dry fir timber as the roofing base. Board is class I. Place foil, which is included in the item price and shall not be separately paid, over the board formwork. Calculation per m² of the inclined surface of the installed board formwork. | m² | 480 |  | 0
3 | 2.14.1 & 2.14.3 | Roof lathing using fir wood double laths, dimensions 3x5 cm, placed on the pitch according to tile type. Join using E31/80 nails. All according to above described. Calculation per m² of the inclined surface. | m² | 480 |  | 0
4 | 2.15.1 &2.15.3 | Supply and installation of the roof covering, using roofing tiles from domestic production, including cutting. Calculation per m² of the inclined surface. | m² | 480 |  | 0
5 | 2.15.1 &2.15.2 | Supply and installation of booms on ridges and hips according to the type of the chosen tiles. Booms need to be placed in the dry, on the shackles, all according to manufacturer's specifications. Calculation per m of actual length of the installed booms. | m | 90 |  | 0
|  | TOTAL: |  |  |  | 0
VI |  | INSULATION WORKS
Waterproofing
1 | 2.16 | Waterproofing of basement floors and walls using penetrates over floor slab and wall surfaces on the inside. Penetrates shall be applied in three coats according to the manufacturer's specifications. Calculation per m² of complete penetrate coating as described above. | m² | 840 |  | 0
2 | 2.16 | Horizontal waterproofing on the ground floor, in the area intended for parking spaces for vehicles, as well as over the slab above the basement (between axes A and B - from axis 1 do axis 13), which consists of three penetrate coats, all in accordance with manufacturer's specifications. Calculation per m² of complete penetrate coating as described above. | m² | 240 |  | 0
3 | 2.16 | Horizontal flexible waterproofing in sanitary blocks and balconies, in three coats and two meshes (3+2) with prior coating of the rooms with cold bitulit coating. Also insulate floor coves at the height of 15 cm around the walls. Calculation per m² of complete flexible waterproofing as described above. | m² | 200 |  | 0
4 | 2.17 | Supply of material and thermal and sound insulation of floors under the cement screed, using insulation materials, extruded polystyrene panels with closed cells (XPS) and minimum compressive strength 300 kPa, d=4 cm and termo silent tape 100/5 mm, which is placed against the wall. The insulation materials, extruded polystyrene panels with closed cells (XPS) and minimum compressive strength 300 kPa, shall not be placed in floors intended for parking places for vehicles. Calculation per m² of installed thermal insulation. | m² | 650 |  | 0
5 | 2.17 | Thermal insulation of the last slab towards the roof space, at the top side, using stone wool d=12 cm and waterproof and vapor-permeable foil. Calculation per m² of executed thermal insulation. | m² | 400 |  | 0
6 | 2.17 | Thermal insulation in the basement floor using insulation materials, extruded polystyrene panels with closed cells (XPS) and minimum compressive strength 300 kPa, d=10 cm in rooms 2 to 9, and room 12. Calculation per m² of executed thermal insulation | m² | 180 |  | 0
7 | 2.17 | Thermal insulation of the slab floor on the bottom side above the basement, using styrofoam d=6 cm in rooms 13, 14 and 15, with coating of surface with two layers of adhesive and one layer of glass fiber mesh. Calculation per m² of executed thermal insulation. | m² | 170 |  | 0
8 | 2.17 | Thermal insulation of the slab floor on the bottom side above the basement, on the cantilevers and between axis A and axis B, and from axis 7 to axis 13, on the slab floor on the bottom side, above the ground floor, above the suspended ceiling, at the part where the balconies are located on the upper floor, which consists of hard pressed styrofoam d=22 cm. Calculation per m² of executed thermal insulation. | m² | 260 |  | 0
9 | 2.17 | Thermal insulation of the walls in the basement, rooms 6, 7 and 8 to the rooms 13 and 14, consisting of a layer of hard pressed styrofoam d=6 cm, over which two layers of adhesive and one layer of glass fiber mesh are applied. Calculation per m² of executed thermal insulation. | m² | 76 |  | 0
10 | 2.17 | Thermal insulation of the walls in the basement, room 9 towards the embankment, consisting of a layer of hard pressed styrofoam d=8 cm over which two layers of adhesive and one layer of glass fiber mesh are applied. Calculation per m² of executed thermal insulation. | m² | 76 |  | 0
|  | TOTAL: |  |  |  | 0
TOTAL A : | [5 empty] | 0
B |  | CONSTRUCTION-CRAFT WORKS
I |  | JOINERY WORKS
Aluminum joinery
1 | 2.18 | Fabrication, transport and installation of the glass entrance portal with thermal break in which the sliding double doors are installed, that opens to a motion sensor, with double-layer safety glazing 4+12+4 mm, filled with argon. Dry installation process is used, and opening according to the diagram. Prior to fabrication, the Contractor shall provide to the Supervisor with the workshop details. For a typical item, fabricate and install a test pattern first, with complete description. All according to the above description and diagrams in the project. Calculation per piece of the completed installation.
|  | - Basement(entrance and windscr.) dim 270x300cm | pcs | 2 |  | 0
|  | - Basement (offices 4 and 5 ) dim 200x300cm | pcs | 2 |  | 0
|  | - Ground floor (entrance) dim 370x320cm | pcs | 1 |  | 0
|  | - Ground floor (wind screen) dim 370x300cm | pcs | 1 |  | 0
|  | - Ground floor (offices 3 and 4) dim 200x300cm | pcs | 4 |  | 0
2 | 2.18 | Fabrication, transportation and installation of the front double glass door, made of aluminum profile with thermal break, power coated in white, with double-layer glazing 4+12+4 mm, filled with argon. Door is equipped with a lock with three keys. Dry installation process is used and the opening according to the diagram. Prior to fabrication, the Contractor shall provide to the Supervisor with workshop details. All according to the above description and diagrams in the project. Paid per piece of the complete installation.
|  | - entrance door - ground floor ramp dim 270 x 320cm | pcs | 1 |  | 0
|  | - entrance door - basement room 13 dim 270 x 300 cm | pcs | 1 |  | 0
3 | 2.18 | Fabrication, transportation and installation of the inner double glass door, made of aluminum profile without thermal break, power coated in white, with double-layer glazing 4+12+4 mm, filled with argon. Door is equipped with a lock with three keys. Dry installation process is used and the opening according to the diagram. Prior to fabrication, the Contractor shall provide to the Supervisor with workshop details. All according to the above description and diagrams in the project. Paid per piece of the complete installation.
|  | - inner door - basement (room 6) dim 220 x 300 | pcs | 1 |  | 0
|  | - inner door- basement (rooms 5 and 6) dim 270 x 300 | pcs | 2 |  | 0
|  | - inner door- floor (room 6) dim 180 x 240 | pcs | 1 |  | 0
4 | 2.18 | Fabrication, transport and installation of full garage door, made of aluminum profile with thermal break, partially power coated in white. The door is equipped with a remote control mechanism for opening, and can be lifted to the ceiling level. Door is equipped with a lock with three keys. Dry installation process is used, and opening according to the diagram. Prior to fabrication, the Contractor shall provide the Supervisor with workshop details. For each different item, fabricate and install a test pattern first, with complete description. Paid per piece according to the above description.
|  | - garage door dim 300x300cm | pcs | 5 |  | 0
5 | 2.18 | Supply and installation of glass balcony single door, made of aluminum profile with thermal break, power coated in white, with double layer glazing 4+16+4 mm filled with argon. Door is supplied with a lock with three keys. Dry installation is used, and opening according to the diagram. Calculation per piece according to the above description and diagrams in the project.
|  | - single balcony door dim 100 x 280cm | pcs | 2 |  | 0
6 | 2.18 | Supply and installation of glass balcony double door, made of aluminum profile with thermal break, power coated in white, with double layer glazing 4+16+4 mm filled with argon. Door is supplied with a lock with three keys. Dry installation is used, and opening according to the diagram. Paid per piece according to the above description and the diagrams in the project.
|  | - double balcony door dim 160 x 280cm | pcs | 1 |  | 0
7 | 2.18.3 | Supply and installation of fire door, constructed of steel sandwich plates with appropriate fire filling. Door frames are made of steel profiles. All finished with paint. Door must have a fire resistance of 60 min, which should be proved with relevant Test certificate. Calculation per piece according to the above description and diagrams in the project.
|  | - Fire door (basement) dim 100 x210 | pcs | 3 |  | 0
8 | 2.18 | Supply and installation of glass staircase portals on aluminum structure with built-in windows. Portals have double layer glazing 4+16+4 mm filled with argon. Calculation per piece according to the description and diagrams in the project.
|  | - staircase portal dim 320 x 580 | pcs | 1 |  | 0
|  | - staircase portal dim 320 x 680 | pcs | 1 |  | 0
9 | 2.18 | Installation of windows made of aluminum profiles with thermal break, power coated in white. Windows sealed with permanent elastic EPDM -ethylene propylene diene monomer (M-class)rubber, vulcanized on the corners. Plan strip curtains on the inside. Fittings are standard. Aluminum sills placed on window ledges, on the outside and inside, all in accordance with architectural details. Window sashes are glazed with thermo float glass d=4+16+4 mm filled with argon. Opening according to diagram. All complete according to the above description paid per piece of installed window.
|  | - window dim 80 x 100cm | pcs | 6 |  | 0
|  | - window dim 80 x 180cm | pcs | 1 |  | 0
|  | - window dim 50 x 220cm | pcs | 2 |  | 0
|  | - window dim 80 x 220cm | pcs | 3 |  | 0
|  | - window dim 160 x 180cm | pcs | 4 |  | 0
|  | - window dim 160 x 220cm | pcs | 5 |  | 0
|  | - window dim 240 x 180cm | pcs | 1 |  | 0
|  | - window dim 240 x 220cm | pcs | 2 |  | 0
|  | - window dim 320 x 180cm | pcs | 17 |  | 0
|  | - window dim 320 x 220cm | pcs | 8 |  | 0
10 | 2.18 | Supply and installation of interior doors without thermal break, made of multi chamber aluminum profiles in white. Doors are sealed permanently with elastic EPDM-ethylene propylene diene monomer (M-class)rubber, vulcanized on the corners. Fittings are standard. Door is equipped with a lock and a lock cylinder. Prior to fabrication, the Contractor shall provide the Supervisor with workshop details. For a typical item, fabricate and install a test pattern first with complete description. Paid per piece according to the above description.
|  | door dim 80/240 cm | pcs | 9 |  | 0
|  | door dim 90/240 cm | pcs | 11 |  | 0
|  | door dim 90/300 cm | pcs | 5 |  | 0
|  | door dim 100/240 cm | pcs | 4 |  | 0
|  | door dim 100/300 cm | pcs | 8 |  | 0
11 | 2.8.4 | Supply and installation of the interior wooden attic cover for exit to the attic which is equipped with folding ladder. Paid per piece according to the above description.
|  | dimensions dim 80/120 cm | pcs | 1 |  | 0
12 | 2.18 | roof window dim 120x90 | pcs | 2 |  | 0
Other joinery
13 | 2.19 | Fabrication and installation of horizontal and oblique staircase railing on the stair flight and ramp for transport of patients to the general hospital, whose supporting elements are made of box-shaped steel profiles 40/40 mm, anchored in the concrete base-staircase, and the joint is covered by protective caps-rosettes, all in accordance with the joinery diagram. Horizontals are made of box-shaped steel profiles 40/40 mm, welded together create a frame. The frame filling of steel profiles 20/40 mm at a distance of 15 cm, anchored in the concrete base, all according to the joinery diagram. Handrail is made of box-shaped steel profile 40/40 mm, all according to the project diagram.
|  | All metal parts need to be double coated with read lead coating at the workshop and painted with synthetic paint in the color chosen by the Beneficiary. The height of the railing is 110 cm. Calculation per m of complete work. The contractor shall ensure stable connection with the construction. Measures shall be checked on the spot. | m | 80 |  | 0
14 | 2.19 | Fabrication and installation of handrails on the staircase wall, whose permanent structures are made of box-shaped steel profiles Ø 50 mm, anchored in the wall. All metal parts need to be coated with read lead coating at the workshop, and painted with synthetic paint in the color chosen by the Beneficiary. Calculation per m of installed handrail. Measures shall be checked on the spot. | m | 30 |  | 0
15 | 2.19 | Fabrication and installation of coconut fiber door mat. Install into the L profile frame, anchored in concrete. The metal parts need to be protected against corrosion and painted with oil paint. Calculation per piece of coconut fiber door mat together with the frame.
|  | 100/150 cm | pcs. | 3 |  | 0
16 | 2.19 | Fabrication and installation of metal fence for the area intended for storage of oxygen cylinders and generator station, 120 cm high, made of metal profiles and elastic fibre wire with the installation of gates made of the same material, with locks equipped for locking. | m² | 14 |  | 0
17 | 2.19.2 | Fabrication and installation of metal floor mat for shoes at the building entrances. The mat frame is made of "L" profile 50/50/5 mm and installed in the base, encased in concrete. The mat itself is made of "L" profile 55/55/5 mm with hoop iron filling 45/5 mm at a distance of 2,5 cm. Dimensions of the mat are 50x270 cm.
All visible parts of the mat are protected against corrosion by hot-dip galvanizing. Calculation per piece of completely finished, installed and painted mat.
|  | size 50/270cm | pcs | 3 |  | 0
|  | TOTAL: |  |  |  | 0
II |  | SHEET METAL WORKS
1 | 2.20.2 | Supply, transport and installation of hidden horizontal gutters in the roof, made of galvanized plasticized steel, thickness d=0,60 mm) with providing necessary falls, which need to be made of cement screed of average thickness d=3 cm before placing the sheet metal. RS of the sheet metal is 100 cm. Sheet metal joints on divider to be executed by lacing. Calculation per m of installed horizontal gutters, all according to the description above and project details. | m | 130 |  | 0
2 | 2.20.1 | Supply, transport and installation of rainwater downpipes ø120 mm, made of galvanized steel sheet, plasticized on both sides, color RAL - 3009, thickness d=0.50 mm, with all necessary material (kettles, holding down clips, knees). Calculation per m. | m | 98 |  | 0
3 | 2.20 | Valley flashing using flat steel, hot-dip galvanized, plasticized sheet metal, 0.50 mm, color brown, r.s. 50 cm. Calculation per m of flashed valleys, completely finished. | m | 30 |  | 0
4 | 2.20 | Supply of materials and fabrication of metal ties and wind strips made of plasticized galvanized sheet metal on the gable end of the roof and the joint of the roof and the gable wall R.S. 50 cm. Calculation per m. | m | 40 |  | 0
5 | 2.19.3 | Fabrication of snow guards on the building roof, type according to tile, of steel, hot-dip galvanized, plasticized sheet metal d=0.6 mm, color brown. Snow guards to be fabricated according to Supervisor's details, and placed alternately in two rows "zig-zag". Calculation per m of installed snow guards. | pcs | 400 |  | 0
6 | 2.20 | Supply, transport and installation of vertical hanging gutters, diameter f100 mm, made of steel galvanized sheet, plasticized on both sides, thickness d=0.50 mm, with all accompanying elements made of the same material (hooks, kettles, outer and inner curve, ends of the vertical gutter to sidewalks). Place gutter horizontals at the edge of the roof overhang for vehicles in the ground floor. Calculation per m of installed gutters, all according to the above description and project details. | m | 41 |  | 0
|  | TOTAL: |  |  |  | 0
III |  | EXTERNAL PLASTERING WORKS
GENERAL DESCRIPTION
All external plastering works must be executed professionally and must be of good quality, and fully according to the technical description, preliminary costs and consultation with the Supervisor, and in accordance with the general description for external plastering works.
Materials used for the facade must possess quality Test certificates for the purpose for which they are used.
1 | 2.13.7 | Fabrication of the thermal facade made of stone wool, with properties: density KRT F-130 kg/m³, thickness 10 cm, with the necessary facade scaffold, as follows: - stone wool density KRT F-130kg/m³ d=10cm , the two component adhesive for bonding and plastering - Silicate mesh min 160gr/m², the two component adhesive for bonding and plastering around openings, intensified - initial AL strip, and in all corners PVC strips - metal screw anchors, type, length min. 18 cm - base in the same color as the facade - final facade, type - silicate, decorative (scratched) plaster d=2mm Installation of AL--initial strip d=10cm, then stone wool d=10cm is bonded to patellas, and vacuum on the edges, exclusively using special adhesive for stone wool (14-16 kg per 1 m of stone wool). After 48h of adhesion, the stone wool is anchored with steel screw anchors (8 anchors per 1 m²). Over the attached stone wool, apply a layer of stone wool adhesive in the thickness of 2-3 mm, and after the adhesive has dried (min 6h), immerse the fiber glass mesh with overlap of 10 cm on a newly set adhesive. All horizontal and vertical edges around the opening and contour edges shall be processed using staff angles with plaster lath. External plastering works shall be executed fully in accordance with instructions of the manufacturer of stone wool and orders of the Supervisor. Calculation per m² of completed facade, all according to norms for this type of work.
|  |  | m² | 690 |  | 0
2 | 2.13.7 | Processing of plinth and visible walls of the basement, same as description for previous item 1, except that instead of the scratched facade, acrylic render made of multi-coloured marble granulate in color chosen by the ordering party is used for final finishing. All complete, processing of the finished plinth and walls according to the above description is calculated per m² of the processed plinth and wall. | m² | 230 |  | 0
3 | 2.13.7 | Fabrication of facade of reinforced concrete self-supporting columns of the canopy at the entrance area, consisting of two layers of adhesive, one layer of embedded glass fiber mesh and the finishing layer of acrylic render made of multi-coloured marble granulate in tone and color chosen by the Investor. Calculation per m of processed columns as per the above description. | m | 36 |  | 0
4 | 2.13.7 | Fabrication of facade on parapet walls of the balconies, cornices and ceilings above the balcony (ceiling above the second floor), consisting of a layer of styrofoam d=3 cm, two layers of adhesive, one layer of glass fiber mesh and finishing treatment with acrylic render made of multi-coloured marble granulate in tone and color chosen by the Investor. Calculation per m² of completed facade according to the above description. | m² | 198 |  | 0
5 | 2.13.7 | Supply of material and installation of marble slabs d=3 cm, width up to 35 cm on the layer of adhesive as the ending of parapet bounding walls of balconies and roof cornice. Ensure to cut the drip channel at the bottom. Calculation per m. | m | 220 |  | 0
|  | TOTAL: |  |  |  | 0
IV |  | CERAMIC WORKS
1 | 2.21 | Floor covering with granite, anti-slip ceramic tiles, class A, dimensions and colors chosen by the Supervisor and Investor. Covering is executed by laying tiles on adhesive to the already prepared cement screed. Calculation per m² of the covered floor surface, complete with pointing. Basement (rooms 2, 3, 8, 13, 14, 15), ground floor (rooms 2, 3, 9, 13), floor (rooms 2, 7, 11a, 11b). Calculation per m² of floor. | m² | 460 |  | 0
2 | 2.21 | Supply of material and laying of granite ceramic tiles on a layer of adhesive along the perimeter of rooms as plinth, height h=10 cm. Calculation per m of plinth. | m | 300 |  | 0
3 | 2.21 | Covering of interior staircase, stair riser, stair tread, stair landing, with granite anti-slip ceramic tiles of extra quality, dimensions and colors chosen by the Supervisor. Covering is done by laying tiles in a layer of cement mortar, joint on joint, place AL coving strips at the joining of the riser and the tread, which is included in the price of the ceramics. Execute skirting along the periphery, using the same tile, height h=10 cm on adhesive layer. All listed above is paid per m² of the actual area of installed marble. | m² | 50 |  | 0
4 | 2.21 | Covering the wall surfaces in sanitary facilities and in rooms, around sinks, dimension 1.6x2.0, with ceramic wall tiles, class A, colors chosen by the Supervisor. Prior to starting the coating works, wall surfaces need to be plastered with cement mortar. Tiles are laid on the adhesive, and laid joint on joint. Upon completion of the laying of tiles, perform rejointing using the waterproof joint. The covering height in the sanitary facilities is 260 cm. Calculation per m² of the covered wall surfaces, complete with preparation of walls, which are being covered, and rejointing. | m² | 160 |  | 0
|  | TOTAL: |  |  |  | 0
V |  | FLOORING
1 | 2.22 | Floor covering with PVC floor covering - homogenised and wear-resistant, slip and abrasion, to the already prepared surface, using levelling compound, thickness 0.5 cm, resistant to wear and tear, slipping and abrasion. Must possess a fire Test certificate. Floor covering is antistatic.
|  | PVC covering needs to be bonded to the surface with the appropriate adhesive and welded on joints, all according to the instructions of the floor manufacturer. Design and color chosen by the Supervisor. Lay PVC skirting, 12 cm high, alongside walls. Calculation per m² of completed floor covering, PVC skirting included in the price and will not be calculated separately, as well as the preparation of surface with acrylic render made of levelling compound. Basement (rooms 4 to 7 and 8), ground floor (rooms 4 to 8 and 10), floor (rooms 3 to 6 and 8).Calculation per m² of floor. | m² | 500 |  | 0
2 | 2.22.4 | Supply of material and processing of floors in the area where vehicle parking spots are foreseen (basement, room 16, ground floor, room 16, access ramp 1) with liquid applied waterproofing system for non-slip and chemical-resistant , resistant to abrasion, resistant to wear and tear, all according to manufacturer's instructions.Calculation per m² of floor. | m² | 435 |  | 0
|  | TOTAL: |  |  |  | 0
VI |  | PAINTING AND DECORATING
1 | 2.23 | Skimming of plastered surfaces using skimming compound in two layers with all the necessary preparatory work (do not perform skimming and painting in the area where the ceilings are suspended). Process surfaces so that they are ready for the finishing coating. Calculation per m² of skimmed surface. | m² | 2890 |  | 0
2 | 2.23 | Finishing of interior surfaces with polikolor with previous coating of surfaces with base. Coating to be executed in three layers, in tone and color chosen by the Supervisor and the Investor. Calculation per m² of treated surface. | m² | 2480 |  | 0
3 | 2.23 | Processing of the hallway walls and doctors' offices with oil paint in two layers with the preparation of the surface, in the height of h=1.40 m. Calculation per m² as described above. | m² | 550 |  | 0
|  | TOTAL: |  |  |  | 0
VII |  | MISCELLANEOUS WORKS
1 | N/A | Fabrication and installation of aerators for ventilation of the attic area with the necessary flashings. Calculation per piece. | pcs | 6 |  | 0
2 | N/A | Supply and installation of stone wool d=5 cm in dilatations between two columns, between two beams and on the part of the reinforced concrete structure in entresol ceilings where plates are dilated. Stone wool coving strips are 30 cm wide. Calculation per m of installed stone wool in dilatations. | m | 16 |  | 0
3 | N/A | Supply and installation of AL-"L" profiles, thickness 4mm, for dilatation on the ceiling and wall of the basement. Calculation per m of installed profile with fixing to the wall and ceiling with F8 screw anchors. | m | 24 |  | 0
4 | N/A | Supply and installation of transitional brass and aluminum coving strips on transitions between two different types of floors, with installation of the same on the silicon. All complete paid per m of installed coving strip. | m | 36 |  | 0
5 | N/A | Supply and installation of wooden battens d=25 cm on the walls of the hallways, at the height h=60 cm from the finished floor. Paint battens with sandolin in color and protect with clear boat lacquer. Calculation per m of installed battens. | m | 200 |  | 0
6 | 2.24 | Supply of material and fabrication of suspended mineral ceilings in the basement (rooms 1 to 9 and 15), ground floor (rooms 2 to 10 and 13), which descend to a height of 320 cm from the floor level. The supporting structure is attached to A.B. slab structure and consists of aluminum joists, plasticized in white, arranged at 60 cm distance in both directions. All complete paid per m² of installed ceiling. | m² | 520 |  | 0
7 | N/A | Supply and installation of a hydraulic elevator for transport of patients, bearing power 1600 kg. speed 0.63 m/s ,3 floor, elevation 7960 mm.Lift car dimension 1500x2400x2200 mm. Drive system is with hanging-suspension, transmission index 2:1 .All according to the elevator design. | pcs | 1 |  | 0
8 | 2.26 | Supply and installation of the canopy structure in the ground floor, where open garages for vans are foreseen, and in the basement area by the ramp, where the passenger vehicle parking is foreseen, all according to the project and manufacturer's details. Standard steel construction (arches, 35-40 kg/m²). The cover is made of polycarbonate panels, 16 mm thick, UV stable, with antidust strips. | m2 | 288 |  | 0
|  | TOTAL: |  |  |  | 0
[5 empty] | TOTAL B : | 0
R E C A P I T U L A T I O N
A. CONSTRUCTION WORKS
I |  | EARTHWORKS ………………………………………………………………………… |  |  | 0 | 0
II |  | CONCRETE AND REINFORCED CONCRETE WORKS ………………… |  |  | 0 | 0
III |  | REINFORCMENT WORKS …………………………………………… |  |  | 0 | 0
IV |  | MASONRY AND BRICKLAYING WORKS …………………………………… |  |  | 0 | 0
V |  | CARPENTRY WORKS…………………………………………………… |  |  | 0 | 0
VI |  | INSULATION WORKS ………………………………………………… |  |  | 0 | 0
|  |  | TOTAL A EUR: |  | 0 | 0
B. CONSTRUCTION-CRAFT WORKS
I |  | JOINERY WORKS ……………………………………………………………………… |  |  | 0 | 0
II |  | SHEETMETAL WORKS…………………………………………………… |  |  | 0 | 0
III |  | EXTERNAL PLASTERING WORKS………………………… |  |  | 0 | 0
IV |  | CERAMIC WORKS……………………………………………………………………. |  |  | 0 | 0
V |  | FLOORING……………………………………………………………………. |  |  | 0 | 0
VI |  | PAINTING AND DECORATING…………………………………………… |  |  | 0 | 0
VII |  | MISCELLANIOUS WORKS…………………………………………… |  |  | 0 | 0
|  |  | TOTAL B EUR: |  | 0 | 0
|  |  | TOTAL A+B EUR: |  | 0 | 0
WATER SUPPLY AND SEWERAGE
EXTERNAL WORKS
WATER SUPPLY WATER RETICULATION - CONNECTION
I EARTHWORKS
1 | 2.6.2 & 3.2.1 | Excavation of the canal trench in III and IV category material, depth up to 2 m, for laying pipes, and construction of manholes, with possible pumping of water, discharge of excavated soil outside the trench, min. 1-2 m from the outer edge of the trench, with cutting of asphalt and concrete. All complete paid per m³ of excavation executed, possibly included in price is pumping of ground water and atmospheric water. | m³ | 62.4 |  | 0
2 | 2.8.1 &3.2.1 | Supply, transport and installation of fine river sand, below, above and around the pipes in a layer of 10+D+10 cm, and full trench profile. Paid per m³ of installed sand. | m³ | 18.6 |  | 0
3 | 2.9.1 &2.9.2 &3.2.1 | Backfilling of trench with coarse gravel-base in layers with thickness of 20-25 cm. Compact the first layer of 1.00 m above the upper edge of the pipe with compaction hammer, carefully, in order to prevent damage to the pipes. Compact the rest of the trench mechanically until a compactness of 150 kg/cm² is achieved. All complete paid per m³ of used material of the backfilled trench. | m³ | 40 |  | 0
4 | 2.5.6 & 3.2.1 | Loading of excess soil from the excavation, transport, with unloading, spreading and planning of the soil according to the configuration of the surrounding terrain, to the landfill determined by the Supervisor or the Beneficiary. Bulking coefficient of 1.25 has been adopted. All complete paid per m³ of transported soil. | m³ | 50 |  | 0
|  | TOTAL EARTHWORKS |  |  |  | 0
II CARPENTRY WORKS
1 | 2.14.4 | One-sided and two-sided timbering and planking and strutting of the canal trench with horizontal planks, d=5 cm, and vertical beams which are strutted with wooden or metal struts. All complete with labor and material paid per m² of developed area of timberwork. | m² | 10 |  | 0
|  | TOTAL CARPENTRY WORKS |  |  |  | 0
III INSTALLATION WORKS
1 | 3.2.4.4 & 3.1.1 | Supply, transport and installation of PE 80 water pipes NP10, with distribution along the trench, adjusting by direction and height, and fabrication of joints. Paid per m of executed water supply line.
|  | Ø110mm | m | 60 |  | 0
2 | 3.2.4.4 & 3.2.2 | Supply, transport and installation of cast iron fittings according to specification. Paid per kg of installed fittings with all the necessary jointing material. | kg | 300 |  | 0
3 | 3.2.4.4 & 3.2.2 | Supply, transport and installation of fiser half joint phi 80. Paid per piece of installed material with all the necessary labor. |  |  |  | 0
|  | Ø80mm | pcs | 2 |  | 0
4 | 3.2.4.4 & 3.2.2 | Supply, transport and installation of non-return valve, made of ductile cast iron NP10. Paid per piece of installed valve with all necessary installed material. |  |  |  | 0
|  | Ø80mm | pcs | 1 |  | 0
|  | TOTAL INSTALLATION WORKS |  |  |  | 0
IV OTHER WORKS
1 | 3.2.4.7 | Testing of the water network pipeline to the test pressure of 12 bar for 30 minutes. During the pressure testing, external pipeline must be partially backfilled, and nodes and valves fastened with concrete anchor blocks, and internal water supply installation network uncovered and uninsulated. During this time, there must be no drop in pressure in the part of the water supply network that is being tested. Only after the successful completion of the testing, thermal and other insulation of lines, closure of grooves and canals and backfilling of trenches can be executed. The contractor undertakes the network testing.Paid by m. | m | 60 |  | 0
2 | 3.2.4.7 & 3.2.4.8 | Cleaning and disinfection of the water supply network after the pressure testing and before commissioning. The Investor is obliged to perform this with the Institute for Health Protection.Paid by m . | m | 60 |  | 0
3 | 3.2.1 & 2.4.1.2 | Cutting of asphalt for the purpose of excavation due to the connection of the water supply network. Paid by m of cut asphalt. | m | 120 |  | 0
4 | 3.2.1 & 2.25 | Paving of the area with asphalt after executing the connection. Paid per m² of executed asphalt. | m² | 48 |  | 0
|  | TOTAL OTHER WORKS |  |  |  | 0
RECAPITULATION
I |  | EARTHWORKS |  |  |  | 0
II |  | CARPENTRY WORKS |  |  |  | 0
III |  | INSTALLATION WORKS |  |  |  | 0
IV |  | OTHER WORKS |  |  |  | 0
|  | TOTAL CONNECTION |  |  |  | 0
INTERIOR WORKS
A. WATER SUPPLY AND HYDRANT NETWORK
I EARTHWORKS
1 | 2.6.2 & 3.2.1 | Excavation of the canal trench in III and IV category material, depth up to 2 m, for laying pipes, and construction of manholes, with possible pumping of water, discharge of excavated soil outside the trench, min. 1-2 m from the outer edge of the trench, with cutting of asphalt and concrete. All complete paid per m³ of excavation executed, possibly included in price is pumping of ground water and atmospheric water. | m³ | 160 |  | 0
2 | 2.8.1 &3.2.1 | Supply, transport and installation of fine river sand, below, above and around the pipes in a layer of 10+D+10 cm, and full trench profile. Paid per m³ of installed sand. | m³ | 45 |  | 0
3 | 2.9.1 &2.9.2 &3.2.1 | Backfilling of trench with coarse gravel-base in layers with thickness of 20-25 cm. Compact the first layer of 1.00 m above the upper edge of the pipe with compaction hammer, carefully, in order to prevent damage to the pipes. Compact the rest of the trench mechanically until a compactness of 150 kg/cm² is achieved. All complete paid per m³ of used material of the backfilled trench. | m³ | 130 |  | 0
4 | 2.5.6 & 3.2.1 | Loading of excess soil from the excavation with transport to a distance of up to 3 km, with unloading, spreading and planning of the soil according to the configuration of the surrounding terrain, to the landfill determined by the Supervisor or the competent authority of the SO. Bulking coefficient of 1.25 has been adopted. All complete paid per m³ of transported soil. | m³ | 180 |  | 0
|  | TOTAL EARTHWORDS |  |  |  | 0
II CARPENTRY WORKS
| 2.14.4 | One-sided and two-sided timbering and planking and strutting of the canal trench with horizontal planks, d=5 cm, and vertical beams which are strutted with wooden and metal struts. All complete with labor and material paid per m² of developed area of the timberwork. | m² | 10 |  | 0
|  | TOTAL CARPENTRY WORKS |  |  |  | 0
III CONCRETE WORKS
1 | 2.11.3 & 2.11.7 &2.12 & 2.13.6 | Construction of water gauge station, according to the following description: Walls and bottom of the station are d=15 cm thick, made of MB20 concrete, with addition of the impermeability agent, reinforced with wire-mesh reinforcement 2xQ235, create an opening in the plate, diameter of 600 mm for entering the manhole. Install manhole cast irons below the opening, at a distance of 30 cm, and the gap of 15 cm. Plaster with cement mortar 1:3, with floating, all inner surfaces of the hole. Paid per piece of completed water gauge station, with all necessary material and labor. Internal dimensions of the water gauge station are: 300x300x280 cm.Paid per piece of completed water gauge station. | pcs | 1 |  | 0
2 | 2.11.1 | 2.Fabrication of concrete cubes and anchor blocks made of MB20 compacted concrete. Paid per m³ of installed concrete. | m³ | 1 |  | 0
|  | TOTAL CONCRETE WORKS |  |  |  | 0
IV INSTALLATION WORKS
1 | 3.2.4.4 & 3.1.1 | Supply, transport and installation of galvanized water supply pipes with addition of fittings, and jointing material (couplings, hemp, oil, etc.) with pipe and fitting protection, namely: - in the ground with two coats of hot bitumen and one jute winding or double winding of bituminous felt.- in the walls with double winding of felt strip - with creation of sound insulation in places of pipe penetration through the structure, at points where pipes touch the joints or other places where noise can arise from the movement of water in pipes. - with punching holes through the foundation, walls and other structural parts for passage of pipes, - with chase cutting of canals-grooves for installation of pipes in the walls, - with patching of the aforementioned holes, canals and grooves with cement mortar 1:3, - with fabrication of the supporting cantilevers, clips and hangers made of non-corrosive material or of material protected against corrosion, for fastening and suspension of pipes to the walls, ceilings and other structural parts. Paid per m of executed water supply network.
|  | Ø50mm | m | 38 |  | 0
|  | Ø65mm | m | 62 |  | 0
2 | 3.2.4.4 & 3.1.1 | Supply, transport and installation of the universal pipe polyethylene flex for drinking water installations in the protective pipe (with addition of fittings (covers, tees, couplings, joints, transitions, knees, connecting sockets, caps and other connecting material) in insulation and with holders). Polyethylene cross linked under high pressure (RAU-PE-Xa) according DVGW-work sheet W544, inliner according to DIN 16892 according to DIN EN ISO 15872 DVGW-registration number: DVGW DW-8501AU2200. DIN Certco registration: 3V257 PE-Xa/oxygen diffusion barrier according to DIN 4726. Color: silver RAL9006 (white aluminum). Building class: B2, normally flammable. Protective pipe: as a protection against condensation according to DIN 1988, part 2, and as mechanical protection of installation for connection of heaters, which require a certain insulation thickness. Material: polyethylene. Features: made according to DIN 49019. Color of protective layer: black. Paid per m of executed water supply network. |  |  |  | 0
|  | Ø16,2x2,6mm | m | 1200 |  | 0
|  | Ø20x2,8mm | m | 160 |  | 0
|  | Ø25x3,5mm | m | 30 |  | 0
|  | Ø32x4,4mm | m | 20 |  | 0
|  | Ø40x5,5mm | m | 20 |  | 0
|  | Ø50x6,9mm | m | 10 |  | 0
3 | 3.2.4.1 | Polyethylene distribution cabinets for wall installation (UP) made of galvanized steel sheets. Adjustable cabinet height (70 mm). Adjustable lower protective sheet metal fitted frame with adjustable front cover in depth of 110-160 mm, galvanized and with a coat of powder color RAL9010. Integrated front door with lock, with a layer of powder color. Special fabrication: polyamide cylindrical lock. Delivery form: packed in cardboard. Paid per installed piece. |  |  |  | 0
|  | Up-cabinet 110 tip3 | pcs | 1 |  | 0
|  | Up-cabinet 110 tip4 | pcs | 3 |  | 0
4 | 3.2.4.4 | Supply, transport and installation of PE 80 water supply pipes NP10, with distribution along the trench, adjustment by the direction and height and fabrication of joints. Paid per m of installed water supply line. |  |  |  | 0
|  | Ø110mm | m | 130 |  | 0
5 | 3.2.4.1 | Support, transport and installation of the thermal insulation, around pipes, where visibly placed. Paid per m of completed thermal insulation. |  |  |  | 0
|  | Ø32mm | m | 20 |  | 0
|  | Ø40mm | m | 20 |  | 0
|  | Ø50mm | m | 38 |  | 0
|  | Ø65mm | m | 62 |  | 0
6 | 3.2.4.2 | Supply, transport and installation of the union joint valve and all the necessary material. Paid per piece of the installed valve. |  |  |  | 0
|  | Ø3/4mm | pcs | 24 |  | 0
|  | Ø32mm | pcs | 8 |  | 0
|  | Ø40mm | pcs | 8 |  | 0
|  | Ø50mm | pcs | 4 |  | 0
|  | Ø65mm | pcs | 4 |  | 0
7 | 3.2.4.9 | Supply, transport and installation of slanted wall fire hydrants in metal cabinet, complete with wall installation, which includes: - skewed hydrant made of hard galvanized sheet metal, - joint clutch at the hydrant and hose - fire hose, length 15 m, diameter 50 mm, - nozzle with jet regulator, - fitting, knee, double nipples, union joint, etc. - standard metal box for equipment storage, painted with red oil paint, with mark "H" in white, - jointing material, etc. Paid per piece of installed hydrant, complete with labor and material, as described. | pcs | 6 |  | 0
8 | 3.2.4.2 | Supply, transport and installation of cast iron fittings, according to enclosed specification. Paid per kg of installed fitting, with all the necessary jointing material. | kg | 500 |  | 0
9 | 3.2.4.2 | Supply, transport and installation of flow meter - combined water gauge, complete.Paid per piece of installed water gauge with all the necessary labor and installed material. |  |  |  | 0
|  | Ø50-65mm | pcs | 1 |  | 0
|  | Ø80-100mm | pcs | 1 |  | 0
10 | 3.2.4.2 | Supply, transport and installation of non-return valve, made of ductile cast iron NP10. Paid per piece of installed valve with all the necessary installed material. |  |  |  | 0
|  | Ø80mm | pcs | 2 |  | 0
11 | 3.2.4.2 | Supply, transport and installation of cast iron manhole covers with frame. Paid per piece of installed cover with the necessary labor and installed material. |  |  |  | 0
|  | Ø625mm,25MP(250KN) without openings | pcs | 1 |  | 0
15 | 3.2.4.9 | Supply, transport and installation of free standing sheet metal cabinets with fire protection equipment for underground and above ground fire hydrants, complete installation, which includes: - two-door sheet metal cabinet, painted with red oil paint, with mark "H" in white, - four fire hoses, length 15m, - two nozzles, diameter 75mm, - free standing extension made of solid galvanized steel, - crescent wrench for opening above ground hydrants, - spanner wrench for opening underground hydrants, - distributor made of galvanized steel for extension of the hose in several directions, diameter 75mm, - MB20 concrete for the base. Paid per piece of the installed cabinet, all with labor and material, as described. |  |  |  | 0
|  | Cabinet size 1200x300x1200cm | pcs | 1 |  | 0
16 | 3.2.4.2 | Supply, transport and installation of underground and aboveground fire hydrants made of cast iron, for installation depth of 1.25 m. Paid per piece of completely installed hydrant. Ø80mm. | pcs | 4 |  | 0
17 | 3.2.4.2 | Supply, transport and installation of Polyethylene finishing batteries with enclosure. Paid per piece of completely installed material. | pcs | 60 |  | 0
18 | 3.2.4.10 | Supply, transport and installation of hydro station with a variable frequency drive (hydrovar) ro raise the pressure in the water supply network of the building (two pumps) height up to 15 m. Paid per piece of installed hydro station, complete, with all the necessary installation material and labor. | pcs | 1 |  | 0
|  | TOTAL INSTALLATION WORKS |  |  |  | 0
V OTHER WORKS
1 | 3.2.2. | Testing of the water network pipeline to the test pressure of 12 bar for 30 minutes. During the pressure testing, external pipeline must be partially backfilled, and nodes and valves fastened with concrete anchor blocks, and internal water supply installation network uncovered and uninsulated. During this time, there must be no drop in pressure in the part of the water supply network that is being tested. Only after the successful completion of the testing, thermal and other insulation of lines, closure of grooves and canals and backfilling of trenches can be executed. The contractor undertakes the network testing.Paid by m . | m | 1570 |  | 0
2 | 3.2.2. & 3.2.3 | Cleaning and disinfection of the water supply network after the pressure testing and before commissioning. The Investor is obliged to do this with the Institute for Health Protection.Paid by m . | m | 1570 |  | 0
|  | TOTAL OTHER WORKS |  |  |  | 0
RECAPITULATION
I |  | EARTHWORKS |  |  |  | 0
II |  | CARPENTRY WORKS |  |  |  | 0
III |  | CONCRETE WORKS |  |  |  | 0
IV |  | INSTALLATION WORKS |  |  |  | 0
V |  | OTHER WORKS |  |  |  | 0
|  | TOTAL WATER SUPPLY |  |  |  | 0
B. SANITARY AND STORM SEWER, DRAINAGE
I EARTHWORKS
1 | 2.6.2 & 3.2.1 | Excavation of the canal trench in III and IV category material, depth up to 2 m, for laying pipes, and construction of manholes, with possible lowering water level, with cutting of asphalt and concrete, as needed, with loading of excavated soil outside the trench, min. 1-2 m from the outer edge of the trench. All complete paid per m³ of the excavation executed, possibly included in the price is lowering of water level and prevention of inflow of rain water. | m³ | 180 |  | 0
2 | 2.6.2 & 3.2.1 | Excavation of the canal trench in III and IV category material, depth 2-4 m, for laying pipes, and construction of manholes, with possible pumping of water, with discharge of excavated soil outside the trench, min. 1-2 m from the outer edge of the trench. All complete paid per m³ of the excavation executed, possibly included in the price is lowering water level and pumping of the rain water. | m³ | 20 |  | 0
3 | 2.8.1 &3.2.1 | Supply, transport and installation of sand, below, above and around the pipes in a layer of 10+D+10 cm, and full trench profile. Paid per m³ of installed sand. | m³ | 40 |  | 0
4 | 2.9.1 &2.9.2 &3.2.1 | Backfilling of trench with coarse gravel-base in layers of thickness of 20-25 cm. Compact the first layer of 1.00 m above the upper edge of the pipe with compaction hammer, carefully, in order to prevent damage to the pipes. Compact the rest of the trench mechanically until a compactness of 150 kg/cm² is achieved. All complete paid per m³ of used material of the backfilled trench. | m³ | 60 |  | 0
5 | 2.9.1 &2.9.2 &3.2.1 | Backfilling of trench with coarse gravel-base in layers of thickness of 20-25 cm. Compact the first layer of 1.00 m above the upper edge of the pipe with compaction hammer, carefully, in order to prevent damage to the pipes. Compact the rest of the trench mechanically until a compactness of 150 kg/cm² is achieved. All complete paid per m³ of used material of the backfilled trench. | m³ | 20 |  | 0
6 | 2.5.6 & 3.2.1 | Loading of excess soil from the excavation with transport to a distance of up to 3 km, with unloading, spreading and planning of the land according to the configuration of the surrounding terrain, to the landfill determined by the Supervisor or the competent authority of the SO. Bulking coefficient of 1.25 has been adopted. All complete paid per m³ of transported soil. | m³ | 80 |  | 0
|  | TOTAL EARTHWORKS |  |  |  | 0
II CARPENTRY WORKS
1 | 2.14.4 | One-sided and two-sided timbering and planking and strutting of the canal trench with horizontal planks, d=5 cm, and vertical beams which are strutted with wooden and metal struts. All complete with labor and material paid per m² of developed area of the timberwork. | m² | 20 |  | 0
|  | TOTAL CARPENTRY WORKS |  |  |  | 0
III CONCRETE WORKS
1 | 2.11.3 & 2.11.7 &2.12 & 2.13.6 | Construction of inspection chambers using MB30 concrete, reinforced with wire-mesh reinforcement, in double-sided formwork or template. Chambers are circular, with inner diameter of 100 cm, and wall thickness d=15 cm. The final segment is conically arched to the diameter of 625 mm, at the height of 90 cm. When concreting the bottom of the chamber, the channel pipe should be shaped according to the pipe profile with grade in the flow direction of water and side slope of 1:3 from the top of the channel pipe in the direction of the chamber wall. The bottom and the channel pipe need to be constructed simultaneously in order to provide better monolithic bond and thus prevent penetration of ground water into the sewer network and vice versa. Manhole step irons should be installed on the walls, at a distance of 30 cm and gap of 15 cm. Concrete must be waterproof. Plaster the interior surfaces of the chamber with cement mortar in two layers with a total thickness of 2 cm. The first layer, thickness 1.5 cm, scale 1:2, and the second layer, thickness 0.5 cm, scale 1:1, with trowel finishing. Paid per m of the usable depth of the completed inspection chamber, including labor and material, including: formwork, reinforcement, mortar and step irons, as well as all consumables and installation material. | m | 16 |  | 0
2 | 2.11 | Construction of the lower slabs of drainage shaft, dimensions 140x140 m, thickness d=20 cm, using MB 20 concrete, all in accordance with the details given in the project and applicable technical regulations for this type of work. The unit price of the item includes all necessary labor and material. Calculation per piece. | pcs | 6 |  | 0
3 | 2.11 | Concreting of flute for the drainage pipe, using MB 20 concrete, all in accordance with the details provided in the design and regulations for this type of work. Concrete the bottom part first, thickness 10 cm, in decline towards the pipeline level. After laying the pipes, concrete the second part with incline towards the pipe. All the necessary labor and jointing and bonding material are included in the unit price of the item. Calculation per m³. | m³ | 10 |  | 0
|  | TOTAL CONCRETE WORKS |  |  |  | 0
IV INSTALLATION WORKS
1 | 3.1.2 & 3.2.4.4 | Supply, transport and installation of PVC sewer pipes, type Polyethylene , for domestic sewage, and for road sewage, with coupling and connecting with the rubber ring, fittings, and sealing rubber rings. Pipes are product of Polyethylene , as well as all the other necessary material.Execute installation of pipes which are laid in the ground, on the previously prepared bedding of fine river sand d=10 cm. Pipes in the ground shall be protected with a layer of river sand 10+D+10 cm and full profile of the trench. After completing the installation and testing of the constructed line for water retentivity, backfill the trench using the manual compaction hammer, in layers of 20 cm. Inside the facility, and above the ground, pipes shall be visibly installed, anchored and suspended on walls, ceilings and other parts of the building, with previous punching holes for the passage of pipes through plate floors, foundations, walls and other parts of the building. All complete with labor and material as described above, paid per m1 of executed sewerage network.
|  | Ø50mm HT | m | 80 |  | 0
|  | Ø70mm HT | m | 32 |  | 0
|  | Ø110mm HT | m | 300 |  | 0
|  | Ø125mm HT | m | 30 |  | 0
|  | Ø160mm HT | m | 240 |  | 0
2 | 3.1.2 & 3.2.4.4 | Supply, transport and installation of PVC vertical floor drains with toilet cover. Paid per installed piece. |  |  |  | 0
|  | Ø70mm | pcs | 24 |  | 0
|  | Ø100mm | pcs | 10 |  | 0
3 | 3.2.4.4 | Supply, transport and installation of PVC ventilation heads-caps, diameter of 100 mm, on ventilation sanitary verticals above the roof. Flash the penetration of verticals through the roof with galvanized sheet metal 0.55 mm, with sheet metal processing. Paid per piece of installed ventilation cap. | pcs | 2 |  | 0
4 | 3.2.4.4 | Supply, transport and installation of cast iron manhole covers with frame. Paid per piece of complete installed cover with necessary labor and installed material. |  |  |  | 0
|  | Ø625mm, 25MP (250KN) without openings | pcs | 5 |  | 0
5 | 3.2.4.4 | Supply, transport and installation of cast downspout. Paid per piece of complete installed downspout. | pcs | 14 |  | 0
|  | TOTAL INSTALLATION WORKS |  |  |  | 0
V OTHER WORKS
1 | 3.2.4.7 | Testing of the sewage network for water retentivity. During the water retentivity testing, the network must be partially covered. During this time, there must be no leakage in the part of the sewage network that is being tested. Only after the successful completion of the testing, closure of grooves and canals and backfilling of trenches can be executed. The contractor undertakes the network testing.Paid by m . | m | 682 |  | 0
|  | TOTAL OTHER WORKS |  |  |  | 0
RECAPITULATION
|  | I EARTHWORKS |  |  |  | 0
|  | II CARPENTRY WORKS |  |  |  | 0
|  | III CONCRETE WORSK |  |  |  | 0
|  | IV INSTALLATION WORKS |  |  |  | 0
|  | V OTHER WORKS |  |  |  | 0
|  | TOTAL SANITARY AND STORM SEWAGE |  |  |  | 0
C. SANITARY SUPPLIES AND EQUIPMENT
1 | 3.1.4 & 3.2.4.5.8 &3.2.4.6 | Supply, transport and installation of ceramic sinks-complete, which includes: - single-lever standing battery with movable spout and aerator at the mouth, - faience toilet bowl, size 56/42 cm, color chosen by the Investor, - faience stand, color chosen by the Investor, - metal holders for fastening the toilet bowl to the wall, with rubber pads, - nickel plated siphon with grating, diameter 32 mm, and nickel plated connecting pipe, - nickel plated towel and soap holders, - brushed wall mirror, size 50/30 cm, attached to the wall with brass screws with nickel plated caps, - ceramic shelf, - connecting material as needed. Paid per piece of complete installed sink, with all the necessary labor and material. | pcs | 30 |  | 0
2 | 3.1.4 & 3.2.4.5.8 &3.2.4.6 | Supply, transport and installation of two-part sinks made of pressed sheet metal, complete, which includes: -wall-mounted single lever battery with movable spout and aerator at the mouth, -nickel plated siphon with grating, nickel plated connecting pipe, diameter 32 mm, and nickel plated grease collector, -nickel plated towel and soap holders, -connecting material as needed. Paid per piece of completely installed sink with all the necessary labor and material. | pcs | 12 |  | 0
3 | 3.1.4 & 3.2.4.5.8 &3.2.4.6 | Supply, transport and installation of toilet bowl, complete, which includes: -noise-free cistern, - connection set for the toilet bowl, fastening material for the element (attaching to the floor), - funnel bowel made of sanitary ceramics, - plastic toilet seat, - nickel plated clothes holders and toilet paper holder, - connecting material as needed, - steel frame. Paid per piece of completely installed toilet with all the necessary material and labor. | pcs | 12 |  | 0
4 | 3.1.4 & 3.2.4.5 &3.2.4.6 | Supply, transport and installation of electric water heaters. Combined water heater possesses an inner sanitary water tank, according to tank-in-tank concept, and two heat exchangers with smooth pipes, resistant to lime. Sanitary water heater is protected against corrosion by the highest quality enamel DIN 4753. The built-in magnesium anodes offer additional protection against corrosion. Heating of solar collectors is done through the lower heat exchanger. If necessary, additional heating via water heater is done over the upper heat exchanger, integrated into the sanitary water heater. The water heater has more connecting options for increasing the temperature of the return heating line. The advantage in using the water heater is also that there is a possibility of combining it with solid fuel boiler. The boiler is insulated with ecological, CFC-free, PU insulation made of soft foam. - High level of comfort - Long life - Quick water heating with energy saving - High quality corrosion protection according to DIN 4753 - Additional solar heating by raising the return heating line - Very efficient transmission of solar heat - Suitable for collector surfaces of up to ca. 15 m² - High flexibility of connections - Connection forms suitable for installation - Possible additional heating through electric heaters of the high pressure water heater, complete. -Connecting material as needed. Paid per piece of complete installed water heater with all the necessary material and labor. |  |  |  | 0
|  | 500 L-1000L | pcs | 2 |  | 0
|  | TOTAL SANITARY SUPPLIES AND EQUIPMENT |  |  |  | 0
RECAPITULATION WATER SUPPLY AND SEWERAGE
A |  | WATER SUPPLY |  |  |  | 0
B |  | SANITARY AND STORM SEWER |  |  |  | 0
C |  | SANITARY SUPPLIES AND EQUIPMENT |  |  |  | 0
|  | TOTAL WATER SUPPLY AND SEWAGE |  |  |  | 0
A HIGH VOLTAGE ELECTRICAL INSTALLATIONS - Emergency ward
1. |  | DISTRIBUTION OF CABLE RACKS
1 | 4.1 & 4.2 & 4.4 | Supply and installation of perforated cable trays, lateral height of 60 mm for laying cables of electrical installations. Trays have bottom and side perforations and curved upper side.This item includes all necessary mounting equipment (ceiling mounts with brackets for standard installation, joints, branches, protective rings, etc.). . Calculation per m.
|  | 400x60 | m | 10 |  | 0
|  | 200x60 | m | 40 |  | 0
|  | 100x60 | m | 60 |  | 0
|  | 50X60 | m | 40 |  | 0
2 | 4.1 & 4.2 & 4.4 | Fire resins for coating and plugging between fire zones. Rack routes and cables are coated with these resins in a length of 1 m on both sides of the wall. Calculation per kg. | kg | 20 |  | 0
3 | 4.1 & 4.2 & 4.4 | Supply and installation of parapet cable distribution systems. The base of the parapet should be with one section for conducting electrical and telecommunication installations. Modular outlet elements are installed into the parapet. Item includes all the necessary material for setting up the distribution (partitions, cable holders, covers, corner elements). Calculation per m. | m | 20 |  | 0
|  | TOTAL |  |  |  | 0
2 |  | MAIN SUPPLY CABLES
1 | 4.1 & 4.2 & 4.4 | Supply and installation of main supply cables with connecting to both ends, type N2XH, of appropriate diameter and number of wires for the power supply of the distribution cabinets. Cables are laid along the perforated cable racks. Calculation per m. |  |  |  | 0
|  | N2XH 4x50mm² from MDC do ATS generator, and from ATS to MDC | m | 100 |  | 0
|  | N2XH-J 1x25mm² | m | 100 |  | 0
|  | N2XH-J 5x16mm²for power supply of the RTP and RT1 | m | 30
|  | N2XH-J 5x10mm² for power supply of the RTTS and RTS | m | 50
|  | N2XH-J 5x6mm² for power supply of the elevator and booster pump station. | m | 50
|  | TOTAL |  |  |  | 0
3 |  | DISTRIBUTION CABINETS
1 |  | MDC
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard tested for the equipment of following characteristics: dimensions up to WxHxD: 1000x2200x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Instal the following equipment in the cabinet: -1 pcs.three pole surge diverter, 500V -1 pcs.three pole low voltage break switch,250A. fixed,3P with power MX button 230V. rated current (voltage) ln=250 A, with extended drive and with chest pull. -2 pcs. three gang (protection) 3P C,230 V 50Hz, rated current (voltage) ln=63 A, breaking capacity 10 kA, with overcurrent shutter button (thermal and electromagnetic) -4 pcs.three gang (protection) 3P C,230 V 50Hz, rated current (voltage) ln=40 A, breaking capacity 10 kA, with overcurrent shutter button (thermal and electromagnetic) ; - 1 pcs. 5 A measuring group ; -3 pcs.current power reducer 200/5 A; -1 pcs. measuring box.; - 1pcs. GPRS device.; - Other fine material (copper bus bar,terminal,conductors,insulatos,pertinax board,lugs,screws, etc.) Calculation pre peace installed block. | pcs | 1 |  | 0
2 |  | RO-S |  |  |  | 0
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard tested for the equipment of following characteristics: dimensions up to WxHxD: 1000x2200x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Place a nameplate under each element. Install equipment in the cabinet the following equipment . -1 pcs. three polle main switches , current rating ln=40 A , two-position, 0-1, monting on the box door. -1 pcs. Four polle differential overload trip 40/0.3 A; -24 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; - 10 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 10 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) - Other fine material (copper bus bar,terminal,conductors,insulatos,pertinax board,lugs,screws, etc.) Calculation pre peace installed block. | pcs | 1 |  | 0
3 |  | RO-TS |  |  |  | 0
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard typically tested for the equipment with the following characteristics: dimensions up to WxHxD: 1000x2200x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Place a nameplate under each element. Install equipment in the cabinet the following equipment . -1 pcs. three polle main switches , current rating ln=40 A , two-position, 0-1, monting on the box door. --2 pcs. one polle (grebenasti) switches , current rating ln=10 A , two-position, 0-1, monting on the box door; -1 pcs.Four polle differential overload trip 40/0.3 A; - 24 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; -8 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; - Other fine material (copper bus bar, terminal, conductors, insulatos, pertinax board, lugs, screws, etc | pcs. | 1 |  | 0
4 |  | RO-P |  |  |  | 0
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard tested for the equipment of following characteristics: dimensions up to WxHxD: 1000x2200x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Place a sign under each element.Instal the following equipment in the cabinet: -1 pcs. three polle (grebenasti) switches , current rating ln=63 A , two-position, 0-1, monting on the box door. --4 pcs. one polle (grebenasti) switches , current rating ln=10 A , two-position, 0-1, monting on the box door; -1 pcs.Four polle differential overload trip 63/0.3 A; - 40 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; -20 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; - Other fine material (copper bus bar,terminal,conductors,insulatos,pertinax board,lugs,screws, etc.). | pcs | 1 |  | 0
5 |  | RO-1 |  |  |  | 0
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard typically tested for the equipment with the following characteristics: dimensions up to WxHxD: 1000x2200x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Place a sign under each element.Instal the following equipment in the cabinet: -1 pcs. three polle main switches , current rating ln=63 A , two-position, 0-1, monting on the box door. --3 pcs. one polle (grebenasti) switches , current rating ln=10 A , two-position, 0-1, monting on the box door; -1 pcs.four polle differential overload trip 63/0.3 A; - 36 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 16 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; -12 pcs. one gang protection switch (1P) B,230 V,50 Hz, rated current 10 A, breaking capacity 10 kA with overcurrent shutter button (thermal and electromagnetic ) ; - Other fine material (copper bus bar,terminal,conductors,insulatos,pertinax board,lugs,screws, etc.) .Calculation pre peace installed block. | pcs | 1 |  | 0
6 |  | RO-HS |  |  |  | 0
| 4.1 & 4.2 & 4.4 | Supply and installation of 0.4kV switchgear block, modular, standard tested for the equipment of following characteristics: dimensions up to WxHxD: 550x650x250 mm, for wall mounting, external degree of protection IP43, complete connecting supplies according to the manufacturer's specifications, access to equipment from the front, access to cables from the front, bus bars 3P+N+E, of corresponding nominal current. Install equipment in the cabinet according to the single pole scheme. Place a nameplate under each element. Leave 30% of spare space in the distribution cabinet for subsequent equipment installation.Calculation pre peace installed block. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
4 |  | SOCKET OUTLETS INSTALLATION
Supply and installation of installation modules, with the possibility of automatic connection and disconnection. Modules include the following types:
1 | 4.1 & 4.2 & 4.4 | – Installation set for six modular elements. Item includes all the elements needed for installation of the set. 1 pc mount for 6 modules 1 pc frame for 6 modules 3 pcs of socket outlets 16A 230V Calculation per peace installed set. | pcs | 23 |  | 0
2 | 4.1 & 4.2 & 4.4 | – Installation set for four modular elements. Item includes all the elements needed for installation of the set. Set includes the following equipment: 1 pc mount for 4 modules 1 pc frame for 4 modules 2 pcs of socket outlets 16A 230V Calculation per peace installed set. | pcs | 18 |  | 0
3 | 4.1 & 4.2 & 4.4 | – Installation set with two modular elements. Item includes all the elements needed for installation of the set. Set includes the following equipment: 1 pc mount for 2 modules 1 pc frame for 2 modules 1 pc of socket outlets 16A 230V Calculation per peace installed set. | pcs | 87 |  | 0
4 | 4.1 & 4.2 & 4.4 | – Installation set with one modular element with IP 55 protection. Item includes all the elements needed for installation of the set. Set includes the following equipment: 1 pc of socket outlet 16A 230V IP55, Calculation per peace installed set. | pcs | 3 |  | 0
5 | 4.1 & 4.2 & 4.4 | Delivery and installation of three-phase earthed socket 400V. Calculation per installed socket. | pcs | 6 |  | 0
6 | 4.1 & 4.2 & 4.4 | Delivery and installation of installation lines, type N2XH, of appropriate cross-section and number of wires, for the supply of installation sets. Conductors are placed partly in cable trays, and partly through the parapet distribution.calculation per m installed lines. |  |  |  | 0
|  | N2XH-J 5x6 mm² | m | 50 |  | 0
|  | N2XH-J 5x4 mm² | m | 50 |  | 0
|  | N2XH-J 5x2,5 mm² | m | 250 |  | 0
|  | N2XH-J 3x2,5 mm² | m | 1900 |  | 0
7 | 4.1 & 4.2 & 4.4 | Delivery and installation of installation pipes phi 23 mm. Calculation per m. | m | 500 |  | 0
|  | TOTAL |  |  |  | 0
5 |  | LIGHTING
1 | 4.1 & 4.2 & 4.4 | Mounted luminaires 771 PC 2x49 W T5 IP65. Calculation per pcs. | pcs | 29 |  | 0
2 | 4.1 & 4.2 & 4.4 | Mounted luminaires P2M 262x49W T16 EB IP20. Calculation per pcs. | pcs | 8 |  | 0
3 | 4.1 & 4.2 & 4.4 | Mounted luminaires LSV 222x54W T16 EB IP54. Calculation per pcs. | pcs | 48 |  | 0
4 | 4.1 & 4.2 & 4.4 | Mounted luminaires 220 FLUO TR 2x26 W EVG IP40. Calculation per pcs. | pcs | 25 |  | 0
5 | 4.1 & 4.2 & 4.4 | Mounted luminaires PSP 272x54W T16 EB IP54. Calculation per pcs. | pcs | 6 |  | 0
6 | 4.1 & 4.2 & 4.4 | Mounted luminaires ROUND 900 8x14W T16 . Calculation per pcs. | pcs | 9 |  | 0
7 | 4.1 & 4.2 & 4.4 | Mounted luminaires ONE WAY LED 1x4 W IP65. Calculation per pcs. | pcs | 13 |  | 0
8 | 4.1 & 4.2 & 4.4 | Mounted luminaires 2x54W T16 EB IP43. Calculation per pcs. | pcs | 49 |  | 0
9 | 4.1 & 4.2 & 4.4 | Emergency luminaire GR312 1x8 W , 3h. Calculation per pcs. | pcs | 40 |  | 0
10 | 4.1 & 4.2 & 4.4 | Delivery and laying of installation lines of appropriate cross-section and number of wires, for the supply of lighting installations. Conductors are placed in cable trays. Calculation per m. |  |  |  | 0
|  | N2XH-Y 3x1,5 mm² | m | 2500 |  | 0
|  | Delivery and installation of installation pipes Ø16 mm. Calculation per m. | m | 800 |  | 0
11 | 4.1 & 4.2 & 4.4 | Delivery and installation of switches. Switches are mounted at a height of 1.1 m from the floor. Item includes delivery of distribution box Ø60 mm for mounting on the wall. Calculation per piece installed switches. |  |  |  | 0
|  | plain - 1 unipolar, in box 2M , complete | pcs | 11 |  | 0
|  | plain - 2 unipolar in box 2M , complete | pcs | 22 |  | 0
|  | plain - 4 unipolar in box 4M , complete | pcs | 1 |  | 0
|  | alternating - 1 alternating in box 2M | pcs | 4 |  | 0
|  | alternating - 2 alternating in box 2M | pcs | 2 |  | 0
|  | alternating - 4 alternating in box 4M | pcs | 2 |  | 0
12 | 4.1 & 4.2 & 4.4 | Wall mounted motion detector IP44. calculation per piece instaled detector. | pcs | 2 |  | 0
|  | TOTAL |  |  |  | 0
6 |  | EQUALIZATION OF POTENTIAL IN SUBSTATION
1 | 4.1 & 4.3 & 4.4 | Supply and delivery of steel galvanized FeZn 25x4 mm strip for forming of the foundation earthing electrode.Calculation per m. | m | 100 |  | 0
2 | 4.1 & 4.3 & 4.4 | Supply and delivery of steel galvanized FeZn 20x3 mm strip for forming of potential equalization ring in the heating substation. It is executed by placing on the supporting mounts at a height of 0.5 m from the floor.Calculation per m. | m | 25 |  | 0
3 | 4.1 & 4.3 & 4.4 | Supply and delivery of supporting mounts SRPS N.B4.925/P for installation of FeZn 20x3mm, which is used to form the potential equalization rings. Calculation per pcs. | pcs | 50 |  | 0
4 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of SRPS N.B4.936/III cross piece, which is placed at all jointing points, i.e. Intersections of iron galvanized strips.Calculation per pcs. | pcs | 20 |  | 0
5 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of the P/F 1x16 mm² l=0,3m conductor with lugs on both ends for bridging of metal masses in the substation.Calculation per pcs. | pcs | 20 |  | 0
|  | TOTAL |  |  |  | 0
7 |  | LIGHTNING ARRESTER INSTALLATION
1 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of complete arrester with early start. Arrester is installed on the mount, height 5 m, lead time t= Δt=25μs. Dimensions Ø100mm, H=330mm.Calculation per pcs. | pcs | 1 |  | 0
2 | 4.1 & 4.3 & 4.4 | Supply and delivery of steel galvanized FeZn 20x3mm strip for forming of the drain of the lightning arrester.Calculation per m. | m | 30 |  | 0
3 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of the arrester mount, length 5 m, made of galvanized water supply pipes Ø50mm, equipped with an anchor plate dimensions 400x400x5mm and all the necessary equipment for securing the mount.Calculation per pcs. | pcs | 1 |  | 0
4 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of aluminum wire phi 10mm on the roof covering. The wire is laid on trays, which are placed at every 0.5 m.Calculation per m. | m | 50 |  | 0
5 | 4.1 & 4.3 & 4.4 | Supply, delivery and installation of measuring compression joint (type D SRPS N.B4.932) for connecting the descending lines of the lightning arrester installation with existing system of the foundation earthing electrode.Calculation per pcs. | pcs | 2 |  | 0
6 | 4.1 & 4.3 & 4.4 | Testing of the lightning arrester installation, continuity check, proper measurement of the resistance distribution and obtaining the Test certificate of the same.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
8 |  | DIESEL-GENERATOR
1 | 4.1 | Diesel-generator, nominal power 120 kVA. Generator 400/230 V, 50Hz in soundproof housing. Included controller for manual and automatic switching on, controlled by the microprocessor unit, ATS 125A and sound attenuator a on the exhaust pipe.Calculation per pcs. | pcs | 1 |  | 0
2 | 4.1 | Installation, connecting of ATS, fabrication of earthing and filling of tanks with 70 liters of fuel.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
9 |  | LOW VOLTAGE CONNECTION
1 | 2.6.2 & 4.1 | Mechanical and manual excavation of the trench for cable ducts on the route in VI category soil, for the cable duct. Dig cable canal according to the drawing. Trench dimensions: 0,5 x 0,8. The price includes breaking and cutting of asphalt and concrete.Calculation per m. | m | 100 |  | 0
2 | 2.9.1 & 2.9.2 & 4.1 | Backfilling the soil trench for cable ducts on the route in VI category soil, with compacting in layers and disposal of excess soil to the designated spot. The price includes other works in connection with excavation and backfilling of canals, which may arise on the spot: paying attention to the underground facilities along the route, protecting them from damage, filling the bottom of the cable trench with fine grained soil or sand, above and below the cable in two layers of 10 cm each, laying of cable ducts, attention tape, as well as other contingencies.Calculation per m. | m | 100 |  | 0
3 | 4.1 & 2.25 | Patching of asphalt and concrete.Calculation per m². | m2 | 50 |  | 0
4 | 4.1 & 2.11 | Supply and installation of concrete cable ducts.Calculation per m. | m | 100 |  | 0
5 | 4.1 & 2.11 | Fabrication of cable manhole, internal dimensions 2 x 2 x 2 x m, complete (formwork, reinforcement and concreting, smoothing, stirrups for climbing, cover for cargo transport), with supply and delivery of necessary material.Calculation per pcs. | pcs. | 4 |  | 0
6 | 4.1 | Supply and installation of main supply cable PPOO-A through already placed installation.Calculation per pcs. | pcs. | 120 |  | 0
7 | 4.1 | Supply and installation of KPK supply boxes.Calculation per pcs. | pcs. | 1 |  | 0
8 | 4.1 | Completing the N connector in the existing TS.Calculation per pcs. | pcs. | 1 |  | 0
9 | 4.1 | Other small unspecified material and contingencies, which are not included in the previous items.Calculation per pcs. | pcs. | 1 |  | 0
10 | 4.1 | Recording of the route of the newly designed cable and entering into the cadastral plan.Calculation per pcs. | pcs. | 1 |  | 0
|  | TOTAL |  |  |  | 0
10 |  | OTHER WORKS
1 |  | Inspection, testing of electrical installations and issuing test protocol - report by the authorized organisation. | LS | 1 |  | 0
|  | Total |  |  |  | 0
|  | RECAPITULATION |  |  |  | 0
1 |  | DISTRIBUTION OF CABLE RACKS |  |  |  | 0
2 |  | MAIN SUPPLY CABLES |  |  |  | 0
3 |  | DISTRIBUTION CABINETS |  |  |  | 0
4 |  | SOCKET OUTLETS INSTALLATION |  |  |  | 0
5 |  | LIGHTING |  |  |  | 0
6 |  | EQUALIZATION OF POTENTIAL |  |  |  | 0
7 |  | LIGHTNING ARRESTER INSTALLATION |  |  |  | 0
8 |  | DIESEL-GENERATOR |  |  |  | 0
9 |  | LOW VOLTAGE CONNECTION |  |  |  | 0
10 |  | OTHER WORKS |  |  |  | 0
|  | TOTAL HIGH VOLTAGE |  |  |  | 0
B |  | LOW VOLTAGE ELECTRICAL INSTALLATIONS
1 |  | TELEPHONE AND COMPUTER SYSTEM
1 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery, installation and connection of the communication cabinet RACK1 (ground floor). Calculation per pcs.
- Communication cabinet 19", 42U with fan, free standing with glass door, lock at the front, with removable sides, removable back, IP20, equipped with:
|  | - cable organizer 19", 1U | pcs | 5
|  | - PATCH panel, 19", 24-port, Cat6,FTP | pcs | 4
|  | - Switch 24 port | pcs | 3
|  | - power supply | pcs | 1
|  | Small installation material, labelling | set | 1
|  |  | set | 1 |  | 0
2 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery and placement of UTP Cat 6 cable.Calculation per m. | m | 1500 |  | 0
3 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery and placement of cable 5x2x0,6 mm² for connecting the installation of telephone cabinet and rack cabinet.Calculation per m. | m | 30 |  | 0
4 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery and placement of halogen free RBC hose, diameter of 16 mm.Calculation per m. | m | 1000 |  | 0
5 | 5.1.1.1 & 5.1.1.2 & 5.2 | Installation of RJ45 module at the end of the cable in the rack.Calculation per pcs. | pcs | 40 |  | 0
6 | 5.1.1.1 & 5.1.1.2 & 5.2 | Installation of RJ45 module at the end of the cable at the socket outlet.Calculation per pcs. | pcs | 40 |  | 0
7 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery of the patch cable l= 1 m.Calculation per pcs. | pcs | 40 |  | 0
8 | 5.1.1.1 & 5.1.1.2 & 5.2 | Labelling of all feeds, connecting, testing and issuing of Test certificate.Calculation per pcs. | pcs | 1 |  | 0
9 | 5.1.1.1 & 5.1.1.2 & 5.2 | UPS (on-line / double conversion) 2000VA/230V .Calculation per pcs. | pcs | 1 |  | 0
10 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery, installation and connecting of telephone .Calculation per pcs. | pcs | 1 |  | 0
11 | 5.1.1.1 & 5.1.1.2 & 5.2 | Delivery, installation and connecting of ITO - L.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
2 |  | VIDEO SURVEILLANCE SYSTEM
1 | 5.1.1.4 & 5.2 | Delivery, installation and connecting of the internal camera • Resolution 1.3 / 3.0 megapixel 1280x960 • Minimum lighting: 0,01 lux@F1.2, AGC ON, 0,028 lux@F2.0, • AGC ON, 0 lux with IR • H.264 / MJPEG video compression • Lens 2,8 mm@F2.0 • HD real-time video, Day / night auto switch • 3D DNR & DWDR & BLC, IR range of up to 30m, vandal proof housing • IP66 protection • 12 VDC ± 10%, PoE (802.3af) Calculation per piece installed camera. | pcs | 7 |  | 0
2 | 5.1.1.4 & 5.2 | Delivery, installation and connecting of the external camera , • Resolution 1.3 / 3.0 megapixel 1280x960 • Minimum lighting: 0,01 lux@F1.2, AGC ON, 0,028 lux@F2.0, • AGC ON, 0 lux with IR • H.264 / MJPEG video compression • Lens 2,8 mm@F2.0 • HD real-time video, Day / night auto switch • 3D DNR & DWDR & BLC, IR range of up to 30m, vandal proof housing • IP66 protection • 12 VDC ± 10%, PoE (802.3af) delivery of wall panel for mounting included Calculation per piece installed camera. | pcs | 9 |  | 0
3 | 5.1.1.4 & 5.2 | Supply and connecting of DNVR-8067NI-SE 8ch NVR 8-CH NETWORK VIDEO RECORDER FOR IP CAMERAS • Supports cameras from different manufacturers • IP video inputs: DNVR-8067NI-SE( / N) 8-ch • Recording resolution up to 5 Megapixel • HDMI and VGA outputs up to 1920×1080P resolution • HDD quota – disk management • 8 independent network interfaces for embedded switch • 12 VDC Calculation per piece installed camera. | pcs | 2 |  | 0
4 | 5.1.1.4 & 5.2 | Delivery and connecting of HDD 1 TB .Calculation per pcs. | pcs | 1 |  | 0
5 | 5.1.1.4 & 5.2 | Delivery LG 22” wide LCD monitor full HD 1920x1080.Calculation per pcs. | pcs | 1 |  | 0
6 | 5.1.1.4 & 5.2 | Delivery and connecting of 16 port POE switch.Calculation per pcs. | pcs | 1 |  | 0
7 | 5.1.1.4 & 5.2 | Delivery and placement of UTP Cat 6 cable.Calculation per m. | m | 500 |  | 0
8 | 5.1.1.4 & 5.2 | Delivery and placement of halogen free RBC hose with diameter of 16 mm. Calculation per m. | m | 300 |  | 0
9 | 5.1.1.4 & 5.2 | Installation of RJ45 module at the end of the cable in the rack.Calculation per pcs. | pcs | 16 |  | 0
10 | 5.1.1.4 & 5.2 | Installation of RJ45 module at the end of the camera cable.Calculation per pcs. | pcs | 16 |  | 0
11 | 5.1.1.4 & 5.2 | Delivery of the patch cable l= 1 m.Calculation per pcs. | pcs | 16 |  | 0
12 | 5.1.1.4 & 5.2 | Testing and commissioning.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
3 |  | INTERCOM INSTALLATION
1 | 5.1.1.5 & 5.2 | Delivery, installation and connecting of intercom sets, consisting of one external calling unit and one internal unit, together with the power supply and batteries. Calculation per installed set. | set | 2 |  | 0
2 | 5.1.1.5 & 5.2 | Delivery and installation of JH(St)H 4x2x0,8. Calculation per m. | m | 60 |  | 0
3 | 5.1.1.5 & 5.2 | Delivery and installation of halogen free RBC hose with diameter of 16 mm Calculation per m. | m | 50 |  | 0
4 | 5.1.1.5 & 5.2 | Testing and commissioning. Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
4 |  | TV INSTALLATION
1 | 5.1.1.3 & 5.2 | Delivery, installation and connecting of the antenna on the roof of the building for reception of TV signal.Calculation per pcs. | pcs | 1 |  | 0
2 | 5.1.1.3 & 5.2 | Delivery, installation and connecting of TV connectors, designed for wall mounting.Calculation per pcs. | pcs | 10 |  | 0
3 | 5.1.1.3 & 5.2 | Delivery, installation and connecting of the RG 6 cable.Calculation per m. | m | 200 |  | 0
4 | 5.1.1.3 & 5.2 | Delivery, installation and connecting of the RG 11 cable.Calculation per m. | m | 40 |  | 0
5 | 5.1.1.3 & 5.2 | Delivery and installation of the halogen free RBC hose with diameter of 16 mm.Calculation per m. | m | 150 |  | 0
6 | 5.1.1.3 & 5.2 | Testing and commissioning.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF LOW VOLTAGE ELECTRICAL INSTALLATIONS
1 |  | TELEPHONE AND COMPUTER SYSTEM |  |  |  | 0
2 |  | VIDEO SURVAILLANCE SYSTEM |  |  |  | 0
3 |  | INTERCOM INSTALLATION |  |  |  | 0
4 |  | TV INSTALLATION |  |  |  | 0
|  | TOTAL |  |  |  | 0
B1 |  | AUTOMATIC FIRE DETECTION AND ALARM SYSTEM
1 | 5.3. | Supply, install and connect in the assembly hall the analogue addressable microprocessor fire alarm control panel with one loop, expandable to two loops, capacity of 254 addresses in the loop, 200 alarm zones, with two programmable relay outputs, two horn sounder outputs, two programmable open collector outputs, and six programmable digital outputs, possesses a digital display, MX4201 and with NiCd batteries of 16 Ah, Calculation per pcs. | pcs | 1 |  | 0
2 | 5.3. | Delivery and installation of accumulator batteries, whose capacity in quiet mode, and 0.5h in alarm mode, 12 VDC, 65 Ahu, set with the placement box (1 piece). Calculation per pcs. | pcs | 2 |  | 0
3 | 5.3. | Supply, mount directly on the ceiling in the base NTN-UB-4 and connect analog, addressable optical fire alarm, type as NTN-EV-P with complete equipment, . The price includes: alarm, base, other necessary material and labor. Calculation per pcs. | pcs | 35 |  | 0
4 | 5.3. | Supply, mount directly on the ceiling in the base NTN-UB-4 and connect analog, addressable thermal fire alarm, type as NTN-EV-H-CS with complete equipment, . The price includes: alarm, base, other necessary material and labor. Calculation per pcs. | pcs | 3 |  | 0
5 | 5.3. | Supply, install in the housing to be mounted on the wall and connect the addressable manual alarm, type as NTN-EV-MCP-RS, . The price includes: alarm, base, other necessary material and labor. | pcs | 10 |  | 0
6 | 5.3. | Supply, mount on the wall and connect the horn sounder, type as EMA 1224 B4R, , with a deep base .Calculation per pcs. | pcs | 7 |  | 0
7 | 5.3. | Delivery, installation and connecting of the addressable output module (2xDO) for connection of MDB. Calculation per pcs. | pcs | 1 |  | 0
8 | 5.3. | Delivery and installation of telecommunication installation halogen free cable, type JH(St)H 2x2x0,8 mm Calculation per m.. | m | 750 |  | 0
9 | 5.3. | Delivery and placement of installation halogen free and fire resistant cable, type NHXHX 3x1,5 mm² FE180/E90.Calculation per m. | m | 200 |  | 0
10 | 5.3. | Delivery and placement of halogen free RBC hose with diameter of 16 mm. Calculation per m. | m | 300 |  | 0
11 | 5.3. | Connecting of all system elements, necessary measurements and tests on all cable routes, programming of the control panel and assigning of addresses, marking of horn sounders, issuing of necessary Test certificates and instructions, training of users. Calculation per set | set | 1 |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF ELECTRICAL INSTALLATION WORKS
A |  | HIGH VOLTAGE |  |  |  | 0
B |  | LOW VOLTAGE |  |  |  | 0
B1 |  | AUTOMATIC FIRE DETECTION AND ALARM SYSTEM |  |  |  | 0
| TOTAL ELECTRICAL INSTALLATION WORKS |  |  |  |  | 0
MECHANICAL INSTALLATIONS-CENTRAL HEATING
1 |  | HEATERS AND ACCESSORIES
1 | 6.1.2. | Delivery and installation of STEEL PANEL radiators, complete, with holders and other accessories. The price includes everything needed for a completely installed radiator.Calculation per pcs.
1.1 |  | TIP 600/22 length: 400 | pcs | 6 |  | 0
1.2 |  | TIP 600/22 lenght:800 | pcs | 1 |  | 0
1.3 |  | TIP 600/22 lenght:1000 | pcs | 2 |  | 0
1.4 |  | TIP 600/22 lenght:1200 | pcs | 3 |  | 0
1.5 |  | TIP 600/22 lenght:1400 | pcs | 10 |  | 0
1.6 |  | TIP 600/22 lenght:1600 | pcs | 5 |  | 0
1.7 |  | TIP 600/22 lenght:1800 | pcs | 9 |  | 0
1.8 |  | TIP 600/22 lenght:2000 | pcs | 9 |  | 0
2 | 6.1.2. | Automatic air vent valve on all radiators | pcs | 45 |  | 0
3 | 6.1.3 | Delivery and installation of nickel-plated radiator valves for TWO-PIPE system. With pre-setting and maintaining the pre-set control. Straight or EC, NO 15. Calculation per pcs. |  |  |  | 0
|  | With thermostatic head. | pcs | 45 |  | 0
4 | 6.1.3 | Delivery and installation of nickel-plated radiator valves. Valves are nickel-plated and have sealable caps. Metal lid on the cap is mandatory. NO 15 Calculation per pcs. | pcs | 45 |  | 0
5 | 6.1.2. | Delivery and installation of drain cock. Ball valves. Complete with hose connection 1/2" NO 15 .Calculation per pcs. | pcs | 45 |  | 0
|  | TOTAL |  |  |  | 0
2 |  | PLASTIC PIPES AND FITTINGS
1 | 6.1.4 | Supply and installation of HEATING pipes. Pipes are laid in a layer of screed in spongy pipe insulation surround. |  |  |  | 0
|  | Pipes made of cross linked polyethylene PE-Xa for heating 16X2,2mm, non-insulated.Calculation per m. | m | 900 |  | 0
2 | 6.1.4 | Set of connecting union joint, for connecting the angle set 15 x 1 and radiator valves. G3/4-15 Adjust according to the supplied valve and angled set.Calculation per pair. | pr | 44 |  | 0
3 | 6.1.4 | Angle connection fitting 16/250 made of stainless steel, dimensions 15x1 mm, for connecting the pipes to radiators length l= 250mm.Calculation per pcs. | pcs | 88 |  | 0
4 | 6.1.4 | Union joint on pipe distributor or equivalent 16X2,2mm.Calculation per pcs. | pcs | 88 |  | 0
5 | 6.1.4 | Mobile cover for permanently sealed connections PX 16X2,2mm ,Calculation per pcs. | pcs | 88 |  | 0
6 | 6.1.4 | Pipe guides for achieving the required radius for pipe f 16/17 mm.Calculation per pcs. | pcs | 176 |  | 0
7 | 6.1.4 | Double rosette 15 x 1.Calculation per pcs. | pcs | 44 |  | 0
8 | 6.1.4 | Delivery and installation Thermal insulation pipes , thickness 9mm for pipes 18/9.Calculation per m. |  |  |  | 0
|  | F 18 /9 | m | 900 |  | 0
|  | TOTAL |  |  |  | 0
3 |  | STEEL PIPE FITTINGS
1 |  | Delivery and installation of black seamless pipes for hot water according to JUS C.B5.221 and 225. Pipes are provided with all the necessary material for joining, fastening, carrying, fixed points, sliding points, work gases, rosettes and passage sleeves, i.e. fittings. Calculation per m.The following pipes are provided: |  |  |  | 0
| 6.1.5. | NO 15 f 21 * 2,65 mm | m | 0 |  | 0
|  | NO 20 f 26 * 2,65 mm | m | 40 |  | 0
|  | NO 25 f 33 * 3.25 mm | m | 40 |  | 0
|  | NO 32 f 42 * 3.25 mm | m | 42 |  | 0
|  | NO 40 f 48 * 3.25 mm | m | 10 |  | 0
|  | NO 50 f 60.3 * 3.65 mm | m | 25 |  | 0
2 | 6.1.5. | Additional material and fittings for connecting of black pipes, 50% of previous item
3 | 6.1.5. | Delivery and installation of axial expansion joints for central heating. Expansion joint for jointing by welding and with a protective sleeve and screw which is unscrewed after the installation is complete. Operating pressure up to 10 bar. Total elongation 30 mm. Mounting length 240 mm. Type AS 10 nominal diameter DN 32/6.Calculation per pcs. | pcs | 2 |  | 0
4 | 6.1.5. | Fabrication of pipe guides for axial expansion joint. They are placed on both sides of the expansion joint at a distance of 10DN which is 500 mm. |  |  |  | 0
|  | nominal diameter DN 32/6.Calculation per pcs. | pcs | 4 |  | 0
5 | 6.1.5. | Automatic vent tap 1/2”, installed at the vertical endings at storey racks.Calculation per pcs. | pcs | 4 |  | 0
6 | 6.1.3. | Delivery and installation of ball valves. NP 6 mandatory together with union joint.Calculation per pcs. |  |  |  | 0
|  | DN 20/6 | pcs | 1 |  | 0
|  | DN 25/6 | pcs | 5 |  | 0
|  | DN 32/6 | pcs | 5 |  | 0
7 | 6.1.3. | Delivery and installation of balancing valve on the return line, with connections for measuring instrument. Calculation per pcs. |  |  |  | 0
|  | DN 15/6 | pcs | 1 |  | 0
|  | DN 20/6 | pcs | 5 |  | 0
8 | 6.1.3. | Delivery and installation of union joint with balancing valve on the return line, with corresponding nipple.Calculation per pcs. |  |  |  | 0
|  | DN 15/6 | pcs | 1 |  | 0
|  | DN 20/6 | pcs | 5 |  | 0
|  | TOTAL |  |  |  | 0
4 |  | STOREY MANIFOLDS
1 |  | Delivery and installation of radiator heating manifolds HLV with ball valves, vents and drain cocks. All with necessary accessories for connecting. Complete for supply and return. Storey racks.Calculation per pair.
| 6.1.4 | MANIFOLD HLV-6 FOR 6 CIRCUITS NO 25 ( 1”) | pr | 2 |  | 0
|  | MANIFOLD HLV-7 FOR 7 CIRCUITS NO 25 ( 1”) | pr | 3 |  | 0
|  | MANIFOLD HLV-9 FOR 9 CIRCUITS NO 25 ( 1”) | pr | 1 |  | 0
2 | 6.1.4 | Delivery and installation of the manifold cabinet for wall mounting. Cabinet has adjustable height and adjustable lid and a lock. Complete with necessary chiselling and polyurethane foam for wall mounting.Calculation per pcs. |  |  |  | 0
|  | MANIFOLD CABINET FOR 6-10 CIRCUITS 874*708*110-160 mm, WALL MOUNTING (UP). | pcs | 6 |  | 0
|  | TOTAL |  |  |  | 0
5 |  | SUBSTATION EMERGENCY WARD
1 | 6 | Delivery and installation of electrical circulation pumps.Calculation per pcs. with these characteristics: |  |  |  | 0
|  | 40-60FN), for operating conditions Q = 4788/h and H = 24.8kPa N=(12-178)W, l=220mm, 1x230V, 50/60Hz | pcs | 2 |  | 0
2 | 6 | Delivery and installation of the motorized 3-way valve. Connections with internal thread, brass. To be manually selected or to work with actuator. Optional installation on the left and right side. Working pressure: 10 bor, max. Temperature +110 C. Calculation per pcs. |  |  |  | 0
|  | 3 WAY VALVE VRG 131, DN=40, Rp 11/2“,Kvs=25,l=116mm | pcs | 1 |  | 0
3 | 6 | Delivery and installation of servomotors for 3-way valves VRG 131. Operating voltage 230V/50Hz, torque 10 Nm, transition time of 140 s, manual/automatic positioning, reversible scale for positioning indication 1 ... 10. Complete with installation components (integrated board adapter for 3-way valves VRG) .Calculation per pcs. |  |  |  | 0
|  | SERVOMOTOR FOR 3-WAY MOTOR VALVE VRG 130, DN=40, Rp 1 1/2“,Kvs=25 | pcs | 1 |  | 0
4 | 6 | Delivery and installation of the TEMPERATURE CONTROLLER, electric motor drive CRS 110 together with distribution sensor and external sensor. Control range: 20-90 C.Calculation per pcs. | pcs | 1 |  | 0
5 | 6 | Delivery and installation of the pressure relief valve, straight or angled, complete with union joints for differential pressure 0.1 bar.Calculation per pcs. |  |  |  | 0
|  | DN 32(5/4“) NP 6 | pcs | 1 |  | 0
6 | 6 | Delivery and installation of pipe thermometers with round scale D= 80 mm to 120 C.Calculation per pcs. | pcs | 3 |  | 0
7 | 6 | Delivery and installation of pressure gauges for pressure up to 10 bar, complete with gauge cock. D=80 mm.Calculation per pcs. | pcs | 2 |  | 0
8 | 6 | Delivery and installation of elastic connections, rubber expansion joints, complete with flanges. GU - KO PN 6.Calculation per pcs. |  |  |  | 0
|  | GU - KO DN40 PN 6 | pcs | 2 |  | 0
9 | 6 | Delivery and installation of flange sets. Complete flange with neck, gaskets and screws with nuts. PN 6.Calculation per pcs. |  |  |  | 0
|  | DN 40/6 | pcs | 4 |  | 0
|  | DN 50/6 | pcs | 14 |  | 0
10 | 6 | Delivery and installation of BALL valves. NP6. Calculation per pcs. |  |  |  | 0
|  | DN 50/6 | pcs | 5 |  | 0
11 | 6 | Delivery and installation of flange sets. Complete flange with neck, gaskets and screws with nuts. PN 6. Calculation per pcs. |  |  |  | 0
|  | DN 50/6 | pcs | 10 |  | 0
12 | 6 | Delivery and installation of concentric reducers. Calculation per pcs. |  |  |  | 0
|  | DN 50/ DN40 | pcs | 2 |  | 0
13 | 6 | Delivery and installation of flat strainers. Calculation per pcs. |  |  |  | 0
|  | DN 50/6 | pcs | 1 |  | 0
14 | 6 | Delivery and installation of BALL valves. NO 15 NP 6.Calculation per pcs. |  |  |  | 0
|  | DN 20/6 | pcs | 2 |  | 0
|  | TOTAL |  |  |  | 0
6 |  | INSULATION AND PAINTING
1 | 6 | Insulation of the pipe network with mineral wool roll, thickness 50 mm in the mesh foil jacket, bound with copper wire or synthetic rope. Item relates to pipe network in the hallways. HEATING NETWORK. Per m² of mineral wool. | m² | 60 |  | 0
2 | 6 | Painting of visible parts of pipes and equipment with radiator varnish in two coats, color chosen by the Investor. Calculation per m. | m | 250 |  | 0
|  | TOTAL |  |  |  | 0
7 |  | TESTING AND MEASURING
1 | 6.2. | Obtaining Test certificates on the noise level in the heating substation room, under Article C.13 of the Technical Terms and Conditions. | LS | 1 |  | 0
2 | 6.2. | Setting the radiator valves to the foreseen regulation positions in accordance with Article D.8 of the Technical Terms and Conditions. | LS | 1 |  | 0
3 | 6.2. | Works on mechanical installation flush with the control of soiling and preparing of report on executed works, in accordance with Article D.11 of the Technical Terms and Conditions. | LS | 1 |  | 0
4 | 6.2. | Flow measurement and balancing the complete installation by using a differential pressure gauge and other certified instruments. Preparation of the study on completed measurement and regulation, in accordance with Article C.84 of the Technical Terms and Conditions. | LS | 1 |  | 0
5 | 6.2. | Testing the central heating installation for pressure and tightness in accordance with JUS M.E6.012 and Article D.10 of the Technical Terms and Conditions. | LS | 1 |  | 0
6 | 6.2. | Thermo technical testing of the central heating installations (hot test). | LS | 1 |  | 0
7 | 6.2. | Compliance of ventilation installations with the preparation of the study on the measurement of air flow. | LS | 1 |  | 0
8 | 6.2. | On-site measurement and testing of air permeability according to JUS U.J5.100 and quality of the installed thermal insulation of external walls according to JUS.U.J5.600, in accordance with Articles D.30-D.32 of the Technical Terms and Conditions. | LS | 1 |  | 0
9 | 6.2. | On-site measurement and testing of the quality of installed thermal insulation of external walls, according to JUS U.J5.062, along with preparation of Report, which should be signed by the main construction contractor, subcontractor for the installation of thermal insulation, and contractor | LS | 1 |  | 0
|  | TOTAL |  |  |  | 0
8 |  | PREPARATORY AND FINISHING WORKS
1 | 6 | Preparatory works: introduction to the building, measuring and marking, material and tools transport, organizing of the construction site and reviewing the technical documentation. The value of the preparatory work is calculated in the amount of 1% of the total value of works. | % | 1%
2 | 6 | Finishing works: pre-commissioning of installations, preparation of operating and maintenance instructions in three copies, preparation and installation of framed connections diagram on a clearly visible place in the heating substation, marking installation elements, clearing construction site. | % | 2%
3 | 6 | Preparation of the as-built design of complete installation. 3 copies of the study are submitted to the Investor. The value of the as-built design is calculated in the amount of 1% of the total value of works according to this Breakdown of the Lump-sum price. | % | 1%
|  | TOTAL |  |  |  | 0
RECAPITULATION OF MECHANICAL WORKS
1 |  | HEATERS AND ACCESSORIES |  |  |  | 0
2 |  | PLASTIC PIPES AND FITTINGS |  |  |  | 0
3 |  | STEEL PIPE FITTINGS |  |  |  | 0
4 |  | STOREY MANIFOLDS |  |  |  | 0
5 |  | SUBSTATION EMERGENCY WARD |  |  |  | 0
6 |  | INSULATION AND PAINTING |  |  |  | 0
7 |  | TESTING AND MEASURING |  |  |  | 0
8 |  | PREPARATORY AND FINISHING WORKS |  |  |  | 0
|  | TOTAL MECHANICAL INSTALLATIONS |  |  |  | 0
HEATING PIPELINE
A |  | MECHANICAL WORKS
1 | 6.1.4. | Delivery and installation of pre-insulated pipes (with manufacturer's Test certificates), with installed electric cables for the control of the pipeline network, the temperature regime of 130° C. Pre-insulated pipes must comply with the European standard EN 253. Welding is executed according to standards and regulations.Calculation per m.
|  | - DN50 (ø60,3x2,9mm)/ ø140mm | m | 60 |  | 0
2 | 6.1.4. | Delivery and installation of pre-insulated pipe arches R=1.5 D (with manufacturer's Test certificates, with installed electric cables for the control of the pipeline network, the temperature regime of 130° C (standard arches) -KB. The pre-insulated arches must comply with European standard EN 448.Calculation per pcs. |  |  |  | 0
|  | - DN50 (ø60,3x2,9mm)/ l= 1000mm | pcs | 10 |  | 0
3 | 6.1.4. | Delivery and installation of one-piece heat shrink coupler which consists of: - PEHD jacketed pipe - PEHD heat shrink coupler - Sealing tape - Openings for filling - Vent with sealing cap - Polyurethane foam components A and B, per piece |  |  |  | 0
|  | - DN50/DA125 l= 600mm | pcs | 26 |  | 0
4 | 6.1.4. | Delivery and installation of drain cocks, complete with couplings for welding.Calculation per pcs. |  |  |  | 0
|  | - DN20 (3/4") | pcs | 2 |  | 0
5 | 6.1.4. | Crossing of existing pipes, fabrication of new connections, cleaning, painting and protection of existing walls from damage. | LS | 1 |  | 0
6 | 6.1.4. | Delivery and installation of black seamless pipes for hot water according to JUS C.B5.221 and 225. Pipes are provided with all the necessary material for joining, fastening, carrying, fixed points, sliding points, work gases, rosettes, and passage sleeves, i.e. fittings. Calculation per m. |  |  |  | 0
|  | NO 50 f 60.3 * 3.65 mm | m | 80 |  | 0
7 | 6.1.4. | Delivery and installation of the new arches R=1.5D.Calculation per pcs... |  |  |  | 0
|  | - DN50 | pcs | 16 |  | 0
8 | 6.1.4. | Delivery and installation of pre-insulated combined shut-off fitting, with service valve, with installed electric cables for control of the pipeline network, temperature regime of 130 ° C. Delivery should also include the protective pipe with protective cap and laminate and T-key. Calculation per pcs. |  |  |  | 0
|  | - DN50 | pcs | 2 |  | 0
9 | 6.1.4. | Pre-insulated fixed piece (fixed point).Calculation per pcs. |  |  |  | 0
|  | - DN50/DA124 | pcs | 2 |  | 0
10 | 6.1.4. | Delivery and installation of the sealing element (EK) - end cap, at the joint between the pre-insulated pipe and the steel pipe.Calculation per pcs. |  |  |  | 0
|  | DN50/DA140 | pcs | 4 |  | 0
11 | 6.1.4. | Delivery and installation of the sealing elements of the pre-insulated pipeline at the passage through the divider (DR).Calculation per pcs. |  |  |  | 0
|  | - DN50/DA125 | pcs | 8 |  | 0
12 | 6.1.4. | Connecting the newly designed heating pipeline to the existing pipelines (material included in the previous items).Calculation per pcs. |  |  |  | 0
|  | - DN50 | set | 2 |  | 0
13 | 6.2. | Radiographic testing by the authorized institution. 20% of welded joints (or as directed by the Investor) is being recorded. They should be noted, documented and evaluated in the report. Depending on the classification of welded joints, take action according to regulations.Calculation per pcs. |  |  |  | 0
|  | - DN50 | pcs | 4 |  | 0
14 | 6.1.4. | Delivery and installation of PE elastic sleeves on the expansion joints of thermal dilatations, length 1 m, partial coating with marginal zone of the laminate. The physical characteristics of the sleeve, as well as the method of installation are provided in the drawing of the pipeline network. Calculation per running meter. |  |  |  | 0
|  | - type I (for insulation diameters ø50-ø160) | m | 20 |  | 0
15 | 6.1.4. | Delivery and installation of styrofoam beams made of polyurethane L-1000x100x100mm for leveling the pipeline in the trench. Calculation per piece. | pcs | 4 |  | 0
16 | 6.2. | Testing the heating pipeline to pressure, by applying the pressure of 6 bar during 24 hours. During the cold probe, the permitted pressure drop is max. 0.2 bar. |  |  |  | 0
|  | Calculation per running meter of the route. | m | 30 |  | 0
17 | 4.1 | Electrical works on the heating pipeline, which consist of delivery, installation and electrical connection, with signal testing, along with report prepared by the Investor.Calculation per set. |  |  |  | 0
|  | - connecting all electric cables (50mTr) | set | 1 |  | 0
18 | 6 | Preparatory and finishing works and transportation costs | LS | 1 |  | 0
19 | 6.1.4. | Entering modifications incurred during construction works into a copy of the Main Project. Modifications are entered in electronic or paper form of the project, depending which form the Contractor has. Any modifications are verified by the responsible contractor, according to which as built design is produced. | LS | 1 |  | 0
20 | 6.1.3. | Delivery and installation of concentric reducers. Item refers to the connection point of the new heating pipeline.Calculation per pcs. |  |  |  | 0
|  | DN 80/ DN50 | pcs | 2 |  | 0
21 | 6.1.3. | Delivery and installation of BUTTERFLY valves. NP 16.Calculation per pcs. |  |  |  | 0
|  | DN 50/16 | pcs | 2 |  | 0
22 | 6.1.3. | Delivery and installation of flange sets. Flanges sets with neck, gaskets and screws with nuts. PN 16.Calculation per pcs. |  |  |  | 0
|  | DN 50/16 | pr | 4 |  | 0
23 | 6.1.7. | Delivery and installation of the venting vessel. F100 x150mm. Calculation per pcs. | pcs | 2 |  | 0
24 | 6.1.7. | Delivery and installation of AUTOMATIC VENT valves. NO 15, addition to the venting vessel.Calculation per pcs. | pcs | 2 |  | 0
|  | TOTAL |  |  |  | 0
B |  | CONSTRUCTION WORKS
I |  | Preparatory works
1 | 2.3 | Marking the route for the commencement of works. |  |  |  | 0
|  | Calculation per m. | m | 30 |  | 0
2 | 2.3 | Marking and cutting, using machinery, existing structures of the asphalt concrete road surface, on the location of the heating pipeline passage. |  |  |  | 0
|  | Calculation per m. | m | 30 |  | 0
3 | 2.4 | Dismantling of the sidewalk concrete slabs, with clearing and stacking of slabs for re-installation, with removal of sand and gravel (debris) to the landfill at a distance of up to 10 km. |  |  |  | 0
|  | Calculation per m². | m² | 4 |  | 0
4 | 2.4 | Demolition of a layer of asphalt concrete, total thickness of 5 cm, with transport of debris to the landfill at a distance of up to 10 km. |  |  |  | 0
|  | Calculation per m². | m² | 12 |  | 0
5 | 2.4 | Manual or machine breaking of the part of the concrete canal for rainwater drain. Thickness of the walls and floor up to 15 cm (presumably) in length of about 1 m. |  |  |  | 0
|  | Calculation per m³. | m³ | 0.5 |  | 0
|  | TOTAL |  |  |  | 0
II |  | EARTHWORKS
1 | 2.5 | Machine trench excavation in II and III category soil. Trench is excavated with proper skew cutting off of the sides. The maximum depth of the excavation is 80 cm starting from the surface of the asphalt. Removal of the material to the city landfill at a distance of up to 10 km. Item also includes the excavation of.Calculation per m³. |  |  |  | 0
|  | mechanically | m³ | 16 |  | 0
|  | manually | m³ | 2 |  | 0
2 | 2.9 | Supply, transport and spreading of sand in the trench and canal. In the canal, the send is spread around the pipes in the full profile of the canal, and in the trench, min. 10 cm below and above the pipe. Bulking coefficient K=1.10. |  |  |  | 0
|  | Calculation per m³ of filled sand. |  |  |  | 0
|  | sand in the earthen canal | m³ | 10 |  | 0
3 | 2.9 | Supply, transport and backfilling of the trench with gravel-sandy material beneath the asphalt and sidewalks. Perform backfilling up to the level of the bedding, in layers of 20-30 cm, with compaction to the required compactness, min. Me = 60 Mpa. The amount of material provided with the bulking coefficient |  |  |  | 0
|  | Calculation per m³. | m³ | 15 |  | 0
4 | 2.9 | Clearing the trench of the material brought during installation of the pipeline. |  |  |  | 0
|  | Calculation based on lump sum. | LS | 1 |  | 0
|  | TOTAL |  |  |  | 0
III |  | REPAIRING WORKS
1 | 2.11 | Concreting of the damaged part of the sidewalk and restoring it to the existing condition to the possible extent . |  |  |  | 0
|  | Calculation per m². | m² | 5 |  | 0
2 | 2.11 | Paving of the part of the yard above the trench in the same thickness as before. |  |  |  | 0
|  | Calculation per m². | m² | 25 |  | 0
3 | 2.11 | Concreting of the demolished part of the rainwater canal, and restoring it to the possible extent . |  |  |  | 0
|  | lump sum | LS | 1 |  | 0
4 | 2.9 | Supply of crushed stone 0-34.5 mm and construction of the upper bearing layer of the road surface. Compacting to min. Me=60Mpa.Calculation per m³. |  |  |  | 0
|  | thickness b=10cm 40,0x0,1= | m³ | 4 |  | 0
5 | 2.11 | Placement of existing kerbs in order to bring the area back to its original state, at the location of the hot-water passages. Item also includes supply of additional kerbs (10%) and cement concrete MB20 for curb installation. |  |  |  | 0
|  | lifted and dropped kerbs 18/24. Calculation per m. | m | 5 |  | 0
|  | TOTAL |  |  |  | 0
IV |  | MASONRY AND CONCRETE WORKS
1 | 2.13 | Supply of material and construction of masonry manhole next to the health center wall, for the entry of new pipes through the wall, with concrete cover and same finishing as the existing wall. Build with concrete blocks or with full brick in cement mortar.
|  | Manhole with light section 1x1 m, depth up to 1.5 m, with providing cover for transport weight.Calculation per pcs. | pcs | 1 |  | 0
| 2.11 | Wall for protection of pipes with external dimensions 1x0.5 m, height of about 1.5 m.Calculation per pcs. | pcs | 1 |  | 0
| 2.11 | Wall for protection of pipes with external dimensions 1x0.5 m, height of about 1.0 m.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
V |  | REINFORCEMENT WORKS
1 | 2.12 | Supply, straightening, cutting, bending, installation, and fixing of reinforcement all according to reinforcement details and specification. Calculation per kilogram of installed reinforcement. | kg | 35 |  | 0
|  | TOTAL |  |  |  | 0
VI |  | OTHER WORKS
1 | 6 | Supply and placement of strips for marking of hot-water pipeline route. Tape is placed over each pipe individually. | m | 45 |  | 0
2 | 6 | Preparatory, finishing, and smaller unforeseen works arising during performing of works on the hot-water pipeline route. | LS | 1 |  | 0
3 | 2.19 | Supply and installation of cast iron cover with frame for heavy traffic in the upper panel of the manhole, all according to the framework details. Calculation per piece of installed cover. | pcs | 1 |  | 0
4 | 6 | Lowering the groundwater level (if needed), using the technology at Contractor's disposal. Calculation of lowering the level of groundwater is done by hours. It is mandatory that the Supervisor controls and certifies the amount of time spent. Calculation per hour. | h | 5 |  | 0
5 | 6 | In the profile grade of the route, the approximate places of the crossing of the existing infrastructure with the hot water pipeline are drawn based on the cadastre of the underground installations. The Breakdown of the Lump-sum price plans their relocation only if it is necessary, which the Supervisor. |  |  |  | 0
|  | During the execution of works it is mandatory to comply with pre-project and Technical Terms and Conditions of JKP "Vodovod", "Telekom Srbija", JKP "Toplana", JKP "Elektrodistibucija". |  |  |  | 0
| 6 | Preparatory, finishing, and smaller unforeseen works arising during performing of works on the hot-water pipeline route. | LS | 1 |  | 0
|  | TOTAL |  |  |  | 0
VII |  | SECURING THE CONSTRUCTION SITE
1 | 6 | Supply, installation and maintenance of protective fence along the route, height 1 m, made of timber and steel profiles and PVC perforated strips in orange; metal pipe joists surrounded by concrete mobile base. |  |  |  | 0
|  | Calculation per m, on both sides. | m | 21 |  | 0
2 | 6 | Supply, transport, installation and removal of pedestrian crossings across the trench of the hot water pipeline canal. |  |  |  | 0
|  | Calculation per piece of the crossing. | pcs | 2 |  | 0
|  | TOTAL |  |  |  | 0
B |  | RECAPITULATION OF CONSTRUCTION WORKS
I |  | PREPARATORY WORKS |  |  |  | 0
II |  | EARTHWORKS |  |  |  | 0
III |  | REPAIRING WORKS |  |  |  | 0
IV |  | MASONRY AND CONCRETE WORKS |  |  |  | 0
V |  | REINFORCEMENT WORKS |  |  |  | 0
VI |  | OTHER WORKS |  |  |  | 0
VII |  | SECURING THE CONSTRUCTION SITE |  |  |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF HEATING PIPELINE WORKS
A |  | MECHANICAL WORKS |  |  |  | 0
B |  | CONSTRUCTION WORKS |  |  |  | 0
|  | TOTAL HEATING PIPELINE |  |  |  | 0
CENTRAL HEATING - HEATING PIPELINE
A |  | MECHANICAL WORKS
1 | 6.1.4. | Delivery and installation of pre-insulated pipes (with manufacturer's Test certificates) with installed electric cables for control of the pipeline network, the temperature regime of 130 ° C. Pre-insulated pipes must comply with the European standard EN 253. Welding is executed according to standards and regulations . Calculation per m.
|  | - DN80 (ø88,9x3,2mm)/ø160mm | m | 22 |  | 0
2 | 6.1.4. | Delivery and installation of pre-insulated pipe arches R=1.5 D (with manufacturer's Test certificates) with installed electric cables for control of the pipeline network, the temperature regime of 130 ° C. (Standard arches) -KB. Pre-insulated pipes must comply with the European standard EN 448.Calculation per pcs. |  |  |  | 0
|  | - DN80 (ø88,9x3,2mm)/ø160mm L= 450mm | pcs | 6 |  | 0
3 | 6.1.4. | Delivery and installation of one-piece heat shrink coupler which consists of: - PEHD jacketed pipe - PEHD heat shrink coupler - Sealing tape - Openings for filling - Vent with sealing cap - Polyurethane foam components A and B, per piece |  |  |  | 0
|  | - DN80/DA160.Calculation per pcs. | pcs | 8 |  | 0
4 | 6.1.4. | Delivery and installation of drain cocks, complete with couplings for welding.Calculation per pcs. |  |  |  | 0
|  | - DN20 (3/4") | pcs | 2 |  | 0
5 | 6.1.4. | Delivery and installation of elements for the sealing of pre-insulated pipeline at the passage through the separator (DR).Calculation per pcs. |  |  |  | 0
|  | - DN80/DA160 | pcs | 2 |  | 0
6 | 6.1.4. | Delivery and installation of the sealing element (EK) - end cap, at the joint between the pre-insulated pipe and the steel pipe.Calculation per pcs. |  |  |  | 0
|  | - DN80/DA160 | pcs | 2 |  | 0
7 | 6.1.4 | Connecting the newly designed heating pipeline to the existing pipelines (material included in the previous items).Calculation per pcs. |  |  |  | 0
|  | - DN80 | pcs | 2 |  | 0
8 | 6.1.4. | Testing the heating pipeline to pressure, by applying the pressure of 6 bar during 24 hours. During the cold probe, the permitted pressure drop is max. 0.2 bar. |  |  |  | 0
|  | Calculation per running meter of the route. | m | 11 |  | 0
9 | 4 | Electrical works on the heating pipeline, which consist of delivery, installation and electrical connection with signal testing, along with report prepared by the Investor.Calculation per set. |  |  |  | 0
|  | - connecting all electric cables (50mTr) | set | 1 |  | 0
10 | 6.2. | Radiographic testing by the authorized institution. 20% of welded joints (or as directed by the Investor) is being tested. They should be noted, documented and evaluated in the report. Depending on the classification of welded joints, take action according to regulations.Calculation per pcs. |  |  |  | 0
|  | - DN80 | pcs | 1 |  | 0
11 |  | Preparatory and finishing works and transport costs | LS | 1 |  | 0
|  | TOTAL |  |  |  | 0
B |  | CONSTRUCTION WORKS
I |  | PREPARATORY WORKS
1 | 2.3 | Marking the route for the commencement of works. |  |  |  | 0
|  | Calculation per m. | m | 11 |  | 0
2 | 2.3 & 2.4 | Marking and cutting, using machinery, of existing structures of the asphalt concrete road surface, on the location of the heating pipeline passage. |  |  |  | 0
|  | Calculation per m. | m | 11 |  | 0
3 | 2.4 | Dismantling of the sidewalk concrete slabs, with clearing and stacking of slabs for re-installation, with removal of sand and gravel (debris) to the landfill at a distance of up to 10 km. |  |  |  | 0
|  | Calculation per m². | m² | 10 |  | 0
4 | 2.4 | Demolition of a layer of asphalt concrete, total thickness of approximately 5 cm, with transport of debris to the landfill at a distance of up to 10 km. |  |  |  | 0
|  | Calculation per m². | m² | 10 |  | 0
5 | 2.4 | Manual or machine breaking of the part of the concrete canal for rainwater drain. Thickness of the walls and floor up to 15 cm (presumably) in length of about 1 m. |  |  |  | 0
|  | Calculation per m³. | m³ | 1 |  | 0
|  | TOTAL |  |  |  | 0
II |  | EARTHWORKS
1 | 2.5 | Machine trench excavation in II and III category soil. Trench is excavated with proper skew cutting off of the sides. The maximum depth of the excavation is 80 cm starting from the surface of the asphalt. Removal of the material to the city landfill at a distance of up to 10 km. Complete with clearing the trench and .Calculation per m³. |  |  |  | 0
|  | mechanically | m³ | 8 |  | 0
|  | manually | m³ | 2 |  | 0
2 | 2.9 | Supply, transport and spreading of sand in the trench and canal. In the canal, the send is spread around the pipes in the full profile of the canal, and in the trench, min. 10 cm below and above the pipe. Bulking coefficient K=1.10. |  |  |  | 0
|  | Calculation per m³ of filled sand. |  |  |  | 0
|  | sand in the earthen canal | m³ | 4 |  | 0
3 | 2.9 | Supply, transport and backfilling of the trench with gravel-sandy material beneath the asphalt and sidewalks. Perform backfilling up to the level of the bedding, in layers of 20-30 cm, with compaction to the required compactness, min. Me = 60 Mpa. The amount of material provided with the coefficient |  |  |  | 0
|  | Calculation per m³. | m³ | 8 |  | 0
|  | TOTAL |  |  |  | 0
III |  | REPAIRING WORKS
1 | 2.11 | Concreting of the damaged part of the sidewalk and restoring it to the existing condition to the possible extent. |  |  |  | 0
|  | Calculation per m². | m² | 5 |  | 0
2 | 2.11 | Paving of the part of the yard above the trench in the same thickness as before. |  |  |  | 0
|  | Calculation per m². | m² | 8 |  | 0
3 | 2.11 | Concreting of the demolished part of the rainwater canal, and restoring it to the possible extent. |  |  |  | 0
|  | lump sum | LS | 1 |  | 0
|  | TOTAL |  |  |  | 0
IV |  | OTHER WORKS
1 | 6.2. | Supply and placement of strips for marking the heating pipeline route. Tape is placed above each pipe individually in the trench. |  |  |  | 0
|  | Calculation per m. | m | 22 |  | 0
2 | 6.2. | Lowering the groundwater level (if needed), using the technology at Contractor's disposal. Calculation of lowering the level of groundwater is done by hours. It is mandatory that the Supervisor controls and certifies the amount of time spent. |  |  |  | 0
|  | Calculation per hour. | h | 3 |  | 0
3 | 6.2. | Preparatory, finishing, and smaller unforeseen works arising during performing of works on the heating pipeline route. |  |  |  | 0
|  | Calculation based on lump sum. | LS | 0.5 |  | 0
|  | TOTAL |  |  |  | 0
V |  | SECURING THE CONSTRUCTION SITE
1 | 6.2. | Supply, installation and maintenance of protective fence along the route, height 1 m, made of timber and steel profiles and PVC perforated strips in orange; metal pipe joists surrounded by concrete mobile base. |  |  |  | 0
|  | Calculation per m, on both sides. | m | 22 |  | 0
2 | 6.2. | Supply, transport, installation and removal of pedestrian crossings across the trench of the hot water pipeline canal. |  |  |  | 0
|  | Calculation per piece of the crossing. | pcs | 1 |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF CONSTRUCTION WORKS
I |  | PREPARATORY WORKS |  |  |  | 0
II |  | EARTHWORKS |  |  |  | 0
III |  | REPAIRING WORKS |  |  |  | 0
IV |  | OTHER WORKS |  |  |  | 0
V |  | SECURING THE CONSTRUCTION SITE |  |  |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF HEATING PIPELINE FOR THE PEDIATRIC CENTER
A |  | MECHANICAL WORKS |  |  |  | 0
B |  | CONSTRUCTION WORKS |  |  |  | 0
|  | TOTAL |  |  |  | 0
RECAPITULATION OF ALL WORKS ON THE CENTRAL HEATING
|  | MECHANICAL INSTALLATIONS-CENTRAL HEATING |  |  |  | 0
|  | HEATING PIPELINE |  |  |  | 0
|  | HEATING PIPELINE FOR THE PEDIATRIC CENTER |  |  |  | 0
|  | TOTAL |  |  |  | 0
MOBILE FIRE FIGHTING EQUIPMENT
1 | N/A | Supply and installation of handheld devices C9 C6.Calculation per pcs. | pcs | 13 |  | 0
2 | N/A | Supply and installation of handheld devices CO2 5.Calculation per pcs. | pcs | 2 |  | 0
3 | N/A | Supply and installation of handheld devices V=0.4m³.Calculation per pcs. | pcs | 1 |  | 0
|  | TOTAL MOBILE FIRE FIGHTING EQUIPMENT |  |  |  | 0
RECAPITULATION OF ALL WORKS ON THE FACILITY EMERGENCY WARD
0 |  | GENRAL ITEMS |  |  |  | 0
1 |  | CONSTRUCTION AND CONSTUCTION-CRAFT WORKS |  |  |  | 0
2 |  | WATER SUPPLY AND SEWERAGE |  |  |  | 0
3 |  | WORKS ON ELECTRICAL INSTALLATIONS |  |  |  | 0
4 |  | WORKS ON THE CENTRAL HEATING |  |  |  | 0
5 |  | MOBILE FIRE FIGHTING EQUIPMENT |  |  |  | 0
|  | Total amount of the works (EUR) |  |  |  | 0
Contingencies (8,7%) | [5 empty] | 0
TOTAL LUMP-SUM PRICE (EUR) -VAT EXCLUDED | [5 empty] | 0
Name and first name: […………………………………………………………………]
Duly authorised to sign on behalf of:
[………………………………………………………..…………………………...…]
Place and date: […………………………………………………………….………….]
Stamp of the firm/company:
Note on B287: Srdjan: Dao sam opsti opis za PP u novoj tacki cevovodi. Ovde je direktno prepisan katalog nekog proizvodjaca ali ja ne znam dovoljno oo tome da prepoznam da li je opis previse specifican.
Note on B294: Srdjan: Ovde je referenca samo na zastitu cevi jer opis za ovako specificnu stavku ne potoji.
Note on A391: Srdjan: OVDE SAM STAO