## Slide 1: Construction of municipal wastewater collection and treatment system in Čačak Tender Ref. No. NEAR/BEG/2023/EA-OP/0148 Site Visit and Clarification Meeting
17 January 2024
Government of the Republic of Serbia
Ministry of Environmental Protection
Ministry of Finance,
Department for Contracting and Financing of
EU Funded Programmes

## Slide 2: The Works
Part 1: Design and construction of WWTP Prelići with construction of the access road to the WWTP
Part 2: Rehabilitation of sewage pumping stations PS Ljubić Polje, PS Beljina and PS Košutnjak with construction of the access road to the pumping station PS Ljubić Polje
Part 3: Cleaning, CCTV inspection, design and rehabilitation of sewers
Part 4: Supply of sewer cleaning and investigation equipment

## Slide 3: Location of The Works
Čačak WWTP

## Slide 4: Part 1: Design and construction of WWTP Prelići with construction of the access road to the WWTP
Čačak WWTP
Location of the WWTP
1 km east of the town
Bordered by three water courses:
  Atenica River in the West
  Zapadna Morava River in the North
  Trnava River in the East
Cadastral plots 138, 139, 140/1, 140/2, 140/3, 141, 142/1, 142/2, 142/3, 148/1, 148/2 in Atenica
Total area ~ 5,4 ha

## Slide 5: Part 1: Design and construction of WWTP Prelići with construction of the access road to the WWTP
Čačak WWTP
Contract Interfaces
Access road – app. 200 m to the Southeast of onterchange with southern by-pass around Čačak;
New Transformer Station 10/0.4 kV (10 kV cable connection to be installed by Electromreže Čačak);
Water meter at entrance of the WWTP to be installed by PUC;
SCADA – WAN of PUC via internet;
Telephone and Internet connection;
Diversion manhole to divert wastewater from the existing sewer mains DN1200 to the WWTP
Flood protection and treated effluent discharge into the Zapadna Morava river

## Slide 6: Collection Manhole, CSO and Diversion Manhole
Loznica WWTP
Čačak WWTP

## Slide 7: Basic Design Criteria
Loznica WWTP
Čačak WWTP
Wastewater Flows | Phase 1 | Phase 2
Average daily dry weather flow QDWF, m3/d | 22,378 | 26,784
Average daily dry weather flow QDWF, l/s | 259 | 310
Maximum dry weather flow, QMDWF, l/s | 431 | 566
Peak flow QWWF1, l/s | 828 | 1,013
Storm flow QWWF2, l/s | 1,428 | 1,613
WWTP Loads | Phase 1 | Phase 2
Population equivalent | 96,000 | 128,000
Required Effluent Quality | Phase 1 | Phase 2
BOD5 | 25 | 25
COD | 125 | 125
TSS | 35 | 35
TN | 15 | 10
TP | 2 | 1
Effluent disinfection | Y | Y

## Slide 8: Part 1: Scope of Works
1
Design
- Conceptual design of the WWTP (Phase I and Phase II) for obtaining Location Conditions
- Preliminary design of the WWTP to be constructed under this Contract (Phase I)
-EIA update (if necessary)
- Design for Construction Permit
- Design for Construction
- As built design
2
Construction
- WWTP (construction, testing and commissioning, trial operation)
- Access road (based on Employer’s design)
- Flood protection – construction of the embankment along the Atenica river (Q1%) and effluent discharge
3
Tests on Completion and Taking Over
- Pre-commissioning tests
- Commissioning tests
- Trial operation
4
Assisted Operation and Training during DNP (90 days)
- Tests after completion
- Performance Guarantee Tests
- DNP 365 days

## Slide 9: Part 2: Rehabilitation of sewage pumping stations PS Ljubić Polje, PS Beljina and PS Košutnjak with construction of the access road to the pumping station PS Ljubić Polje (based on Employer’s design)
Čačak WWTP
Contract Interfaces
Municipal roads;
Electricity provider’s meter in the 0.4kV distribution board (to be moved as necessary);
Wastewater collection system;
Connection of new pressure pipe from Beljina SPS;
SCADA – WAN of PUC via internet.

## Slide 10: SPS Ljubić Polje
Čačak WWTP
SPS Ljubić Polje | Unit | Value
Q (duty) | l/s | 350
Head | m | Contractor to design

## Slide 11: SPS Beljina
Čačak WWTP
SPS Beljina | Unit | Value
Q (duty) | l/s | 25
Head | m | Contractor to design

## Slide 12: SPS Košutnjak
Čačak WWTP
SPS Košutnjak | Unit | Value
Q (duty) | l/s | 32
Head | m | Contractor to design

## Slide 13: Part 2: Scope of Works
1
Design
- Conceptual and Preliminary designs for SPS Beljina only
- Designs for Construction for all SPSs
- As built design for all SPSs
2
Construction
- SPS Ljubić Polje with access road (based on Employer’s design)
- SPS Beljina (based on Contractor’s design)
- SPS Košutnjak (based on Employer’s design)
3
Tests on Completion and Taking Over
- Pre-commissioning tests
- Commissioning tests
4
DNP
- DNP 365 days

## Slide 14: Part 3: Cleaning, CCTV inspection, design and rehabilitation of sewers (based on Employer’s design)
Čačak WWTP
No. | Street | Depth m | Material
1 | Heroja Đurakića | 3.0-4.0 | Ceramic
2 | Hajduk Veljkova | 4.5-5.0 | Concrete
3 | Veselina Milekica F.Filipovica | 4.5-5.0 | Ceramic
4 | Vojvode Stepe | 4.5-5.0 | Concrete

## Slide 15: Time for Completion(based on Employer’s design)
Čačak WWTP
Activity | Duration
Part 1: Preparation of designs for the construction of the WWTP Prelići (update/adjustments of Employer’s designs, obtaining updated Location Conditions and approval on adjusted Preliminary Design, Design for Construction Permit, Design for Construction) | 365 days from the Commencement Date
Part 3: Completion of CCTV investigations in preparation for sewer rehabilitation | 180 days from the Commencement Date
Part 4: Supply of Sewer Cleaning and Investigation Equipment | 180 days from the Commencement Date
Conceptual design, preliminary design and other design for rehabilitation of sewers | 365 days from the Commencement Date
Time for Completion | 1095 days from the Commencement Date
Defects Notification Period | 365 calendar days from Issue of Taking-Over Certificate
Assisted operation during DNP | 90 days from Issue of Taking-Over Certificate

## Slide 16
Questions

## Slide 17: Thank you
Government of the Republic of Serbia
Ministry of Environmental Protection
Ministry of Finance,
Department for Contracting and Financing of
EU Funded Programmes