LOT 1

VOLUME 3

SECTION 2B

GENERAL TECHNICAL SPECIFICATIONS FOR MECHANICAL WORKS

LOT 1: GENERAL TECHNICAL SPECIFICATION

FOR MECHANICAL WORKS

1	GENERAL DATA	6

1.1	Introduction	6

1.2	Objective of the Works	6

2	GENERAL REQUIREMENTS	7

3	CERTIFICATES	8

4	EXISTING CABLES AND PIPELINES	9

4.1	Authorized Institutions	9

4.2	Information and Instructions	9

4.3	Precautions	9

4.4	List of abbreviations and terms	9

5	STANDARDS AND MATERIALS FOR WORKS	11

5.1	Scope	11

5.2	Adherence to Standards and list of applicable Standards	11

5.3	Standards, Regulations and Engineer’s Approval	20

5.4	Mixture of Standards	21

5.5	Design and Design Life	21

5.6	Design Safety Features	21

5.7	Materials General	22

5.8	Cast Iron	22

5.9	Fastenings, Bolts, Nuts and Washers	23

5.10	Labels	24

5.11	Works Finish	24

5.12	Suppression of Noise	25

5.13	Bearings	25

5.14	Lubrication	25

5.15	Location and Alignment	26

5.16	Flexible Couplings	26

5.17	Standard Gearboxes	26

5.18	Setting of Machinery	27

5.19	Machinery Finish	27

6	SPECIFICATION FOR PROTECTIVE COATING	28

6.1	General	28

6.2	Contractor’s Responsibility	28

6.3	Submissions	28

6.4	Appropriate Standards	29

6.5	Trial Areas and Sample Pieces	30

6.6	Color, Coding, Labels, Arrows	30

6.7	Metal Coatings General	30

6.8	Prefabrication Primers	31

6.9	Surface Preparation by Blasting	31

6.10	Dehumidification Required for Special Purposes	31

6.11	Damage to Works Preparation	31

6.12	Embedded Steel	32

6.13	Preparation and Painting of Works	32

6.14	Steelwork in Locations ‘A’, ‘B’ and ‘C’	32

6.15	Steelwork in Location ‘D’	33

6.16	First Finish Steelwork in Location ‘A’	33

6.17	Final Finish in Locations ‘A’, ‘B’ & ‘C’	34

6.18	Final Finish in Location ‘D’	34

6.19	Galvanized Surfaces	35

6.20	Painting of Welds	35

6.21	Uncoated Surfaces	35

6.22	Repair of Damaged Work	35

6.23	Preparation and Painting of Pipes	36

6.24	Preparation and Painting Metal Parts	36

6.25	Preparation and Painting of Non-Ferrous Parts	36

6.26	Preparation and Painting of Mild Steel Supports	36

6.27	Preparation and Painting of Fastenings	36

6.28	Painting and Protection of Bolted Connections	37

6.29	Overcoating of Bituminous Coatings	37

7	PIPEWORK	38

8	METALWORK	39

8.1	Structural Work	39

8.2	Standards (Steel)	39

8.3	Submissions by the Contractor	39

8.4	Drawings	40

8.5	Calculations	40

8.6	Welding	41

8.7	Identification of Members	41

8.8	Storage and Erection on Site	41

8.9	Bolted Connections in Steel Structures	42

8.10	Crane Beams and Rails	43

8.11	Quality and Testing of Materials	43

8.12	Flooring, Rails and Other Metalwork	43

8.13	Floor Plating	44

8.14	Open Mesh Flooring	44

8.15	Access Covers	44

8.16	Cast Iron Covers and Frames	44

8.17	Surface Boxes	45

8.18	Step Irons	45

8.19	Handrailing	45

8.20	Ladders - general	45

8.21	Steel Ladders	45

8.22	Non-ferrous Ladders	46

8.23	Stairways	46

8.24	Miscellaneous – Dissimilar Metals	46

8.25	Aluminum Fittings	47

8.26	Opening Tools	47

8.27	Protection	47

8.28	Installation	47

9	PUMPING EQUIPMENT	48

9.1	General	48

9.2	Pump Motor	49

9.3	Pump Bearings and Seals	49

9.4	Connecting Flange	49

9.5	Pressure Gauge	49

9.6	Centrifugal Pump	50

9.7	Submersible Pump	51

9.8	Submersible Drainage Pump	52

9.9	Portable Site Drainage Pump	53

9.10	Horizontal Centrifugal Pump	53

9.11	Positive Displacement Pump (Progress cavity pump)	54

9.12	Booster Unit	55

9.13	Macerator	55

10	VALVES	56

10.1	Gate valves	56

10.2	Check valves	57

10.3	Air and gas relief valves	58

10.4	Pressure control valves	58

10.5	Butterfly valves	60

10.6	Dismantling joints	60

10.7	Support of pipeworks and valves	61

11	PENSTOCKS AND HAND STOPS	62

11.1	Penstocks general requirements	62

11.2	Hand stops	63

12	ELECTRICAL ACTUATORS FOR VALVES AND PENSTOCKS	64

13	PRESSURE AND VACUUM GAUGES	65

14	Lifting equipment	66

14.1	General	66

14.2	Travelling cranes	66

14.3	Monorail cranes	67

14.4	Lifting Davit	67

15	Chemical dosing equipment	68

15.1	Chemical dosing	68

15.2	Dosing pump	68

15.3	Transfer pumps	69

15.4	Chemical Pipework	69

15.5	Chemical Valves	69

16	GENERAL EQUIPMENT	70

16.1	Water decanter unit	70

16.2	Filters (cartridge filters) units	70

16.3	Reverse osmosis (RO) units	71

16.4	Coalescence separators	71

16.5	Air compressor units	71

16.6	Lobe-type air blowers	72

16.7	Centrifugal blowers	73

16.8	Positive displacement rotary screw blowers	74

16.9	Ventilators	75

16.10	Jet aerators	75

16.11	Mixers	76

16.12	Vertical aerators	76

16.13	Compressed Air Aeration	78

16.14	Membrane diffusers	78

16.15	Upgrade of existing sorting line	78

16.16	New sorting line	79

16.17	Bag opener/shredder	79

16.18	Disc separator	80

16.19	Permanent belt magnet with steel support	81

16.20	Sorting cabin	81

16.21	Boxes with conveyers for separated raw materials discharging	81

16.22	MBT-Bio-drying plant	82

16.23	MBT-RDF preparation plant	84

16.24	MBT-Biogas plant	84

16.25	Wheel washing equipment	89

16.26	Spraying guns	90

16.27	Screw Conveyor	90

16.28	Belt Conveyor	90

16.29	Chain Belt Conveyor	91

16.30	Slide roller belt Conveyor	91

16.31	Sorting belt conveyor and sorting platform	92

16.32	Container	92

16.33	Rotostrainer	92

16.34	Heating plant	93

16.35	Weighbridge	94

17	SPARE PARTS	95

# GENERAL DATA

## Introduction

These Specifications are to be read in conjunction with the rest of Volume 3 and in particular with the Employer’s Requirements.

## Objective of the Works

The main objective of this Contract is design and construction of Regional Waste Management Centre (RWMC) in the City of Novi Sad, in order to establish a long-term sustainable regional waste management system.

# GENERAL REQUIREMENTS

The Works shall consist of newly manufactured materials only. In selecting materials, which differ on the electrolytic scale, the dangers of these being in close proximity shall be addressed by the Contractor in his design and suitable preventive measures taken.

Each item of Works shall bear, in an easily readable position, an identification plate with text in Serbian and English language stating the name of the manufacturer, year of manufacture and type and serial numbers.

Pipelines shall be identified with flow arrows at entry and exits of machines and pump stations together with a color identification bands. The Contractor shall provide marking proposal to the Engineer with details for approval. Top finish color coats shall be determined in agreement with the Engineer. Color samples shall be submitted if so required.

The Contractor is liable for the first fill of oil and grease for all mechanical Works and equipment.

Lifting equipment shall be provided for all Works items over 50 kg (where not under the lift area of overhead cranes specified elsewhere).

Where the Contractor includes bought-in manufactured items, then full details shall be submitted to the Engineer for approval prior to incorporation in the works.

# CERTIFICATES

Certificate suppliers will be approved, only. All manufacturers shall be certified in accordance with ISO 9001.

The electro-mechanical equipment (MEICA) must be provided with the certification “CE” in accordance to Machinery Directive 98/37/EEC, in particular the following directives shall be considered:

- Directive 2006/42/EC on Machinery, amended by Regulation (EC) No 596/2009, Directive 2009/127/EC, Regulation (EU) No 167/2013, Directive 2014/33/EU and Regulation (EU) No 2019/1243

- Directive 2014/35/EU on the harmonization of the laws of the Member States relating to the making available on the market of electrical equipment designed for use within certain voltage limits (recast)

- Directive 2014/30/EU on the harmonization of the laws of the Member States relating to electromagnetic compatibility (recast)

- And others as required by Directive 2006/42/EC on Machinery, amended by Regulation (EC) No 596/2009, Directive 2009/127/EC, Regulation (EU) No 167/2013, Directive 2014/33/EU and Regulation (EU) No 2019/1243.

In addition, the following documentation shall be included for each individual machine and/or apparatus:

- Certificate of Conformity in acc. to EN 10204/2.1

- Manufacturers Test Certificate in acc. to EN 10204/2.22

- Manufacturers Work’s Test Certificate in acc. to EN 10204/2.3

All certificates are subject to approval from the Engineer. Expenditures for certification of equipment are to be included in the Contractor’s prices.

# EXISTING CABLES AND PIPELINES

## Authorized Institutions

The Authorities are public institutions responsible for the public utility services of electricity, water, sewerage, drainage, gas, telephone or other telecommunication facilities and roads.

## Information and Instructions

Further information and instructions on measures to be taken before and during the execution of the Works will, to the extent known to the Authorities, be submitted to the Contractor by the Employer/Investor or the Engineer in co-operation with the relevant Authorities.

As soon as a service pipeline, cable or any other installation is encountered in the excavation whether previously located or discovered during the course of the excavation for the works the Contractor shall immediately inform the Engineer who will then inform the Authorities concerned. In urgent cases the Contractor shall inform the relevant Authority directly in absent of the Engineer.

In this case, the Contractor shall follow the instructions given by the Employer/Investor, the Engineer or the relevant Authorities. If necessary, precautions shall be taken by the Contractor to protect the systems during the execution of the works.

## Precautions

No excavating machines shall be used in the immediate surroundings of cables and/or pipelines unless approved by the Engineer.

Special care shall be taken to ensure that the existing facilities are accessible in the case of an emergency.

Temporary Works, which have to be made in the vicinity of the existing facilities during the execution of the Works shall be maintained by the Contractor and shall be removed as soon as practicable.

The Contractor shall be responsible for maintaining all such utilities encountered by him in the construction of the Works and shall bear the cost of making good any damage caused directly by his activities.

## List of abbreviations and terms

| Abbreviation | shall mean: |
| --- | --- |
| % | per cent |
| c | centre |
| CA | Contracting Authority |
| Day | Calendar Day |
| DCP | Design for Construction Permit (Projekat za gradjevinsku dozvolu) |
| DE | Design for Execution (Projekat za izvodjenje) |
| DIN | German Standard |
| DN | nominal diameter |
| EN | European Standard |
| FFL | Final floor level |
| h | hour |
| HDPE | High density extruded polyethylene |
| ISO | International Standards Organization |
| kg | kilogram |
| km | kilometer |
| kW | kilo Watt (1,000 Watts) |
| l | liter |
| L.S. | lump sum |
| m | meter |
| m/d | man-day |
| m² | square meter |
| m³ | cubic meter |
| masl | meters above see level |
| mm | milimeter |
| mm² | square milimeter |
| Month | 30/31 Calendar Days |
| MSDS | Material Safety Data Sheet |
| pcs | pieces |
| PD | Preliminary Design |
| PE | Population Equivalent |
| PM | Project Manager |
| PVC | Polyvinyl chloride |
| QAS | Quality Assurance System |
| RC | Reinforced Concrete |
| t | tone (1,000 kg) |
| TA | Technical Assistant |
| ER | Employer’s Requirements |
| GTS | General Technical Specification |
| TR | Technical Requirements (= ER + GTS) |

# STANDARDS AND MATERIALS FOR WORKS

## Scope

This part of the Specification sets out the general standards of design and materials to be supplied and the work to be carried out by the Contractor in connection with Works. Mention of any specific material or Works does not necessarily imply that such is to be included in the Works.

All component parts of works, the installations and the “supply” shall, unless otherwise specified, comply with the General Provisions. Where very detailed requirements are expressed in other parts of the requirements, they shall take precedence over the requirements of this part.

The names of the manufacturers of materials and equipment proposed for incorporation in the Works together with performances, capacities, certified test reports and similar information, shall be furnished at the times specified in these TR or when requested by the Engineer, who shall have power to reject any parts which (in his opinion) are unsatisfactory or not in compliance with the Specification.

## Adherence to Standards and list of applicable Standards

Wherever in the Employer’s Requirements and General Technical Specifications is referred to specific standards and codes to be met by the materials, plant and other supplies to be furnished, and work performed or tested, the provisions of the latest current edition or revision of the relevant standards and codes in effect shall apply, unless otherwise expressly stated in these documents. Where such standards and codes are national, or relate to a particular country or region, other authoritative standards which ensure a substantially equal or higher performance than the standards and codes specified will be accepted subject to Engineer’s prior review and written approval. Differences between the standards specified and the proposed alternative standards must be fully described in writing by the Contractor and submitted to the Engineer at least twenty-eight (28) days prior to the date when the Contractor need the Engineer’s approval. In the event the Engineer determines that such proposed deviations do not ensure substantially equal performance, the Contractor shall comply with the standards specified in the documents.

The conditions specified in these general specifications are minimum requirements for all deliveries and performances. If special requirements are given for particular items, they apply only to these particular items. The Contractor shall propose Standards for the execution of the works, which shall be approved by the Engineer. A list of Standards is included in these GTS.

In referring to the Standard Specifications the following abbreviations are used:

| ATV | Abwasser Technische Vereinigung - German Association for Water, Wastewater and Waste, see DWA |
| --- | --- |
| CEE | International Commission of Rules for the Approval of Electrical Equipment |
| DIN | Deutsches Institut für Normung e.V. - German Institute for Standardisation |
| DVGW | Deutsche Vereinigung des Gas- und Wasserfachs e.V. - The German technical and scientific organisation on Gas and Water |
| DWA | Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall - German Association for Water, Wastewater and Waste (former ATV) |
| EN | European Standards |
| IEC | International Electrotechnical Commission |
| ISO | International Organization for Standardization |
| SRPS EN | Serbian standards harmonized with EN |
| UVV | Unfall-Verhütungs-Vorschriften (Regulations of Accident Prevention) |
| VDE | Verband Deutscher Elektrotechniker – German Association for Electrical, Electronic & Information Technologies |

The applicable standards are listed below, but they are not limited to the following:

| - SRPS EN 12255 | Wastewater treatment plants |  |  |
| --- | --- | --- | --- |
| - DIN 19569 | Wastewater treatment plants - Principles for the design of structures and technical equipment |  |  |
| - DIN 19558 | Wastewater treatment plants - Outlet installations, weir and scum baffle, submerged effluent pipes in tanks - Construction principles, main dimensions, layout |  |  |
| - SRPS EN 805 | Water supply - Requirements for systems and components outside buildings |  |  |
| - SRPS EN 806 | Specifications for installations inside buildings conveying water for human consumption |  |  |
| - SRPS EN 1610 | Construction and testing of drains and sewers |  |  |
| - ATV-DVWK-A 127 | Rules and standards for the static calculation of sewage pipes and pipelines. |  |  |
| - ATV-DVWK-A 134 | Planning and Construction of Wastewater Pumping Stations, June 2000. |  |  |
| - ATV-DVWK-M 265E |  | Regulation of Oxygen Transfer with the Activated Sludge Process, ed. March 2000. |  |
| - ATV - M 204E |  | Status and Application of Emission Reduction Technology with Sewage Treatment Plants - Odours, Aerosols, ed. October 1996. |  |
| - ATV-DVWK-A 199-1E |  | Service and Operating Instructions for the Personnel of Wastewater Systems Part 1: Service Instructions for the Personnel of Wastewater Systems, ed. July 2002. |  |
| - ATV-DVWK-A 199-2E |  | Service and Operating Instructions for the Personnel of Wastewater Systems Part 2: Operating Instructions for the Personnel of Sewerage Systems and Stormwater Treatment Systems, ed. July 2007. |  |
| - ATV-DVWK-A 199-3E |  | Service and Operating Instructions for the Personnel of Wastewater Systems Part 3: Operating Instructions for the Personnel of Wastewater Pumping Installations, ed. June 2007. |  |
| - ATV-DVWK-A 199-4E |  | Service and Operating Instructions for the Personnel of Wastewater Systems Part 4: Operating Instructions for the Personnel of Wastewater Treatment Plants, August 2006. |  |
| - SRPS EN 253 | District heating pipes - Preinsulated bonded pipe systems for directly buried hot water networks - Pipe assembly of steel service pipe, polyurethane thermal insulation and outer casing of polyethylene |  |  |
| - SRPS EN 476 | General requirements for components used in drains and sewers |  |  |

Steel Names and QC standards

- SRPS EN 10027	 	Steel names and numbers

- SRPS EN 10204 		Metallic products - Types of inspection documents

- SRPS EN 10088-1 	Stainless steels - Part 1: List of stainless steels

- SRPS EN 10088-2 to 5 	Stainless steels: Technical delivery conditions

Equipment and Parts

- SRPS EN 1012	 	Compressors and vacuum pumps - Safety requirements

- SRPS EN ISO 2151 	Acoustics - Noise test code for compressors and vacuum pumps –

Engineering method (Grade 2)

- ISO 3857-2 		Compressors, pneumatic tools and machines - Vocabulary - Part 2: Compressors

- ISO 5388 		Stationary air compressors - Safety rules and code of practice

- SRPS M.F3.150	 	Stationary air compressors - Safety rules and code of practice

- SRPS EN ISO 9906 	Rotodynamic pumps - Hydraulic performance acceptance tests –

Grades 1, 2 and 3

- SRPS EN 14492	 	Cranes - Power driven winches and hoists

- SRPS EN 13135	 	Cranes - Safety - Design - Requirements for equipment

- SRPS EN 13157	 	Cranes - Safety - Hand powered cranes

- DIN 15020	 	Lifting Appliances; Principles Relating to Rope Drives; Calculation and

Construction

- SRPS EN 837	 	Pressure gauges

- SRPS EN 840 		Mobile waste and recycling containers

- DIN 30720 		Containers

- SRPS EN 10028	 	Flat products made of steels for pressure purposes

- SRPS EN 10222	 	Steel forgings for pressure purposes

• 	SRPS EN 10250	 	Open die steel forgings for general engineering purposes

• 	SRPS EN 10272 		Stainless steel bars for pressure purposes

Covers, Step Irons, Ladders

•	SRPS EN 124 		Gully tops and manhole tops for vehicular and pedestrian areas – Design

requirements, type testing, marking, quality control

•	DIN 1229 		Gully tops and manhole tops for vehicular and pedestrian areas – Mass

per unit area and pull-out force

•	DIN 1211 		Step irons for staggered manhole steps

•	DIN 1212 		Step irons with upstand for staggered manhole steps

•	SRPS EN 13101		Steps for underground man entry chambers - Requirements, marking,

testing  and evaluation of conformity

- DIN V 1264  		Steps for underground man entry chambers - Application in

construction works for wastewater disposal

- DIN 19555  		Step irons for straight manhole steps in in-situ concrete manholes

- SRPS EN 14396 		Fixed ladders for manholes

- DIN 3580 		Surface boxes and ground plates; requirements and testing; DVGW code

of practice

Steel Pipes

- SRPS EN 10216 		Seamlesss steel tubes for pressure purposes - Technical delivery

conditions

- SRPS EN 10224 		Non-alloy steel tubes and fittings for the conveyance of aqueous liquids

including water for human consumption - Technical delivery conditions

- SRPS EN 10296 		Welded circular steel tubes for mechanical and general engineering

purposes - Technical delivery conditions

- SRPS EN 10297 		Seamless circular steel tubes for mechanical and general engineering

purposes - Technical delivery conditions.

- SRPS EN 10255 		Non-Alloy steel tubes suitable for welding and threading – Technical

delivery conditions

- SRPS EN 10220 		Seamless and welded steel tubes - Dimensions and masses per unit

length

- DIN 2460 		Steel water pipes and fittings

- SRPS EN 10216 		Seamless steel tubes for pressure purposes - Technical delivery

conditions

- SRPS EN 10217 		Welded steel tubes for pressure purposes - Technical delivery conditions

- SRPS EN 10226 		Pipe threads where pressure tight joints are made on the threads

- SRPS EN ISO 3183 	Petroleum and natural gas industries - Steel pipe for pipeline

transportation systems

- SRPS EN 10311 		Joints for the connection of steel tubes and fittings for the conveyance

of water and other aqueous liquids

Fittings

- SRPS EN 10241 		Steel threaded pipe fittings

- SRPS EN 10253		Butt-welding pipe fittings

Material Tests

- SRPS EN ISO 6892 	Metallic materials - Tensile testing

- SRPS EN ISO 6506 	Metallic materials - Brinell hardness test

- SRPS EN ISO 6508 	Metallic materials - Rockwell hardness test

- SRPS EN ISO 8491 	Metallic materials - Tube (in full section) - Bend test

Corrosion Protection

- SRPS EN ISO 12944-1 ‘til Part 8 Paints and varnishes - Corrosion protection of steel structures by

protective paint systems

- SRPS EN ISO 14916 	Thermal spraying - Determination of tensile adhesive strength

- SRPS EN ISO 1461 	Hot dip galvanized coatings on fabricated iron and steel articles –

Specifications and test methods (ISO 1461:2009)

- SRPS EN ISO 2063  	Thermal spraying - Metallic and other inorganic coatings - Zinc,

aluminum and their alloys

- SRPS EN 10240	 	Internal and/or external protective coatings for steel tubes –

Specification for hot dip galvanized coatings applied in automatic plants

- SRPS EN 13144	 	Metallic and other inorganic coatings - Method for quantitative

measurement of adhesion by tensile test

- SRPS EN 10298	 	Steel tubes and fittings for on shore and offshore pipelines – Internal

lining with cement mortar

- SRPS EN 545 		Ductile iron pipes, fittings, accessories and their joints for water

pipelines - Requirements and test methods

- DIN 2880 		Cement mortar inside lining for ductile cast iron and steel pipes and

fittings, application

- DIN 30670 		Polyethylene coatings of steel pipes and fittings - Requirements and

testing

- DIN 30675 		External corrosion protection of buried pipes; corrosion protection

systems for steel pipes

- SRPS EN 10288 		Steel tubes and fittings for onshore and offshore pipelines - External two

layer extruded polyethylene-based coatings

- SRPS EN 10289 		Steel tubes and fittings for onshore and offshore pipelines – External

liquid applied epoxy and epoxy-modified coatings

- SRPS EN 10290 		Steel tubes and fittings for onshore and offshore pipelines – External

liquid applied polyurethane and polyurethane-modified coatings

- SRPS EN 10300 		Steel tubes and fittings for onshore and offshore pipelines – Bituminous

hot applied materials for external coating

- SRPS EN 10310 		Steel tubes and fittings for onshore and offshore pipelines - Internal and

external polyamide powder-based coatings

- SRPS EN ISO 21809-3	Petroleum and natural gas industries – External coatings for buried or

submerged pipelines used in pipeline transportation systems – Part 3: field joint coating

Welding General

- DIN 1910 		Welding and allied processes - Vocabulary - Part 100: Metal welding

processes with additions to DIN EN 14610

- SRPS EN 14610 		Welding and allied processes - Definitions of metal welding processes

- SRPS EN ISO 9606 	Qualification test of welders - Fusion welding

- API 1104 		Welding of Pipelines and Related Facilities

- SRPS EN ISO 15607  	Specification and qualification of welding procedures for metallic

materials - General rules

- SRPS EN ISO 14731 	Welding coordination - Tasks and responsibilities

- SRPS EN ISO 3834 	Quality requirements for fusion welding of metallic materials

- SRPS EN 1011-1 	Welding - Recommendations for welding of metallic materials - Part 1:

General guidance for arc welding

- SRPS EN ISO 4063 	Welding and allied processes - Nomenclature of processes and reference

numbers

- SRPS EN ISO 5817 	Welding - Fusion-welded joints in steel, nickel, titanium and their alloys

(beam welding excluded) - Quality levels for imperfections

- SRPS EN ISO 9692 	Welding and allied processes - Recommendations for joint preparation

Welding Consumables

- SRPS EN ISO 2560 	Welding consumables - Covered electrodes for manual metal arc

welding of non-alloy and fine grain steels - Classification

- SRPS EN ISO 14341 	Welding consumables - Wire electrodes and deposits for gas shielded

metal arc welding of non-alloy and fine grain steels - Classification

- SRPS EN ISO 14171 	Welding consumables

- SRPS EN ISO 18275 	Welding consumables - Covered electrodes for manual metal arc

welding of high-strength steels

- SRPS EN ISO 17632 	Welding consumables - Tubular cored electrodes for gas shielded and

non-gas shielded metal arc welding of non-alloy and fine grain steels

- SRPS EN ISO 544 	Welding consumables - Technical delivery conditions for filler materials

and fluxes - Type of product, dimensions, tolerances and markings

- SRPS EN ISO 14174 	Welding consumables - Fluxes for submerged arc welding and

electroslag welding

- SRPS EN ISO 636 	Welding consumables - Rods, wires and deposits for tungsten inert gas

welding of non-alloy and fine-grain steels

- SRPS EN 12074 		Welding consumables - Quality requirements for manufacture, supply

and distribution of consumables for welding and allied processes

- SRPS EN ISO 20378 	Welding consumables - Rods for gas welding of non-alloy and creep-

resisting steels – Classification

Welding Tests

- SRPS EN ISO 4136 	Destructive tests on welds in metallic materials - Transverse tensile test

- SRPS EN ISO 5173 	Destructive tests on welds in metallic materials - Bend tests

- SRPS EN ISO 17637 	Non-destructive testing of welds - Visual testing of fusion-welded joints

- SRPS EN ISO 23277 	Non-destructive testing of welds - Penetrant testing of welds –

Acceptance levels

- SRPS EN ISO 3452 	Non-destructive testing - Penetrant testing

- SRPS EN ISO 17638 	Non-destructive testing of welds - Magnetic particle testing

- SRPS EN ISO 23278 	Non-destructive testing of welds - Magnetic particle testing of welds –

Acceptance levels

- SRPS EN ISO 17636 	Non-destructive testing of welds – Radiographic testing

- SRPS EN ISO 17643 	Non-destructive examination of welds - Eddy current examination of

welds by complex plane analysis

- SRPS EN ISO 11666 	Non-destructive testing of welds - Ultrasonic testing - Acceptance levels

- SRPS EN ISO 23279 	Non-destructive testing of welds - Ultrasonic testing – Characterization

of discontinuities in welds

- SRPS EN ISO 17640 	Non-destructive testing of welds - Ultrasonic testing - Techniques,

testing levels, and assessment

- SRPS EN ISO 10893 	Non-destructive testing of steel tubes

- SRPS EN ISO 17635 	Non-destructive testing of welds - General rules for metallic materials

- DIN EN ISO 10675  	Non-destructive testing of welds - Acceptance levels for radiographic

testing

Stainless Steel Pipes

- SRPS EN ISO 1127 	Stainless steel tubes - Dimensions, tolerances and conventional masses per unit length

- SRPS EN ISO 14175 	Welding consumables - Gases and gas mixtures for fusion welding and

allied processe

- SRPS EN ISO 3506 	Mechanical properties of corrosion-resistant stainless steel fasteners

- SRPS EN 10027 		Designation systems for steels

- SRPS EN 10305 		Steel tubes for precision applications - Technical delivery conditions

- SRPS EN ISO 14343 	Welding consumables - Wire electrodes, strip electrodes, wires and rods

for arc welding of stainless and heat resisting steels – Classification

- SRPS EN 10312 		Welded stainless steel tubes for the conveyance of water and other

aqueous liquids - Technical delivery conditions

- SRPS EN 10297 		Seamless circular steel tubes for mechanical and general engineering

purposes - Technical delivery conditions

Ductil Iron Pipes

- SRPS EN 545 		Ductile iron pipes, fittings, accessories and their joints for water

pipelines - Requirements and test methods

- SRPS EN 598+A1 	Ductile iron pipes, fittings, accessories and their joints for sewerage

applications - Requirements and test methods

- SRPS CEN/TR 16017  	Guide to the use of EN 598

- SRPS EN 969 		Ductile iron pipes, fittings, accessories and their joints for gas pipelines –

Requirements and test methods

- DIN 2880 		Cement mortar inside lining for ductile cast iron and steel pipes and

fittings, application

- ISO 8179 		Ductile iron pipes - External zinc-based coating

- ISO 4179 		Ductile iron pipes and fittings for pressure and non-pressure pipelines –

Cement mortar lining

Plastics piping systems

- SRPS EN ISO 12162 	Thermoplastics materials for pipes and fittings for pressure applications

- Classification, designation and design coefficient

- SRPS EN ISO 9969 	Thermoplastics pipes - Determination of ring stiffness

- ISO 161 		Thermoplastics pipes for the conveyance of fluids

- SRPS EN 13476-1 	Plastics piping systems for non-pressure underground drainage and

sewerage - Structured-wall piping systems of unplasticized polyvinyl

chloride (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 1:

General requirements and performance characteristics

- SRPS EN 13476-2 	Plastics piping systems for non-pressure underground drainage and

sewerage - Structured-wall piping systems of unplasticized polyvinyl

chloride (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 2: Specifications for pipes and fittings with smooth internal and external surface and the system, Type A

- SRPS EN 13476-3 	Plastics piping systems for non-pressure underground drainage and

sewerage - Structured-wall piping systems of unplasticized polyvinyl chloride (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 3: Specifications for pipes and fittings with smooth internal and profiled external surface and the system, Type B

- SRPS EN 13598-1 	Plastics piping systems for non-pressure underground drainage and

sewerage - Unplasticized polyvinyl chloride (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 1: Specifications for ancillary fittings including shallow inspection chambers

- SRPS EN 13598-2 	Plastics piping systems for non-pressure underground drainage and

sewerage - Unplasticized polyvinyl chlorid (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 2: Specifications for manholes and inspection chambers

uPVC Pipes

- DIN 1187 		Unplasticized polyvinyl chloride (PVC-U) drainpipes; Dimesions,

requirements, testing

- SRPS EN ISO 1452 	Plastics piping systems for water supply and for buried and above-

ground drainage and sewerage under pressure - Unplasticized polyvinyl chloride (PVC-U)

- SRPS EN 1401-1 	Plastics piping systems for non-pressure underground drainage and

sewerage - Unplasticized polyvinyl chloride (PVC-U) - Part 1: Specifications for pipes, fittings and the system

- ISO 1452-3 		Plastics piping systems for water supply and for buried and above-

ground drainage and sewerage under pressure - Unplasticized polyvinyl chloride (PVC-U) – Part 3: Fittings

PE Pipes

- DIN 8074 		Polyethylene (PE) - Pipes PE 80, PE 100 – Dimensions

- DIN 8075 		Polyethylene (PE) pipes - PE 80, PE 100 - General quality requirements,

testing

- SRPS EN 1519 		Plastics piping systems for soil and waste discharge (low and high

temperature) within the building structure - Polyethylene (PE)

- SRPS EN 12201 		Plastics piping systems for water supply, and for drainage and sewerage

under pressure - Polyethylene (PE)

- SRPS CEN ISO/TS 15875 Plastics piping systems for hot and cold water installations – Crosslinked

polyethylene (PE-X)

- SRPS EN 12666 		Plastics piping systems for non-pressure underground drainage and

sewerage - Polyethylene (PE)

- SRPS EN 1555 		Plastics piping systems for the supply of gaseous fuels – Polyethylene

(PE)

GRP Pipes

- SRPS EN ISO 23856 	Plastics piping systems for pressure amd non-pressure water supply,

drainage or sewerage - Glass-reinforced thermosetting plastics (GRP) systems based on unsaturated polyester (UP) resin

- DIN 16868 		Glass fibre reinforced unsaturated polyester resin (UP-GF) pipes

- SRPS CEN/TS 14578 	Plastics piping systems for water supply or drainage and sewerage –

Glass-reinforced thermosetting plastics (GRP) based on unsaturated polyester resin (UP) - Recommended practice for installation

Flanges

- SRPS EN 1092-1 	Flanges and their joints - Circular flanges for pipes, valves, fittings and

accessories, PN designated - Part 1: Steel flanges

- SRPS EN 1092-2 	Flanges and their joints - Circular flanges for pipes, valves, fittings and

accessories, PN designated - Part 2: Cast iron flanges

- SRPS EN 1092-3 	Flanges and their joints - Circular flanges for pipes, valves, fittings and

accessories, PN designated - Part 3: Copper alloy flanges

- SRPS EN 1092-4 	Flanges and their joints - Circular flanges for pipes, valves, fittings and

accessories, PN designated - Part 4: Aluminium alloy flanges

- SRPS EN 1514 		Flanges and their joints - Dimensions of gaskets for PN-designated

flanges

- SRPS EN 1591 		Flanges and their joints - Design rules for gasketed circular flange

connections

- SRPS EN 681 		Elastomeric seals - Materials requirements for pipe joint seals used in

water and drainage applications

Valves

- SRPS EN 558  		Industrial valves - Face-to-face and centre-to-face dimensions of metal

valves for use in flanged pipe systems - PN and Class designated valves

- SRPS EN 1984 		Industrial valves - Steel gate valves

- SRPS EN 1171 		Industrial valves - Cast iron gate valves

- SRPS EN 593 		Industrial valves - Metallic butterfly valves

- SRPS EN 19 		Industrial valves - Marking of metallic valves

Copies of the standards shall be available any time for the Engineer. If the Engineer requires an English translation of any of the Standards or Manuals the Contractor shall provide a typed copy of the translation within 7 days of receiving a written request from the Engineer.

## Standards, Regulations and Engineer’s Approval

The design, workmanship, materials, strength and dimensions of all parts shall be to the satisfaction of the Engineer and shall comply with one or more of the standards, as mentioned above.

Where no standards are stated in the Contract, all materials, components, equipment, workmanship and tests for which DIN or their acceptable equivalents have been issued, shall be in accordance with such standards.

The electrical installations shall comply with and be tested in accordance with national or internationally recognized regulations or codes of practice subject to any specific requirements of the local electricity supply authority.

Material and equipment supplied and work performed shall comply with these standards and regulations as a minimum. Where manufacturers offer equipment to other standards, the standards shall be equal or superior to those specified and full details of the difference shall be supplied to the Engineer if requested.

Where the design or choice of materials or Works is affected by Statutory Safety Acts, then the materials and works supplied shall comply with all relevant sections of those acts even though no particular reference may be made in the Specification.

## Mixture of Standards

The Contractor should note that the Engineer will not approve of any complete system incorporating component parts and design standards to different Serbian Standards unless the entire system has been designed to function as a whole within the standards and design codes laid down by only one of the approved authorities.

## Design and Design Life

The Contractor shall design the Works in accordance with the TR and to the satisfaction of the Engineer. The design of works shall be in accordance with good modern practice and shall be such as will facilitate operation, inspection, cleaning, lubrication and repair to ensure long life and satisfactory operation under all service conditions. The Contractor’s design calculations shall be submitted to the Engineer as required.

Works shall be designed for a long reliable operating life and shall be suitable for 24 hours per day continuous operation for prolonged periods in the applying climatic conditions and with a minimum of maintenance.

The Contractor may be called to demonstrate this for any component, either by the service record or evidence of similar equipment already installed elsewhere or by records of relevant type tests.

Wherever possible works shall be designed and arranged so that the degree of skill required maintaining and servicing the works shall be minimal. Except for consumable items such as carbon brushes and the like, which normally require more frequent replacement, no part subject to wear shall have a design life from new to replacement or repair of less than five years of continuous normal operation and where major dismantling is required to replace a part, the life of such parts shall not be less than ten years.

The works shall be designed for the prevention of corrosion, entry of insects and vermin, entry of dirt and dust, and to minimize risk and damage in the event of a fire. Works shall operate without undue vibration and parts shall be designed to withstand the maximum stresses under the most severe conditions of normal service after loss due to any corrosion allowance, or the specified test condition including any corrosion allowance.

Works shall be designed so that when operating at the normal condition, the intensity of emitted noise in the working environment shall not constitute a health hazard to operators and other personnel or cause a nuisance outside the boundary of the works. The anticipated noise characteristics of all items of works and systems, which have high noise potential, shall be submitted to the Engineer early in the design stage of the Contract.

The Contractor shall ensure that all pollutants are discharged from the works in a controlled and safe manner.

## Design Safety Features

Works, as designed and installed, shall have no feature that could be a hazard to operators, maintenance staff, visitors or other persons having access thereto. Guard electrical safety devices, thermal insulation, noise suppression devices, written notices, safety covers, lifebelt and similar, shall be provided where needed.

Adequate safeguards shall be provided to prevent personnel accidentally coming into contact with dangerous machinery mechanisms, hot surfaces, electrically live parts and any other hazardous components or contents.

Emergency stop devices shall be provided and positioned adjacent to all driven works which:

- Involves a risk of injury to personnel during normal and maintenance operations;

- Handles high pressure fluid or dangerous chemicals;

- Is located at a distance of more than five meters from its controller;

- Has no direct, unimpeded access between the controller and the item of controlled works, irrespective of distance.

Secure and substantial guards shall be supplied throughout the installation to cover drive mechanisms. All rotating and reciprocating parts, drive belts, etc. shall be shrouded to removable for gaining access to the works without the need to first remove or displace any major item of works; and they should also allow for adequate ventilation.

Guards shall not have to be removed during normal operation running maintenance and routine inspections and shall be designed to prevent access of fingers to the moving parts.

## Materials General

Works and any component parts thereof shall be made of new materials of suitable grade, quality and strength, protected where appropriate for the operating conditions and the working and climatic environments.

Where there is slight relative motion of two materials to contact, one or both being metals, suitable precautions shall be taken, to prevent damage by friction.

Materials shall have a high resistance to any change in their properties due to the passage of time, exposure to light or any other cause, which may have a detrimental effect upon the performance or life of the works.

Where dissimilar materials in contact or proximity can be bridged by an electrolyte producing a corrosive condition, the Contractor shall demonstrate to the satisfaction of the Engineer those adequate precautions have been taken to prevent corrosion.

Where brass and bronze are to be used in environments where “de-zincification” or “de-aluminification” may occur, suitable inhibitors to prevent this type of attack shall be incorporated.

## Cast Iron

All castings supplied shall be to the appropriate grade. No plugging, filling, welding or “burning on” will be acceptable.

The structure of the castings shall be homogenous and free from non-metallic inclusions and other injurious defects. Surfaces of castings, which are not machined, shall be smooth and shall be carefully fettled to remove all foundry irregularities.

Non-destructive tests will be required for any casting containing defects whose extent cannot otherwise be judged.

## Fastenings, Bolts, Nuts and Washers

Bolts for fixing metal work other than works to concrete brickwork or block work shall be of the following types:

- For fixings into drilled holes in horizontal, vertical and inclined surfaces, approved proprietary epoxy resin fixed bolts shall be used. The epoxy resin shall be a quick setting formulation, supplied in suitable pre-measurement sachets to separate the components until punctured in the hole and mixed by rotation of the fixing bolt. The resin and bolts shall be used in accordance with the manufacturer’s instructions. When fixed, the resin shall completely fill the space between the bolt and the hole to the surfaces of the concrete, brickwork or block work.

- Alternative to a), approved mechanical expansive type bolts may be supplied for fixing to concrete surface inside buildings above ground level where the application proposed by the Contractor is approved by the Engineer. Expansion bolts shall not be used inside liquid retaining structures, in chambers, basements and similar locations below ground level, in exterior locations, nor in any block work or brickwork.

- Fixing into horizontal upward facing surfaces in concrete, by grouting using cement based grout or mortar into preformed, drilled or cut pockets, stainless foundation bolts may be used.

- Screws and approved fixing plugs may be approved for use in some applications.

- The Contractor shall submit details of his proposed type of resin fixed and mechanical expansion bolts for the approval.

- The materials used for fixings, anchors, bolts, nuts, studs and washers and other demountable fastenings in the works shall be in accordance with the following:

- Unpainted stainless steel in the following circumstances:

- Where specifically specified;

- For all fastenings and fixing connections or holding galvanized or aluminum alloy parts;

- In locations liable to high humidity, or condensation or total, partial or intermittent submergence in corrosive liquid.

Otherwise, general holding-down bolts, nuts, washers, anchor plates, and self-drill anchor fittings shall be bright steel galvanized, and all exposed surfaces painted after assembly and tightening.

Fastenings, except high tensile, of all ferrous parts shall be steel prepared and galvanized or sherardized, primed and painted in accordance with the Protective Coating Specification. Electro-galvanizing, nickel, cadmium or any other plating process except chromium plating, will not be acceptable.

All exposed bolt-heads and nuts shall be hexagonal and the length of all bolts shall be such that when fitted with a nut and tightened down the threaded portion shall fill the nut and not protrude from the face thereof by more than half a diameter in the fully tightened condition.

PTFE (polytetrafluoroethylene) washers shall be fitted beneath bolt-head and nut when fastening parts of different materials, i.e. mild steel and stainless steel or aluminum.

Fitted bolts shall be a light driving fit in the reamed hole they occupy, shall have the screwed portion of the diameter such that it will not be damaged or cause damage in driving and shall be marked in a conspicuous position to ensure correct assembly at the Site.

Washers, locking devices and anti-vibration arrangements shall be provided where necessary to ensure that no bending stress is caused in the bolt.

Where there is a risk of corrosion, bolts and studs shall be designed so that the maximum stress in the bolt and nut not exceed half the yield stress of the material under all conditions.

Except where otherwise approved, wood screens shall be brass with round or countersunk heads. Nails will only be permitted in specifically approved circumstances.

Should the protective coating or physical form of any fixing be damaged due to over-tightening or any other cause, the Contractor shall replace the fixing.

## Labels

The Contractor shall supply and fit engraved labels and each item of works throughout all installations. The labels shall be permanently attached in a conspicuous position and shall detail the design performance, function manufacturer’s identification and system identification. In general, the function and system identification shall be separately labeled.

All indicating and operating devices shall have securely attached to them or marked upon them designations in English and Serbian language as to their function and proper manner of use. Items such as valves shall have direction of rotation for closing and opening indicated.

Only non-flame-propagating materials may be used for place and labels.

Inscriptions shall be permanently engraved and, in general, a dark inscription on a light background shall be provided.

The proposed style, label material, inscription, location and means of fixing shall be submitted to the Engineer for approval. Embossed materials and techniques will not be accepted.

Where withdraw able or detachable equipment is provided, both the fixed and moving or detachable portions shall be similarly labeled.

Labels shall be provided to warn of dangerous or potentially dangerous circumstances or substances.  Inscriptions on danger labels shall start with the word “DANGER” and be white on a red background in Serbian language.

Inscriptions on caution labels shall start with the word “CAUTION” in Serbian language.

Instruction labels shall be provided where safety procedures are essential to protect operating and maintenance personnel from hazardous or potentially hazardous conditions, e.g. advising the isolation or earthling of electrical circuits or the wearing of protective clothing.

In addition to the above works identification labels the Contractor shall ensure each item of machinery shall have a manufacturer’s identification/rating plate detailing the following:

- Manufacturer’s name and address

- Model/type identification

- Serial number

- Year of manufacture

- Appropriate rating details

- Other relevant details, limitations, etc.

All labels shall be removable to facilitate replacement by an equivalent sized label should the need arise.

## Works Finish

The following general requirements shall define the standard of finish required on various items of the works:

- Welding and flame cutting; a smooth neat finish, by careful grinding if necessary, is required on all exterior welding and flame cutting. All plates and bars used in fabrications shall have good smooth surfaces with no pitting or deep inclusions;

- Castings; surfaces shall be smooth and free from surface blowholes. Stock castings shall be specially selected with this in mind. All castings shall be shot blasted before machining;

- Covers; shall be firmly fixed. Weld mesh shall sit square in its frame;

- Flanges and beadings; all bolt holes shall be spot face parallel with the mating face for good seating of nut and bolt heads. Mating faces and peripheries shall be machined true.

- Small exposed screw and bolt heads, nuts and washers; shall be chromium on copper plated or made in stainless steel or otherwise as specified or approved in advance.

- Hand wheels; the Hand wheels rims shall be machined and groom square or they may be chromium or copper plated.

- Gauges; all indicating gauges fitted to any one piece of machinery shall be of similar appearance and grouped together to present a pleasing aspect.

## Suppression of Noise

In order to suppress noise outside of location of the RWMC, the sound barrier shall be constructed. Sound barrier shall fulfil requirements defined in the Employer’s Requirements.

The indoor noise limit values must be in accordance with the current national regulations, but in any case noise level at 1 m distance from all noise producing equipment must not exceed 75 dB (A).

Noise test measurements shall be made on completion of the installation of the equipment at Site to verify that it complies with this Specification. Equipment, which fails to comply with the noise level limits when tested, will render it liable for rejection unless it is satisfactorily modified at the Contractor’s expense by the commissioning date.

## Bearings

All bearings shall be generously rated and sized to ensure satisfactory and stable running without vibration under all conditions of operation for a minimum running life of 50,000 hours. They shall be sufficiently lubricated and adequately protected from ingress of moisture and sand and the particular climatic conditions prevalent at the Site. All bearings shall be to ISO standard SI unit dimensions where practicable.

## Lubrication

All bushes and ball or roller bearings shall be arranged for grease gun lubrication. Grease nipples shall be standardized.

Provision shall be made in the design to prevent the over lubrication of any part. It is preferable that routine lubrication of the works shall be kept to a minimum.

Grease lubrication systems shall preferably be of the pressure type designed so that adjustment or recharging is not required more than once per thirty days under normal operating conditions. Grease application points shall be easily accessible and where needed, extension piping shall be provided.  When several such points can be grouped, they shall be brought to a rigidly constructed battery plate and each point shall be clearly labeled. A permanently labeled grease gun shall be supplied for each type of grease required and each standard type of nipple fitted.

Oil lubrication shall preferably be of the re-circulating reservoir type, which automatically maintains the correct oil, level and shall be designed for continuous normal operation for long periods.  Sight glass level indicators shall be fitted on all oil reservoirs, and the levels shall be easily read over the maximum operating range. Re-circulating oil lubrication systems shall be provided with an external replaceable filter element.

The level indicators shall be simple to dismantle for cleaning, clearly marked, with the minimum, normal and maximum oil levels at normal running temperatures, and shall show the normal filling level at design ambient temperature. The sight glass shall be positively protected against mechanical damage.

Particular care shall be taken in arranging lubrication points to protect the works and the process water from accidental contamination. Catch trays, drip trays, screens and the like shall be generously provided throughout the works.

The type of lubricants and intervals of lubrication for each individual item of equipment shall be entered on a working schedule, which shall form part of the operating and maintenance instructions.

A complete draft of this schedule of recommended lubricants, with their trade names, their purpose, viscosity, etc., container size and life, and the name of the manufacturer and his local supplier shall be submitted to the Engineer for approval before the schedule is incorporated in the draft operation and maintenance instructions. The number of different lubricants shall be kept as small as possible.

## Location and Alignment

Where separate items of interconnected works, such as motors, couplings gearboxes and similar items depend upon correct alignment for satisfactory operation then each item shall be positively located in its correct operational position by means of dowels, locating pins, fitted bolts or other approved means to ensure that correct realignment can be easily achieved when reassembling the items after removal for overhaul.

## Flexible Couplings

Couplings, where supplied, shall be generously rated to cover the full range of duty and shall be of the flexible multi-pin and bush type having not less than six bushes and each bush shall have an inner sleeve to allow rotation on the pin (bushes shall not be in direct contact with the pin). All pins shall have shoulders to allow positive location and securing to the coupling flanges, bosses shall be a tight fit on the shafts and secured with hand fitted keys.

Couplings shall be supplied in matching balanced sets and shall be dynamically balanced and marked before leaving manufacturers works.

## Standard Gearboxes

Standard enclosed gearboxes for machines shall be obtained from an approved manufacturer where necessary. The gearbox shall be designed to operate with the output shaft oriented at the required angle of inclination without lubricant leakage. The input shaft shall be horizontal where possible and appropriate.  All gearboxes shall be suitable for outdoor installation and made for continuous operation and heavy shock loads. Service factor shall not be less than 2. The gearbox selection shall be checked for overloads, and overhung radial and thrust loads.

Gearbox housing shall be of rigid high-strength close-grained cast iron with provisions for:

- Proper closing inspection cover;

- Ventilation opening;

- Oil level gauge;

- Gauge window protection.

The ingress of moisture into the gearbox shall be prevented and splash and leakage water etc. must be able to drain off easily.

Where immersion or splash lubrication is not effective, gears and bearings shall be lubricated automatically by a forced lubrication system. Lubricants shall be as or the equal to that recommended by the manufacturer of the gearbox.

Provision shall be made in the design of the gearbox for oil filling and drainage. If the drain is not easily accessible, the gearbox shall be equipped with an outlet hose and small hand pump.

The gearbox shall be provided with a flexible overload coupling (including safety guards) between the motor and the input shaft of the gearbox. Parts subject to wear must be easily replaceable without disassembling the motor.

## Setting of Machinery

The machinery shall be mounted on flat steel packing of thickness selected to take up variations in level of the concrete foundations.

The machinery shall be aligned, leveled and pulled down by the nuts of the holding down bolts with a spanner of normal length. Only grouting of holding down bolts to the approval of the Engineer shall be carried out before the machinery has been run and checked by the Engineer for stability and lack of vibration. Final grouting of shims etc. shall be carried out only after the aforementioned run and check by the Engineer has been completed, approval given, and the grouting area clean and suitable in every way.

## Machinery Finish

All covers, flanges and joints shall be clean, properly faced, bored, fitted, hollowed, molded or chamfered as the case may be according to the best approved practice and all working works and other apparatus shall in like manner be well and accurately fitted, finished, fixed and adjusted.

# SPECIFICATION FOR PROTECTIVE COATING

## General

This section of the Specification shall apply to the general requirements and standards of workmanship for the painting and protective coatings required to be carried out by the Contractor in the works.

These Specifications are to be considered for both civil and mechanical applications!

Unless specified otherwise or unless the Contractor has submitted an alternative specification at the time of tendering to meet one of the following conditions:

- Particularly corrosive local environment;

- Possible reaction of released aggressive gases;

- Reaction of aggressive gases or waste/leachate water on paints;

- Harmful or toxic paint in contact with process liquids.

No alternative or substitute painting standard or specification will be accepted unless it is specifically required for the above stated reason. No painter work or protective coatings will be accepted by the Engineer unless it is at least to the standard and of the quality specified herein.

## Contractor’s Responsibility

The Contractor shall be responsible for the complete cleaning, preparation, priming, painting and protection of the works carried out by him:

- At the place of manufacture;

- In preparation for packing and transit;

- For preservation during storage;

- For immediate ‘touch up’ or remedial work when received, placed in store, and/or delivered to the Site;

- For supervision of the protection of the coating during the erection, testing and commissioning of the works;

- For the supervision of final painting following testing of the works;

- For the supervision of ‘touch up’ or ‘re-protection’ as the result of any trouble-shooting activities during the commissioning of the works.

## Submissions

The Contractor shall submit to the Engineer for approval triplicate copies of a comprehensive submission (in English) with samples, certification and data regarding the final materials, sources, manufacturer’s instructions, methods of application etc., which are specified or which he proposes finally to adopt to protect the works as Method Statement per each individual item.

The samples shall include for all paints:

- Applied paint coatings and colors on samples;

- Reference samples of the paint.

The certification shall include:

- The results of test and odor tests for all coatings proposed or specified for any pipeline, equipment or item of Works or surfaced which is designed to be or could normally be in contact with solid waste, leachate or wastewater being processed, stored or pumped;

- The results of meaningful tests on the effects of solid waste, leachate or wastewater and/or any other chemical fluid or gas which the coating is specifically required to protect against, and to which, by nature of the works arrangements, the protected installations may be exposed.

The data shall include:

- A complete schedule of the protective coating and paint systems;

- Color charts for finishing coats (including the system color notation);

- Manufacturer’s product data on the protective treatment, coatings and paint systems;

- Manufacturer’s preparation and application instructions;

- Method of application.

The schedule required with the submission shall contain the following information, in detail:

- Item;

- Environment of item;

- Type of surface;

- Surface preparation;

- Protective or paint system to be applied;

- Name of coating manufacturer;

- Brand name and reference number for each coat to be used;

- Manufacturer’s data sheet for each coat, including the technical description and formulation of paint, and the color of each paint;

- Color of finishing coat stating the system color notation;

- Proposals concerning place of application and detailed;

- Method of application of each coat, including information on equipment to be used;

- Wet film minimum and target thickness for each coat;

- Dry film minimum and target thickness for each coat;

- Density of paint for each coat and coverage of paint per unit volume including volume solids.

The work detailed on the painting schedule shall meet the requirements of the Specifications and the Drawings.

Prior to the commencement of erection of the works, the Contractor shall submit quadruplicate copies of the final approved painting schedule to the Employer/Investor and during the erection, testing and commissioning periods, maintain a copy of the document on site for his own use and shall provide a separate copy for exclusive use by the Employer/Investor and the Engineer.

## Appropriate Standards

Where no explicit instruction is given in the Specifications or by the manufacturers concerning any particular aspect of the workmanship, materials or procedures in connection with anti-corrosion protective systems in the works for iron and steel structures, the relevant recommendations of the German DIN Standard or equivalent harmonized European Standard and code of practices shall apply.

## Trial Areas and Sample Pieces

Site procedures specified shall be such that prior to the commencement of the site paint work designated area(s) or section(s) of the works shall be completely painted as a sample of the work and workmanship to be carried out. The area(s) or section(s) shall include complete samples of all the major painting required in the works.

The area(s) shall be offered for review and shall, upon approval, be then preserved as a reference standard for the work.

## Color, Coding, Labels, Arrows

Pipe work, tanks and ducting shall be detailed as color coded either by banding with the appropriate code color over the decorative paint, or by totally painting with the appropriate code color as detailed on the drawings or specified.

The principal code colors shall be as follows:

| - Potable water Blue | 7.5 PB 2.5/10 |
| --- | --- |
| - Hot water Crimson | 5 R 2.5/12 |
| - Service water Medium green | 7.5 GY 4.5/8 |
| - Wastewater Dark green | 10Y 3/1.5 |
| - Gas Yellow | 5y 9/14 |
| - Compressed air Light blue | 10BG 7.5/1.5 |
| - Air Scour Silver | - - - - |

Alternative colors or notations (i.e. RAL codes) can be applied after approval from the Engineer. The color coding for other minor pipelines will be notified by the Contractor prior to the commencement of erection after approval from the Engineer.

Where color banding of pipe work (as distinct from total painting in the code color) is detailed, the bands shall be of the sizes shown on the approved drawings.

All pipes and tanks shall be detailed to also bear painted labels to indicate the contents. Lettering shall be in English and Serbian language. Labels on pipe work shall incorporate arrows showing the direction of flow within the pipe work. When pipes are color coded with colored bands, the label shall be located on the color band. Black lettering shall be used on orange, yellow and green and white lettering shall be used on red and blue. Sufficient labels shall be used to ensure adequate identification throughout the length of the pipe runs. These shall be located at least adjacent to each flange or disconnecting joint, where pipe work passes through walls, floors, crosses, doorways and other access ways and at intervals in long runs of pipe work.

## Metal Coatings General

Metal coatings required for protective purposes on any item of metalwork shall be applied after fabrication of the items is completed, including all punching, welding, drilling, grinding, screw tapping and cutting, and after the removal of surface defects.  Tapped holes shall be blanked off before the metal coating is applied.

Any damage to zinc coatings during installation shall be made good with a suitable cold galvanizing compound.

## Prefabrication Primers

Unless otherwise specified, prefabrication primers for steelwork shall incorporate corrosion inhibiting pigments, shall adhere firmly to the substrate and form suitable bases for the succeeding coats in the protective paint system.

## Surface Preparation by Blasting

All surfaces to be coated shall be free of scale, rust, grease, oil, dust and other deleterious materials.  The surface finish of blast cleaned steel shall be in accordance with (second quality) (new sheet should be finished to a SA 2.5 quality), the blast profile shall be within the limits 50 - 75 microns.

Only abrasive cleaning techniques shall be used. The clean abrasives shall be carefully stored in a dry atmosphere; they shall be clean and shall not be re-used unless properly recycled in equipment, which has de-dusting, screening and drying facilities. Abrasives shall be restricted to re-usable iron or steel (grit or shot) or copper slag. The blasting shall be carried out in a dry atmosphere, as high humidity will result in agglomerates of dust and abrasive particles forming which will inhibit the cleaning process. Clean, dry compressed air should be available in sufficient quantity at an adequate pressure. It should be free from water and oil.  Separators, filters and traps shall be fitted to collect water and oil. These should preferably be of automatic operation.

After blast cleaning and immediately prior to painting, all accumulated dust; residue and debris shall be removed by means of a hand-held or equivalent vacuum cleaning method.

Laminations, blow holes, crevices and other surface defects exposed after blasting shall be overfilled with suitable weld metal and ground flush.  Welding flux and spatter remaining after blasting shall be removed by grinding or other best mechanical means and edges made flush. All sharp corners, edges and burrs shall be removed by grinding. Where extensive rectification has been necessary to areas greater than 0.15 m² these shall be blasted to the original quality of surface preparation.

Within four hours of completion of surface preparation, and before surface re-resting occurs, a coating of primer shall be applied to avoid deterioration of the prepared base metal. No contamination shall be permitted to occur between blast cleaning and primer coating.

## Dehumidification Required for Special Purposes

All surfaces to be coated shall free of scale, rust and deleterious substances. Re-humidification equipment shall be utilized as may be necessary to preserve blast-cleaned surfaces in a pristine condition until they can be coated and/or to provide the curing conditions necessary for such coats.

## Damage to Works Preparation

Works (shop) prepared surfaces (other than galvanized surfaces), damaged during site fabrication and/or handling shall comply with at least the following:

- All slag and spatter shall be removed from areas of welds by chipping hammer and these areas together with all other areas of priming coat damaged in the process of fabrication and/or handling shall be thoroughly mechanically wire brushed and given one priming coat of an approved polyamide cured - zinc phosphate epoxy corrosion resistant primer - two pack

- Where relevant the first finishing paint system shall be applied within 48 hours of the above primer.

## Embedded Steel

Steel, which is to be totally embedded in concrete, shall be sand blasted and cleaned and shall not be primed.

## Preparation and Painting of Works

Lettered classification of surfaces shall be used for the purpose of identifying protective coatings specified herein:

‘A’	Surfaces above process liquid level, like wastewater and leachate, which are not liable to splashing thereby, in non-aggressive atmosphere;

‘B’	Surfaces in contact with untreated or treated water for potable use;

‘C’ 	Surfaces below process liquid level like wastewater and leachate which are liable to splashing thereby in non-aggressive solutions and/or atmospheres;

‘D’	Surfaces in contact with aggressive solutions and/or atmospheres.

## Steelwork in Locations ‘A’, ‘B’ and ‘C’

Works (shop) preparation and initial protection of steelwork in locations ‘A’, ‘B’ and ‘C’ shall comply with at least the following:

a) Works preparation shall be carried out when all machining has been completed and all traces of grease removed;

- All steel, other than stainless steel, (except that which subsequently will be totally embedded in concrete or that which may be pieced sufficiently small to hot dip galvanize), shall be sand blast cleaned to the Standard SA 2.5 such that the depth of surface from valleys to peaks shall not exceed 75 µm ± 25 %;

- Initial protection shall be applied within 4 hours of sand blast cleaning in a ‘clean condition’ area of the workshop subject to the provisions of requirements for the working environment;

- All surfaces shall be completely freed of loose abrasive and given a priming coat of an approved polyamide cured:

Zinc phosphate epoxy corrosion resistant primer - two pack; or (alternative shall not apply to surfaces in location ‘B’) Zinc chromate epoxy corrosion resistant primer - two pack;

- An approved airless spray process shall be used to apply a dry film thickness above peaks of not less than 50 µm;

- Painted identification markings shall be reproduced on the priming coat;

- Steelwork fabricated at works shall only receive the above preparation and initial protection after all machinery and fabrication has been completed and when such fabrication is by means of continuous welded runs with all exposed surfaces accessible for subsequent treatment. All slag and spatter shall be removed from the area of welds by chipping hammer prior to grit blast of cleaning;

- The inside surfaces of box members and similar non-fabricated sections where sand blast cleaning is impracticable shall be cleaned to Standards (shall not apply to surfaces in location ‘B’);

- Where relevant, the first finishing paint system shall be applied within 48 hours of the initial primer in accordance with the specification;

- Surfaces of steelwork to be fabricated at site shall receive works preparation as above and initial protection with a prefabrication primer of an approved:

  - Zinc phosphate epoxy - two pack;

  - or (alternative shall not apply to surfaces in location ‘B’)

  - Zinc chromate epoxy - two pack;

- An approved air-less spray process shall be used to apply a dry thickness above peaks of not less than 50 µm;

- Painted identification markings shall be reproduced on the priming coat;

- Steel work shall be protected in covered storage works until fabrication is ready to commence at Site where the first finishing coat shall be applied after fabrication provided the provisions of the Specification have been satisfactorily complied with  (alternative shall not apply to surfaces in location ‘B’).

## Steelwork in Location ‘D’

Works (shop) preparation and initial protection of steelwork in location ‘D’ shall comply with at least the following:

- Shop preparation shall be carried out when all machining has been completed and all traces of grease removed;

- All steel, other than stainless steel, shall be: prepared and hot dipped galvanized;

- Initial protection shall be applied at works (shop) only when exposure to aggressive solutions and atmospheres is expected within three months and/or before an adequate protective patina has formed;

- Initial protection when required to hot dip galvanized surfaces shall comprise: - Thoroughly clean and degrease all surfaces followed by etching with T wash as described in DIN 5493.  (In the event of any surface failing to turn back the cleaning, degreasing and etching process shall be repeated);

All surfaces shall then be thoroughly washed with clean water, completely dried and given a priming coat of an approved:

- Polyamide cured zinc phosphate epoxy corrosion resistant primer - two pack;

- An approved airless spray process shall be used to apply a dry film thickness of not less than 50 µm.

## First Finish Steelwork in Location ‘A’

The first finishing paint system for surfaces in location ‘A’ (other than galvanized surfaces), shall comply with the least the following:

- All surfaces of fabricated steelwork shall be given in accordance with location a first finishing coat, differing slightly in shade from the intended final coat, application being brush or airless spray;

- To surfaces in location ‘A’ one coat of an approved: Polyamide cured epoxy miscellaneous iron oxide, two pack shall be applied at the place of manufacture to give a dry film thickness not less than 125

- µm. Interval after application of priming coat shall not exceed 48 hours;

- Painted identification markings shall be reproduced on the first finishing painting system.

## Final Finish in Locations ‘A’, ‘B’ & ‘C’

The final finish paint system for surfaces in locations ‘A’, ‘B’ and ‘C’ other than galvanized surfaces shall comply with at least the following:

- All surfaces of the fabricated steelwork (except those areas which are inaccessible and to which the final coat was applied at works) shall be given a final coat of color to be approved. This final coat shall be applied at site when all associated supervising work has been completed;

- Bolted site connections other than fraying surfaces of grip bolt connections shall be brought together

- ‘wet’;

- All areas where the first finishing coat has been damaged in transit and/or erection shall be repainted as specified;

- Special attention shall be given to severe damage exposing bare metal in which instance the damaged areas shall be thoroughly sanded to a bright finish, primed and repainted as specified;

- To surfaces in location ‘A’ sufficient coats of silicone alkyd enamel shall be supplied to give a dry film thickness of not less than 50 µm;

- On site, to surfaces in location ‘B’ two coats of approved: - amine adduct - cured pure epoxy resin - two pack shall be applied to give a dry film thickness not less than 125 µm per coat;

- On site, to surfaces in location ‘C’ two coats of approved: - polyamide cured epoxy coal tar - two pack shall be applied to give a dry film thickness not less than 125 µm per coat.

## Final Finish in Location ‘D’

Priming and first finishing paint system surfaces in location ‘D’ shall comply with at least the following:

- All surfaces of galvanized fabricated steelwork (except those on which an adequate protective patina has not formed and/or those surfaces which have received initial protection under the provision of the Specification) shall receive a priming coat immediately following erection at site and prior to immersion in or exposure to aggressive solutions or atmospheres;

- All surfaces shall lightly wire brushed and all traces of grease and other contaminants removed;

- All loose particles shall be removed and immediately thereafter all surfaces including those of fastenings shall be given a priming coat of an approved: polyamide cured zinc phosphate epoxy corrosion resistant primer - two pack to give a dry film thickness not less than 50 µm, care being taken to ensure that no ‘Holidays’ remain;

- All surfaces of galvanized fabricated steelwork on which an adequate protective patina has not formed shall be treated and given a priming coat immediately following erection at Site and prior to immersion in or exposure to aggressive solutions or atmospheres followed by a first finishing coat as described below;

- All surfaces which have received initial protection at works or a priming coat at site shall be thoroughly cleaned and given a first finishing coat of an approved: - polyamide cured epoxy coal tar – two pack applied to give a dry film thickness not less than 125 µm;

- No ‘holidays’ shall exist in the finished work;

- The final finishing paint system shall be applied within 48 hours of the above.

## Galvanized Surfaces

Surfaces shall not be immersed within three months of hot dip galvanizing, according to relevant standard and/or before an adequate protective patina has formed.

## Painting of Welds

After the completion and grinding of exposed welds, weld spatter, weld residues and all alkaline deposits and contamination shall be removed from the surface of the steelwork, and welds and any other areas affected or damaged by the welding process shall be blast-cleaned. The primer shall be applied to the blast cleaned areas as specified and the remainder of the paint system applied as necessary to complete the protection across the welded seam and damaged areas to the same state as that existing generally on the faces of the parent metal. Each coat applied shall overlap the corresponding existing paint coat by 50 mm both sides of the weld on each exposed face of the parent metal.

## Uncoated Surfaces

The only surfaces of iron or steelwork not of corrosion-resistant material, which are to be left unprotected by paint or metal coating, are:

- The internal surfaces of boxes or hollow sections which are of dimensions too small to permit access for painting either at the fabrication stage or for maintenance during the operational life of the steelwork and which are to be hermetically sealed by welding;

- Those surfaces of built-in iron or steel members, which are to have concrete cast against them;

- Machine bright parts and bearing surfaces which shall be thoroughly cleaned, polished and protected from corrosion by painting with one coat of a mixture of white lead and tallow or other similar approved material before dispatch.  The Contractor shall provide solvent for removing the treatment;

- Parts which are specified to include corrosion allowances instead of protective coatings.

Surfaces of iron or steel members, which are to have concrete cast against them, shall be clean and free of deleterious matter and loose rust at the time of concreting. The paint protection system, to be applied to the permanently exposed faces of these members before the members are built in, shall be continued for 50 mm as marginal stripes along the contact surface. No paint containing aluminum in metallic form shall be allowed to come into direct contact with the concrete.

## Repair of Damaged Work

Unless specified elsewhere, areas of paint on steelwork that have been damaged shall be cleaned to basic material and the edges of the undamaged paint smoothed with sandpaper to a gentle level.

The specified paint system shall then be applied to bring the damaged area up to the same state of protection as the surrounding paintwork, with each coat of new paint overlapping the corresponding existing coat of paint by at least 50 mm.

Areas of paint on which weld spatter, concrete or their adherent matter has fallen shall be cleaned or washed free of the adherent material immediately and any repair or making good of the affected surface to its original standard shall be carried out before the area is over-coated with paint.

Where the steel is exposed, it shall be cleaned to remove all corrosion, by blast cleaning if necessary. Where epoxy coatings are damaged, suitable repair material supplied by the manufacturer of the original coating shall be applied in accordance with the manufacturer’s instructions i.e. methodology.

## Preparation and Painting of Pipes

Steel pipes below 80 mm in diameter for use at temperatures up to 40 °C shall be made of stainless steel minimum grade W 1.4301 or hot dip galvanized and security wrapped with polythene sheeting where laid in ground. For use at temperatures above 40°C galvanized steel pipes shall not be laid in ground.

In locations ‘A’, ‘C’ and ‘D’ cast iron and steel pipes 80 mm in diameter and greater for use at temperatures up to 40°C shall be cleaned in accordance with the pipe manufacturer’s accepted trade practice and shall be hot dipped internally and externally in an approved bitumen solution.

Ductile iron and steel pipes shall be securely wrapped with polythene sheeting where laid in ground. For use at temperatures above 40°C and up to 80°C approved bitumen shall be applied to the external surface only of ductile iron and steel pipes prior to lagging and they shall not be laid in ground.

External surfaces of exposed pipes shall be given two coats of approved Silicone alkyd enamel to give a dry film thickness of not less than 50 μm after all civil Supervising work has been completed.

In location ‘B’ cast iron, ductile iron and steel pipes 80 mm in diameter and greater shall be treated strictly in accordance with the requirements for equipment in location ‘B’.

## Preparation and Painting Metal Parts

Mild steel items (including steelwork sections, pieced small and machinery castings) shall be hot dip galvanized when all machining and fabricating has been complete where such fabricating is by means of continuous or intermittent welded runs with all exposed surfaces accessible for galvanizing. Alternatively, mild steel items shall be prepared in accordance with the provisions herein regarding preparation and printing of works.

All other parts and attachments, whether of cast-iron or cast steel, shall be thoroughly cleaned by sand blazing to the Standard SA2.5. Priming and painting shall then be carried out in accordance with location.

## Preparation and Painting of Non-Ferrous Parts

Non-ferrous metal parts except structural metal aluminum (in locations ‘A’ only) shall not be painted unless specifically called for by the Engineer except bolt holes and faces which shall be given one coat of zinc chromate epoxy - two pack.

## Preparation and Painting of Mild Steel Supports

Mild steel supports and hangers in locations ‘A’, ‘B’ and ‘C’ shall be prepared, and hot dip galvanized when all machining and fabrication has been completed and they shall remain unpainted.

## Preparation and Painting of Fastenings

Bolts, nuts and washers and other demountable fastenings of all galvanized parts and stainless steel shall remain unpainted. PTFE washers shall be fitted beneath bolthead and washer when fastening galvanized parts and aluminum alloy.

Fastenings, except high tensile, of all ferrous parts shall be steel prepared and galvanized or sherardized, primed and painted in accordance with location.

Unless specifically approved and required for superior protection, electro-galvanizing, nickel, cadmium or any other plating process, except chromium plating, will not be acceptable, and shall not be offered.

## Painting and Protection of Bolted Connections

Joint areas of bolted connections shall be masked to maintain the surfaces free from any paint applied prior to making the connections. Masking shall be removed before erection.

After installation and all bolts have been tightened the area of the connection shall be cleaned to remove all dirt, dust, oil or other contaminant. Particular care shall be taken to ensure that all traces of oil and grease are removed from bolts, nuts and washers.

Any surrounding areas of paintwork that have been damaged shall be prepared as specified in repair of damaged work.

Bolts, nuts and washers and any exposed surfaces at bolted connections shall also be primed as specified, particular care being taken to ensure that any crevices are fully sealed.

The remaining coats of the paint system shall then be applied.

Following painting and where the bolted connections are in an area to be backfilled (pipe trench flanges etc.) the bolt, nuts and washers and the entire joint assembly shall be carefully packed with an approved purpose made water proof protective paste (non solvent) and finally wrapped with an approved protective paste impregnated tape to completely encase the assembly. Pipe joints protection shall continue along the length of the barrel for a distance of 200 mm.

## Overcoating of Bituminous Coatings

Where items with factory applied bituminous coatings are to be over coated with a decorative finish, the surface shall be sealed with a suitable oleo resinous or alkyd aluminum primer compatible with both the bituminous coating and the decorative system.

# PIPEWORK

(2A GTS Civil and Building Works)

# METALWORK

This Section sets out the general requirements for the metalwork's required both externally and internally in the structures.

These Specifications are to be considered for both civil and mechanical applications!

## Structural Work

The Contractor shall fabricate, supply, deliver and erect all steelworks, fixing materials and associated parts according to the specifications and drawings and shall comply with the specifications of the relevant Standards, unless otherwise specified or instructed by the Engineer.

The steelworks shall comprise of the following main items:

- Columns and beams;

- Open mesh flooring and gratings including framework and supports;

- Hatches, including frameworks;

- Covers for chambers;

- Sheet piling;

- Flanges and bolted connections;

- Anchors;

- Angles for protection of edges in several lengths, including anchors;

- Step irons, ladders and pipes where shown on the approved Contractor's Drawings or instructed by the Engineer;

- Staircases, landings and platforms;

- Other structural steelwork associated with the specified civil, mechanical and electrical works.

For all fabricated steel works the Contractor shall submit fabrication details, Drawings and calculations for the approval of the Engineer prior to the manufacture of any of the items.

## Standards (Steel)

Rolled structural steel sections shall be mild steel conforming to EN, ISO or national standards. The dimensions, tolerances and properties of the structural sections shall conform to EN, ISO or national standards. Where the use of prefabricated proprietary designs is proposed, the standards to which they are manufactured shall be no less rigorous than specified herein.

For structural steel work assemblies, steel bolts and nuts shall be high strength friction grip bolts or black bolts. Bolts & washers shall conform to EN, ISO or national standards. High strength friction grip bolts shall be used in conduction with approved proprietary load indicating washers.

All welding consumables (electrodes, wire, filler rods, flux, shielding gas and the like) shall comply with the requirements of EN, ISO or other international recognized standard.

## Submissions by the Contractor

Except where specified on the drawings the Contractor shall design, detail and fabricate the metalwork in accordance with the specified standards and shall minimize the need for site welding, brazing or other special skilled assembly work.

Structures and components, such as required for the cranes and laddering, hoppers etc., shall be shop fabricated to form sub-assemblies of the largest practical size suitable for transportation, handling and erection. Connections between members at the erection stage shall generally be bolted.

Structural steelwork shall be detailed and fabricated to minimize the formation of pockets to hold condensation, water or dirt. Where such pockets are unavoidable, suitable drainage shall be provided.  Prior to any steel fabrication work the supplier shall submit full details of his proposed procedure, qualification, and methods of fabrication to the Engineer for approval.

This information shall include (but not be limited to) the details concerning the method of plate forming; joint design; proposed welding procedure and proof of competence of welders; methods of straightening, sizing and hydrostatic testing; quality control and inspection procedures.

## Drawings

The Contractor shall prepare detail shop and erection drawings and welding procedure sheets for all structural steelwork and shall submit these to the Engineer for approval before fabrication commences. The sequence of submittals shall match the order of fabrication and erection.

Shop drawings for fabrication shall show full details of the type of steel, member sizes and dimensions, weld details, welding sequences and any requirements for weld stress relieving.

Welding procedure sheets shall show all details of the welds including:

- Welding method;

- Current type, voltage and amperage;

- Welding positions;

- Preparation angles and methods;

- Number of runs and their welding positions;

- Type, size and class of electrode;

- Shielding gas type and flow rate (where applicable);

- Non-destructive testing methods and extent of coverage;

- Pre-heat, post-heat and stress relief methods, temperatures and the like.

Erection drawings shall detail all connections, bolt types and sizes, and all site weld details if applicable.  Shop and erection drawings shall show all marks necessary to facilitate erection and the marks shown on the drawings shall be identical with those shown on the fabrications.

## Calculations

The Contractor shall submit to the Engineer for his approval calculations of the following items:

- Structural calculations where applicable or required by the Engineer;

- Mounting plates;

- Stiffening parts;

- Welded seams;

- Anchors and bolts, even when these items are shown on the Drawings.

In the event of unavailability of certain materials and steel sections, deviations from the original design can be made after approval from the Engineer. In such cases the Contractor shall submit to the Engineer his calculation for the proposed design. Such calculations shall be submitted to the Engineer for approval in three copies together with three copies of corresponding workshop drawings.

The Contractor shall submit to the Engineer for his approval calculations of weights of all relevant steel structural components. The basis for the calculations shall be the measurements of items as indicated on the approved workshop drawings multiplied by their number and the specific weights.

These calculations shall be submitted in three copies together with three copies of corresponding workshop drawings.

## Welding

All welding carried out during fabrication in the factory and erection on the Site shall be carried out in accordance with the requirements as shown on the approval detail drawings.  Details of the proposed weld procedures shall be submitted to the Engineer for approval at the same time as the detail drawings.  All connections shall be welded in such as manner as to make the finished connections neat and smooth in appearance, and suitable for painting. All slag shall be removed, and any sharp projections shall be ground smooth.  Before welding is commenced either in the fabrication shop or on Site, weld procedure tests shall be carried out in accordance with EN, ISO, SRPS or other international recognized Standards.  All welders employed either in the fabrication shop or on Site shall pass qualification tests relevant to the weld procedures in use in accordance with national standard or equivalent EN, ISO standard. Welders shall have least 9 months skilled experience in the preceding 12-month period. If the work of any welders employed on the Contract is unsatisfactory, the Contractor shall carry out such further welder qualification tests as are necessary to demonstrate that the welders are proficient.

Where directed and/or specified, welds shall be subject to non-destructive testing by processes which may include but not necessarily be limited to radiographic, ultrasonic, magnetic particle, or dye penetrate methods, depending on the type of weld and its position in the structure.

If any work shows defects or fails to comply with the requirements of the approved drawings or the specification for any reason, it shall be repaired or rejected, even though it may have been carried out by qualified welders using approved procedures.

Special precautions shall be taken to avoid lamellar tearing when welding thick plates and low hydrogen content electrodes shall be used. Class 1 welds shall be fully radiographed except where otherwise specified.

In bad weather, additional measures are needed in the course of welding consequently, in case of rainy weather; provision shall be made to keep the places of welding dry. In weather with temperatures below 5 C, a strip of 100 mm should be preheated to 50 ºC, on both sides of the welded joint in case of both seams and tack welds.

Splash, burning-in, uneven arc, oversized root edges at corner joints, unsatisfactory seam or any crack are impermissible in the course of welding. Surfaces should be free from any marks of impact, indentation and deformation.

## Identification of Members

All members of assemblies shall be marked at the factory with distinguishing numbers, letters or marks corresponding to those of approved drawings or parts lists. Such markers if impressed before painting shall be clearly readable afterwards. Care shall be taken that any temporary bolts for field erection are readily distinguishable from any high strength bolts for permanent connections.

## Storage and Erection on Site

All structural elements and other materials shall be stored (whether at the place of fabrication or on site) clear of the ground and shall be protected against deterioration from any cause.

The Contractor shall supervise all site erection processes, which, as far as is possible, shall be supervised with the following standards as the objective. The works used for handling and erection shall be suitable and safe. Temporary protection shall be required for workmen and materials below any structural steel under erection of any part of the completed structure may be safely carried out.

Anchor bolts shall be properly located using templates or other approved method and after building in the anchor bolts, a sufficient time shall be allowed for concrete strength to develop before finally pulling down to shims and grouting.

Every part of the structural steelworks shall be positioned accurately in accordance with the dimensions on the approved drawings with a maximum tolerance of ± 5 mm except where the steelwork supports metal flooring, when the finished tolerances shall be such that differences in level between adjacent flooring sections or between flooring sections and adjacent building floors shall not exceed 3 mm and the gaps between flooring sections shall not exceed 3 mm.

Where structural steelwork is to be grouted on or against concrete or other similar surfaces and where it is considered essential to affect a uniform contact area under the base plate or where necessary, the erection team shall remove all steel shims or wedges and replace these with grout of the same constituents and consistency as the main grout. Such steel shims shall be initially positioned to aid removal. In the case of baseplates with large overhangs or with heavy bearing loads, the Contractor shall specify the shim position before the structure is erected on them.

During erection, the work shall be securely bolted or otherwise fastened, and if necessary, temporarily braced, to make adequate provision for all erection stresses and conditions including those due to erection works and its operation. No permanent bolting shall be done until proper alignment has been obtained.

The Contractor shall report immediately to the Engineer any errors in shop fabrication or deformations resulting from handling and transportation that prevent proper assembly and fitting of parts. Agreement as to methods to be used to correct such errors or deformations shall be reached with the Engineer prior to beginning of any corrections.

During erection, provision shall be made to hinder any foreign body from entering the pipes and to avoid the inside surface of the pipe from getting contaminated. Open pipe ends should be closed and welding residuals like droplets of welding, slag, electrode residuals should completely be removed.

In processing stainless steel components, rigorous measures should be taken to avoid any direct contact between stainless steel components and standard steel. While processing, stainless steel components should undergo careful and professional treatment, pipes and shapes should be stored on timber and only non-metallic grinder should be used for grinding. Welding with protective atmosphere is permissible. Welded joints should be etched at the topcoat by immersion in full and should undergo passivation.

In case of no stainless steel fixings, supports, flanges, screw joints, etc., metals should consistently be separated. Coupling of galvanized steel parts with stainless steel parts components is not permissible. Preparations preceding welding should permit inside pipe diameter to fit, gap sealing to be within tolerances and root to be the same in size.

## Bolted Connections in Steel Structures

The Contractor shall make bolted connections in accordance with the details shown on the shop or erection drawings. Where necessary, washers shall be tapered or otherwise suitably shaped to give the nuts and heads of bolts a satisfactory bearing. The threaded portion of each bolt shall project through the nut not less than one thread and not more than five threads when fully tightened.  The length of bolt shall be such that there shall be at least two threads under the nut after tightening.

Facing surfaces (i.e. those surfaces required to transmit friction in connections with high strength friction grip bolts) shall be kept free of contamination by grease, rust, moisture, dust and the like.  If the surfaces are primed after fabrication, the primer shall be suitable for use in such connections and shall be protected from damage during transit or erection.

If contamination should occur, it shall be removed by appropriate means, e.g.:

- On coated surfaces, with a degreasing agent followed by washing and drying;

- On uncoated surfaces, as above, or by blast cleaning or wire brushing to clean steel.

These remedial measures shall be applied immediately before bolting the surfaces together.

High strength friction grip bolts shall be used in accordance with DIN or equivalent EN, ISO Standards using approved load-indicating washers to check bolt tension. They shall be tightened in accordance with the manufacturer’s recommendations and the tension shall be re-checked not less than three hours after the first tightening. The bolts shall then be re-tightened to the initial load.

## Crane Beams and Rails

Crane beams shall be aligned to ensure satisfactory performance of the crane under all reasonable circumstances and shall be generally in accordance with the crane manufacturer’s requirements.

Crane beam fixings shall be so designed as to allow adjustment to be readily carried out to accommodate misalignment of the structure. End stops shall be provided faced with hardwood blocks or similar approved buffer materials and shall be designed to withstand a fully loaded crane running into such that they will arrest the crane in the event of overrun under full load.

## Quality and Testing of Materials

The Engineer may require inspecting any metalwork during fabrication and to witness testing at the fabrication shop in addition to inspections and tests undertaken on the Site. The Contractor shall give the Engineer 21 working day’s notice of any operations, which the Engineer has notified to the Contractor in order that the Engineer may arrange to undertake such inspections.

Should the Contractor propose to use materials, complying with Standards other than those specified above, he shall receive approval from the Engineer. At least two weeks before ordering materials, the Contractor shall send a written notice to the Engineer giving the details regarding type, quality and quantities to be ordered.

Test certificates from the steel manufacturers shall be required to be submitted to the Engineer for the materials ordered. Material obtained from stocks shall be checked by the Engineer for the exterior defects either in the workshop or at the Site.

## Flooring, Rails and Other Metalwork

Flooring shall be fabricated from ribbed sheet or open mesh panels.

Flooring and its support shall be designed and manufactured to resist a uniform applied live loading of 7.5 kN/m² or such higher loading as may be specified or applicable and so that when loaded with the specified design live loading, the maximum deflection shall be not greater than 0.005 of the span or 10 mm, whichever is the lesser.

Flooring panels shall generally be removable by one man and the maximum weight of each panel shall not exceed 25 kg. Removable sections of flooring shall be provided with holes for lifting keys, keys to suit for each location, and be arranged to permit its removal without disturbance to support brackets, spindles, pipework, etc. Intermediate support members shall be provided as required and attached to the supporting structure.

Flooring shall be detailed and fabricated so that no cutting is required on site.  Supporting steelwork shall comply with the requirements of clauses for Structural Steelwork. Bolt holes in brackets and mountings shall be slotted to allow for adjustment of line and level. Mild steel continuous kerbing shall be provided for seating the flooring in concrete. Kerbing and other supporting structures for building into concrete shall have lugs welded on at maximum spacing of 600 mm. Panels shall be fixed with adequate flush stainless steel screws or clips so that movement is prevented.

The clear width of any access walkway shall be not less than 1,100 mm.

All members of assemblies shall be marked at the factory with distinguishing numbers, letters or marks corresponding to those of approved drawings or parts lists.

## Floor Plating

Floor plating shall have a raised pattern and be complete with cut-outs and in sizes suitable for removal by hand; steel flooring shall be less than 10 millimeters thick (as measured excluding the raised pattern).

Floor plating over openings in concrete or brickwork shall be set flush in mild steel framed kerbing provided with adequate integral lugs for building in. External floor plating and frames shall be mild steel, heavily galvanized or aluminum alloy.

## Open Mesh Flooring

Open mesh flooring panels shall be fabricated from hot dip galvanized mild steel with load bearing bars of flat section braced with round, square, or twisted bars perpendicular to and welded to each load bearing bar.

Panels shall be trimmed across the ends of load bearing bars by flats of the same cross section welded to each load bearing bar. Box-outs for works items shall be trimmed with curved or straight edge trimming as appropriate.

Panels shall be fixed with adequate flush stainless steel screws or clips so that movement is prevented.

## Access Covers

Internal and external access covers shall generally be designed and fabricated as specified for flooring. In situations, which warrant special measures to prevent pollution of filtered water, the covers shall be air tight, or cast.

External access cover such as sludge channels or chambers shall be steel open mesh, hot dip galvanized.

## Cast Iron Covers and Frames

Access covers and frames for use with manholes, chambers, draw pits and other structures shall be cast grey iron or ductile iron and shall comply with the relevant quality requirements of current Standards. Lockable covers shall be provided for the locations specified or otherwise vulnerable.

Access covers and frames shall have minimum openings of diameter 625 mm or of 600 x 600 mm or 750 x 750 mm and shall be capable of taking a load of 40 tone (400 kN) as per relevant standards.

Covers and frames detailed as sealed shall incorporated suitable neoprene or other synthetic rubber sealing rings, or other approved sealing methods.

Where covers are ventilated, the total area of ventilation and the size of individual slots shall be designed. Where covers and frames are supplied from manufacturers to standards other than those specified, the alternatives shall be designed and tested for loading equal to or greater than the covers specified, and the clear openings of the frames of the alternatives shall be equal to or greater than the covers specified.

## Surface Boxes

Cast iron surface boxes shall comply with the relevant specifications of relevant standards. The lid shall be chained to the frame.

## Step Irons

Step irons shall comply with relevant standards and be of the general purpose or pre-cast concrete chamber as appropriate.

Step irons of both purpose pattern shall have 80 mm tails.

## Handrailing

Handrail shall consist of galvanized steel with handrails and standards designed to withstand a horizontal force at handrail level of 740 Newton per meter run. The deflection of rails shall not exceed 0.8 percent of their span between standards and the deflection of standards shall not exceed 0.8 percent of their height. Standards and handrails shall be not less than 32 mm in diameter. Horizontal handrails shall be 1.100 mm high with an intermediate rail, knee-bar and kick-plate. Handrail height shall be measured vertically from finished floor level to the handrail centerline.

Sloping handrails shall be as specified for horizontal handrails but with the top rail 900 mm vertically above the line of pitch and stanchions vertical and spaced at not more than 1.5 m measured parallel to the line of pitch.

Horizontal mounting flanges shall be drilled for not less than three bolts with two bolts on a line parallel to and on the walkway side of the line of the handrail. Vertical mounting flanges shall be drilled for not less than two bolts the line through the bolts being vertical. Fittings shall be screwed or secured with grub screws. The standards shall be set at not more than 1.5 m centers. When provided in sections handrails shall be gained together with purpose made fittings secured by screws or grub screws.

Ladders and other openings shall be closed with two galvanized mild steel hanging chains, which shall be secured at one end and detachable at the other.

Bolts, nuts and washers shall be made of stainless steel.

The Contractor shall ensure that, unless specified to the contrary, all handrails shall be of uniform appearance and manufacture.

Detailed drawings of handrailings to be provided shall be prepared prior to fabrication for approval by the Engineer.

## Ladders - general

With exception of internal access ladders to water tanks, reservoirs and wet sumps, laddering shall be in steel (fully hot-dip galvanized). Ladders for internal access shall be in stainless steel. Generally all ladders shall be in accordance with relevant standards.

## Steel Ladders

Mild steel ladders shall generally be in accordance with relevant standards and shall have the following dimensions:

- Minimum thickness of stringer 12 mm

- Diameter of rungs 25 mm

- Rung spacing (uniform) between 230 mm and 260 mm

- Rung length 400 mm

- Minimum clearance to wall or other obstruction 200 mm.

The stringers shall be sized to suit the height of the ladders and the interval of the stringer supports.  Stringers shall be radiused over the top and drilled to receive the rungs that shall be welded to the stringers on each side of each stringer. The bottom ends of the stringers shall not be designed for floor fixing, but shall terminate at wall fixing supports at least 150 mm above the floor. All edges of stringers shall be ground smooth to remove burrs and sharp edges.

Ladders exceeding 3 m high shall be provided with safety hoops at intervals not exceeding 900 mm, with the lowest hoop 2.5 m above the ladder foot. Landings of open mesh flooring and handrails as specified shall be provided at intervals not greater than 9 m. Anchorage points may be provided for attaching safety harnesses instead of the above safety hoops where hoops would be inappropriate.

Ladders over three meters long shall have pairs of intermediate stringer stays at not more than 2.5 m centres.  Stays shall be fabricated to be continuous with the stringer section.  At least one fixing hole shall be provided at each palm type stay.

The Contractor shall provide detailed drawings prior to fabrication for approval by the Engineer.

## Non-ferrous Ladders

Ladders for internal access to reservoirs, tanks and submerged sumps shall be either made of stainless steel or GRP and shall be otherwise provided to the same specification for steel ladders. Safety hoops shall be avoided in these locations.

## Stairways

Stairways shall be designed for a loading of 7.5 kN/m² of plan area of the stairway. Steel stairways shall be provided with tubular handrailing’s, stringers of cross section suitable for the span and loading, and treads of open mesh flooring or ribbed sheet.

Except where specified otherwise, the rise between treads shall be uniform and between 150 mm and 175 mm. Stairways in the same area of the works and in similar locations shall have the same angle and height of rise between treads.

The width of the treads shall be between 250 mm and 300 mm. The width of the stairways shall not be less than 1,100 mm.

The stringer shall be mounted by means of angle brackets with slotted holes for adjustment of line and level.

## Miscellaneous – Dissimilar Metals

Where metals dissimilar to those specified above used in close proximity to structural steel members or their connections, contact between such metals and the steel shall be avoided unless the Contractor can demonstrate to the satisfaction of the Engineer that contact between the dissimilar metals will not lead to galvanic corrosion.

Contact between aluminum and aluminum alloy or galvanized mild steel will be permitted. For fixing aluminum to steel structures, bolts, nuts, washers and screws shall be unpainted stainless steel.

Where galvanized parts might otherwise become sacrificial anodes to the main structure, or where the electrolytic potential difference exceeds 250 mV, the parts shall be separated by an insulating medium of adequate strength.

## Aluminum Fittings

The materials for fittings made of aluminum shall be in accordance with the relevant standards.

## Opening Tools

Lifting keys and devices for unfastening screws shall be galvanized mild steel and supplied at the rate of one set for each five similar covers supplied, with a minimum of two sets of each particular type.

## Protection

Galvanized metal work shall be protected in accordance with the general painting and protective coating specification.

## Installation

Where metalwork is to be founded on and fastened to concrete, the Contractor shall specify the use one of the following methods as subsequently detailed:

- Bolting or screwing the metalwork to plates or angle sections with anchors set into the concrete structures or set into pockets left in the concrete structure.

- Setting the metalwork into pockets or recesses formed in the concrete structure.

- Bolting the metalwork to bolts set into the concrete structure or set in pockets or holes in the concrete structure.

- Bolting the metalwork to self-anchoring epoxy resin fixed bolts placed in drilled holes.

- Bedding the metalwork on cement-mortar placed on the concrete surface.

During installation, each item of metalwork shall be temporarily braced as necessary to resist all forces that are likely to be applied to it during installation, fixing and building in. Any bolted connections required as part of the installation operation shall be fitted and tightened before fixing bolts are tightened or pockets are grouted. The nuts of grouted or resin fixed bolts shall not be tightened until the grout has fully cured.

Small or lightly loaded items may be fixed using screws and approved plugs set in drilled holes.

# PUMPING EQUIPMENT

## General

The whole of the pumping works, machinery and apparatus shall be new and of first-class manufacture and shall be in accordance with EN 809 and EN 752-6.  Pumps characteristic curves (Q-H, Q-P2, Q-η, Q-NPSH) shall be supplied by Contractor and will be tested through their complete range at the manufacturer’s works. Test certificates will be presented to Engineer for approval. Test certificates will be provided for all pumps which shall be delivered irrespective of witness or non-witness tests. Hydraulic performance acceptance test will be in accordance with ISO 9906 Grade 2B. NPSH tests will be performed where the Engineer requires such tests.

The system design and pump curves shall illustrate the design conditions with operational efficiencies and power demands illustrated on the systems curve or envelopes and shall take account of at least the following conditions:

- When the pipework is new and in good condition;

- When the pipework is older;

- The full range of static heads occurring in the works;

- The various possible combinations of parallel pump operation.

Where possible the pumps shall be positioned so that a positive suction condition is obtained within the full curve of operation. The net positive suction head required (NPSHR) curve for the full range of operation shall be submitted which shall be compatible with that available to enable the pump to operate, without cavitation’s over the full range of flows at all liquid levels.

The design speed of any pump shall not exceed 1,500 rpm or more with approval of the Engineer. Pump unit assembly design and the method of supporting rotating assemblies shall ensure that no unit or shaft operates at a speed within 25 % of any critical speed.

The impeller of the pumps shall have minimum free passage of 75mm or less with explanation of the Contractor and approval of the Engineer.

The rotating parts of each pump shall be supported by substantial bearings. The design shall be such that no thrust is transferred from the pump to the motor shaft where these do not form an integral unit. The combined thrust and journal bearings shall be capable of reverse rotation at 150 % of full forward speed.  Dry installed pumps shall be equipped with double acting mechanical seals with sealing water /sealing liquid connection and shaft sleeve. Submersible pumps shall be equipped with double acting mechanical seals with leak detection sensor in the oil chamber between the two seals. All mechanical seals shall be of material SiC/SiC. Where shafts are susceptible to wear at bearings and glands, renewable sleeves shall be fitted. Wear rings and bushes shall be fitted to the casing and impeller at the points of running clearance. Where sealing and lubricating water is supplied to bearings and glands, it shall be free from suspended solids and the associated pipework shall be fitted with air release cocks and flow indicators.

Each pump shall be complete with all necessary ancillary equipment and fittings to render the unit complete and immediately ready for service. This shall include isolating valves, non-return valves, cooling water discharge pipework, gland leakage pipework, air release pipework, pressure gauges, gauge pipework, holding down bolts, access platforms and other items as appropriate. Where practicable, pressure gauges shall be wall mounted.

All studs, bolts and nuts used in the construction of the pumps shall be of stainless steel.

All intermediate shafting between pumps and motors shall be provided complete with adequate guards.  All pumps, where possible, shall be of the same manufacture and design to simplify spares requirements and maintenance.

## Pump Motor

The Contractor must ensure that the pump motors provided shall be of sufficient power, without overloading, to drive the pumps when operating at the worst static head conditions and when operating against worst pressure condition on Site at an ambient temperature of 40°C. The motors shall comply with the requirements of the Electrical Specifications.

The Contractor shall in his offer give details of motor power requirements; pump configuration and pump-motor set assembly dimensions.

All pump motors shall be equipped with thermal switches in the motor windings as a safeguard against overheating.

The following reserve capacities should be provided as a minimum with regard to a sufficient engine power to avoid blocking of the impeller:

| Power requirement of the pump in kW | Reserve capacity of the driving motor |
| --- | --- |
| up to 7.5 | ca. 50 % |
| 7.5 – 20 | ca. 25 % |
| 20 -50 | ca. 15 % |
| over 50 | ca. 10 % |

## Pump Bearings and Seals

The rotating element shall be carried on ball and/or roller bearings generously rated to ensure satisfactory and stable running without vibration under all conditions of operation. Bearings shall be suitable for an ISO B10 life of 50,000 hours at the pump speed. Seals shall be provided to protect the bearings from ingress of moisture, dust, sand and the particular climatic conditions prevalent at the Site.

- All bearings shall be according to DIN standard, SI unit dimensions where practicable.

- Pump bearings shall be external to the pump casing and be removable with the rotating element.

- Pump bearings shall be adequately rated ball or roller type and shall be arranged to take all radial and axial loads during start-up and running conditions.

- Pump bearings shall be mounted in dust-proof housing and provided with accessible lubricating points for grease gun greasing.

## Connecting Flange

Connecting flanges of horizontal and vertical split casing pumps, single end suction pumps and centrifugal sludge pumps shall be pressure rated to PN10 in accordance with relevant standards and shall incorporate two adjacent tapping plugged unless otherwise specified. Flanges shall be machined on face and edge and spot faced at the back.

## Pressure Gauge

The gauge mechanism shall be of the bourbon tube type with 100 mm diameter made of stainless steel and shall comply and be tested in accordance with DIN 16064 (or internationally acceptable standards).

- Gauge graduations shall be such that the gauge is never used continuously beyond 60 % the max graduations. Pressure gauges shall be graduated in bars or milli-bars.

- The face of the dial shall have a warning label marked in red attached thereto, reading

“IMPORTANT TURN OFF WHEN NOT IN USE”.

- All gauges shall be provided with glycerin filling to dampen pressure pulsation.

As far as possible, all pressure gauges shall be mounted either on walls, pump supports or brackets that do not have any vibration. Direct mounting at the pressure gauges on the pump casings or pipes must be avoided. They must also be mounted at a height suitable for ease of reading.

## Centrifugal Pump

Centrifugal pumps characteristics shall be stable with the delivery pressure falling continuously from a maximum at the closed delivery valve condition. Characteristics shall be non-overloading and unless otherwise specified all pumps shall be suitable for parallel operation with other pumps delivering to the same system. Except for axial flow pumps, all pumps shall be capable of being started and run for short periods with their delivery valves closed.

Pumps shall be designed to handle leachate, sanitary wastewater and sludge and shall run unattended for long periods. They shall be capable of passing solids up to a maximum sphere size of 75 mm; they shall pass stringy matter, rags, paper and plastics without choking.  Net positive suction head (NPSH) required for the pumps when pumping singly or in any combination as specified shall satisfy the NPSH available. Any deviation in NPSH of pumps shall be corrected on Contractor’s responsibility and expense.

Rotating parts of pumps shall be statically balanced during manufacturing and dynamically balanced after assembly.

Casings shall be so designed that the withdrawal of the impeller and drive end cover assembly can be affected without disturbing the pump casings.

Renewable internal “wear plates” shall be fitted or the casing shall be arranged for replaceable suction and gland plates.

Impellers shall be constructed of best nickel cast iron; they shall be smooth, well finished, and free from blowholes and imperfections, statically and dynamically balanced.

The impellers shall be securely fitted to pump spindles in such manner that they do not loosen or become detached when the pump is in operation, or when the impeller is rotated in the wrong direction by reversed flow or reversed motor connections.

The impellers shall be provided with means to prevent abrasive matter getting to the glands and, in fully shrouded impellers, to prevent the collecting of matter between the outer shroud and the pump casing.  Pump spindles shall be of stainless steel or high tensile steel and fitted with renewable stainless steel, nickel chrome or bronze sleeves to protect the spindles against wear over the distance it passes through the stuffing box.

Casing wearing rings shall be of best quality close-grained cast iron or nickel iron in a full circle and fully concealed and machined.

Casing wearing rings shall be deep and of adequate section to prevent sag and distortion when not in the seating and when stored.

Casing wearing rings shall be a light drive fit in the casing and be located in suitable recesses machined in the casing.

Casing wearing rings shall form a continuous and smooth surface without gaps or steps with the adjoining surfaces of the pump casing.

Intermediate shafting between vertical spindle pumps and motors shall, whenever possible be by “Hardy Spicier” transmission shafting with a splined slip joint above the pump and universal flexible couplings with needle roller bearings.

When the transmission requirement is too great for 'Hardy Spicier' shafting, solid transmission shafting may be offered with rigid flange type couplings utilizing fitted bolts.

Every length of transmission shaft complete with couplings shall be dynamically balanced.

The weight of transmission shafts shall be carried by trust bearings in the motor mountings.

Where intermediate bearings are required to steady the shafting, independent bearing supports must be provided.

All intermediate bearings must be provided with facilities for greasing and those in inaccessible locations must be piped to a common greasing manifold.

A 20 mm bore drainage pipe shall be provided for vertical spindle pump from the invert of the sill on the top cover and leading down into the floor drainage channel to allow drainage of gland seepage water.

Each centrifugal pump shall be provided with air release valve and pipe.

- Air/gas release pipe mounted at the top of the pump delivery branch of not less than 25 mm diameter. The pipework shall be arranged with crosses and tees and plugs at each section to permit rotating of each leg of the pipework.

- An automatic air release valve shall be fitted into the air/gas release pipework at a position convenient for maintenance.

The suction arrangements shall avoid peroration in the suction pipework and present a good flow pattern at the entrance to the impeller. The suction pipework shall not be less in diameter than the eye of the impeller.

If “water hammer” is possible, the necessary precautions shall be installed. In such cases the preventive measures shall be described.

Permissible frequency of starts per hour for electric motors and dry pump installation:

| Motor installation | Frequency of starts per hour |
| --- | --- |
| up to 4 kW | 15 |
| up to 7.5 kW | 15 |
| up to 11 kW | 12 |
| up to 30 kW | 12 |
| above 30 kW | 10 |

## Submersible Pump

The pumps shall be designed for handling of leachate, wastewater and water and shall be capable of passing solids up to a sphere size of 75 mm or less with explanation of the Contractor and approval of the Engineer. They shall pass stringy matter, rags, paper and plastics without clogging.

The pump casings shall be of cast iron, and shall be provided with a renewable suction end, wear plate, a discharge cover and a support foot.

The impellers shall be designed to give non-overloading characteristics over the complete working range of the pump and shall be capable of conveying liquids, which will evolve gas.

The pumps shall be capable of working for long periods without cleaning or attention and special precautions shall be taken to avoid wear on working surfaces due to grit.

Sealing ring, sealed for life shall be provided between motor and pump.

The unit shall be supplied with an adequate length of suitably sheathed flexible cable and pass through a watertight gland on the entry of the motor body.

The pumps shall be installed as a permanent wet sump installation and each unit shall be complete in all respects with guide rails complete with upper and lower fixing brackets, lifting chain, automatic pump discharge branch connection, cable guides and holders to allow pumps to be raised or lowered without entering the sump.

Glands shall be fitted with mechanical seals (Material: SiC/SiC) with automatic seal supervision in the oil chamber.

The shafts of pumps shall be made wear resistant with protection sleeve where they pass through the mechanical seal.

The pumps shall be suitable for operation on a 400 V, three phase, 50 Hz supply.

The pump motor shall be of squirrel cage induction type, with protection class IP 68, ex-rated and be continuously rated for use in sewage at ambient temperature.

The motor shall be protected with a moisture resistant Class “F” insulation capable of resisting temperature of up to 155°C. For monitoring moisture intrusion into the motor cavity, the pump shall be supplied with an additional and independent moisture sensor in the motor cavity.

Each pump shall be fitted with a removable lifting handle and supplied with a connected stainless steel lifting chain to facilitate removal. The upper end of the chain shall be conveniently anchored in an approved manner and location. Chain ends shall be fitted with stainless steel shackles and pins.

Permissible frequency of starts per hour for electric motors and wet pump installation:

| Motor installation | Frequency of starts per hour |
| --- | --- |
| up to 4 kW | 30 |
| up to 7.5 kW | 25 |
| up to 11 kW | 25 |
| up to 30 kW | 20 |
| above 30 kW | 10 |

## Submersible Drainage Pump

Each sump pump shall be installed as a fixed unit and shall be complete with all necessary pipework, level controls, motor starter and cabling.

Sump pump shall be of the submersible type with pump units suitable for operation on 400 volts three phase, 50 Hz supply. It shall be capable of handling floor drainage from the various pump chambers and floor ducts.

The sump pump shall be of heavy construction with impellers made of high-grade abrasive resistant material having non-overloading characteristics.

Discharge pipework and valves shall be provided with check valve and gate valve and shall discharge into an adjacent chamber channel or pipe.

Discharge pipework shall be 50 mm minimum nominal bore and the pump shall be capable of passing sphere of up to 18 mm diameter.

Each pump shall be fitted with a removable lifting handle and supplied with a connected stainless steel lifting chain to facilitate removal. The upper end of the chain shall be conveniently anchored in an approved manner and location. Chain ends shall be fitted with stainless steel shackles and pins.

## Portable Site Drainage Pump

Portable site drainage pumps shall be provided complete with all necessary hoses, cables, starter and support rope suitable for transportation to and use at any location on the works.

The pumps shall be of submersible type suitable for operation on a 400 V, three phase, 50 Hz supply.  Each pump shall be capable of handling sludge, liquids containing grit, and solids as found in pump suction sump drainage, tanks and general site drainage duties.

The pumps shall be of heavy construction with open type impellers of high abrasive material having nonoverloaded characteristics and shall be generously rated for prolonged operation. The pump shall be suitable for operation in liquids that have been subject to direct sun and the rating must be continuous when operated at any point on the characteristic curve between closed valve and zero head.

The pumps delivered shall be suitable for the connection of flexible hoses utilizing a quick release type coupling.

Discharge hoses 15 m long of 50 mm diameter rubber with fabric or cord reinforcement shall be provided for each small pump, each length fitted with quick release type metal coupling to suit the pump.

Large pumps shall be rated to deliver 15 - 20 liters per second against heads up to 16 meters. The pump shall be capable of passing solids up to 75 mm diameter sphere.

Small pumps shall be rated to deliver 5 - 7.5 liters per second against heads up to 10 m. The pump shall be capable of passing solids up to 18 mm diameter sphere.

Manual control shall only be provided for the portable pumps. The motor-overheating protection by thermal switch in the windings shall be included in the control circuit.

## Horizontal Centrifugal Pump

Horizontal single stage casing pumps in modular construction with single vane impeller not self-priming.

Casing shall have an interchangeable wear ring, axial inlet nozzles and radial top discharge nozzles.  Fitting and removal of the rotor shall be possible axially without having to remove the pump from the pipeline or the foundation.

Shaft bearings are sealed for life anti-friction bearings. The bearings are to be sized to guarantee a service life of 50,000 hours.

Shaft Sealing; at the drive end: mechanical seal independent of direction of rotation SiC/SiC material combination at the rubbing surfaces.

Common, permanent liquid quench consisting of paraffin oil.

Assembly parts: Belt drive, inclusive baseplate, belt pulleys, belts, belt guard, masonry bolts dowels.  Materials specification:

- Casing parts in contact with media  	grey cast iron 25

- Impeller 	 	 	 	grey cast iron 25

- Discharge Cover 	 	 	grey cast iron 25

- Wear ring  	 	 	 	grey cast iron 25

- Shaft 	 	 	 	 	1.4021.05

- Bearing Bracket 	 	 	 	grey cast iron 25.

Each pump shall be complete with all necessary ancillary equipment and fittings to render the unit complete and immediately ready for service, as required in the pump-sections before.

## Positive Displacement Pump (Progress cavity pump)

Positive displacement pumps (eccentric pumps), whether rotary or reciprocating, shall be self-priming and of the horizontal helical rotor and fixed stator type. They shall be driven by electric motors and mounted together with their motors on a combined base plate or frame. Rotors shall be long enough to provide more than 360 degrees of helical passage.

Stators shall be of synthetic rubber molded into a rigid outer barrel. Suction and delivery connections shall be flanged.

Pumps shall be provided with dry running protection (DSP) of the rotor by conductivity sensor or thermal stator protection.

Max. relative velocity between stator and rotor to be 1 m/s.

Pumps shall be provided with pressure relief valves to prevent generation of excessive pressures and, unless specified otherwise, means to minimize pressure fluctuations. Pressure relief valves may be integral parts of the pumps or fitted externally. Liquid bled off from pressure relief valves shall be returned to the suction side of the pump or to the suction sump. Each suction and discharge pipeline of positive displacement pumps will be equipped with connection for service water wash out.

Positive displacement pumps, which are belt driven, shall incorporate means to prevent overstressing the belt drive by using a torque-limiting clutch.

Positive displacement pumps comprising, but not limited to:

- Horizontal dry-mounted pump

- Common base plate for pump and motor

- Three phase motor

- Progressive cavity type complete with hand-wheel controlled variable speed drive (if required by ER)

- Pressure switch for overpressure protection and temperature control element for stator protection

- Suction switch for low pressure protection and temperature sensing element for stator protection.

Materials specification:

- Casing parts in contact with media   	grey cast iron 25

- Shaft 	 	 	 	 	Cr-Steel 1.4021

- Coupling rod 	 	 	 	Cr-Steel 1.4021

- Rotor 	 	 	 	 	hardened tool steel 1.2436

- Stator 	 	 	 	 	Perburan SB

- Shaft sealing 	 	 	 	gland packing or equal.

## Booster Unit

Multistage centrifugal vertical pumps shall be provided as booster pumps for the service and firefighting water supply system.

The connection to the distribution network shall be via a hydro-pneumatic pressure tank. The pressure tank shall be fitted between the booster pumps and the system. The wetted parts of the pumps must be made in stainless steel and materials resistant to chlorine solution.

The booster units shall be driven by a speed regulation system.

The pressure pipework shall be provided with non return valve and gate valves and shall be of stainless steel and flanged.

The booster units shall be supplied with pressure switches for cut out at low intake pressure (pressure smaller than 15%) and switches for the pump control.

The booster units shall be provided with local control panel. The panel shall include all necessary connection devices, fuse, protection switches, control transformer, digital controller with analogue inputs, programmable logic controller (PLC), selector switch and push buttons. For transmission of operation and fault signals voltage-free contacts shall be provided.

The electrical system has to be completely supplied, installed, connected, tested and commissioned, including all documentation and all cabling between the switchboards and the electrical consumers and cable to feed main power to the works will be supplied by the Employer/Investor and has to be connected by the Contractor.

All signals relevant to monitor the function of the works have to be brought potential-free to terminal strips. All electrical components have to be of high quality.

## Macerator

In line macerator shall be used for crushing of solids at various stages of landfill and its treatment processes.

- Crushing elements are the rotating impeller and the stationary cutting ring. By means of two crushing stages (cutting tips / cutting teeth and slotted cutter disc (toothed rim), grain sizes of 3.5 mm or fibre sizes of 1.5 cm² should be obtained;

- The crushing elements should be arranged symmetrically for the operation of the macerator in both directions of rotation, which increases the service life considerably. A higher wear-resistant mechanical seal must be provided as shaft seal;

- Materials specification:

  - Casing parts in contact with media 	grey cast iron 25

  - Impeller 	 	 	 	G-X 1 0 (Cr Ni 1 8 8 with stellite segments)

  - Cutting Ring 	 	 	 	G-X165 (Cr Mo V 12 hardened 60 HRC)

  - Discharge Cover 	 	 	grey cast iron 25

  - Wear ring 	 	 	 	grey cast iron 25

  - Shaft 	 	 	 	 	1.4021.05

The complete system for the seal water supply to admit the macerator shaft seal for lubrication and cooling purposes should be delivered, including the complete pipework, instruments and accessories for the regulation and control of the seal water flow.

# VALVES

## Gate valves

Gate valves from 50-1000 mm shall be in accordance with EN 1171 (Cast iron wedge and double disk gate valves for general purposes).

Gate valves shall be of the double-flanged cast iron wedge-gate or parallel slide type, unless otherwise specified. They shall have a cast iron body with renewable gunmetal faces on body and wedge, and a bolt-on cast iron bonnet.

Where gate valves above 350 mm bore are mounted with the spindle in the horizontal plane, the valve bodies shall be fitted with renewable machined gunmetal gate slides, and the gates with renewable hard bronze shoes, accurately machined to reduce sliding friction.

All gate valves above 500 mm bore shall be provided with jacking screws. Valves above 350 mm bore, where mounted in the vertical plane, shall be provided with feet.

Unless otherwise specified, each valve shall be provided with a suitable hand wheel of adequate diameter for the duty required. Gearing shall be supplied where necessary, to ensure that the required operating force applied by hand to the rim of the wheel does not exceed 250 N.

Hand wheels shall have smooth rims and the direction of closing, which shall be clockwise, cast on them.

Valve stems shall be of forged aluminum bronze or stainless steel, machined all over with a machine cut, robust trapezoidal or square form thread, operating in gunmetal nut.

Stem seals shall be the O-ring type with two such seals arranged for easy replacement of O-rings.

Extension spindles, headstocks and foot brackets shall be provided where required for normal operation. Where extended spindles require to be operated at open flooring level, spindle guides or guide brackets shall be provided close to flooring level.

Headstocks for non-rising spindle installations shall incorporate a valve position indicator.

Extension spindles shall be of stainless steel or manganese bronze and shall conform to the requirements for valve stems, with the exception of non-threaded sections, which may be of mild steel. Extension spindle couplings shall be of the drilled “muff” type and provided with a nut and bolt for securing the spindle to the valve stem, which shall likewise be drilled to accept the bolt.

Extended spindles for all motorized/actuator operated valves shall be provided with thrust tubes between valve and headstock in order to absorb the thrust in both directions of operation. Thrust tubes shall incorporate all necessary fixing brackets and spindle guide plates.

Where valves are required to be operated by tee keys, spindle caps shall be fitted. The caps shall be drilled and each provided with nut and bolt for securing to the spindle, which shall likewise be drilled to accept the bolt. Each cap where fitted shall be supplied complete with operating tee key.

The buried valves on the distribution pipe systems shall be operated with extension spindles as shown on the typical drawings.

The extension spindles shall be protected with a 90/86 tube made of PVC or ductile iron. The extension spindle shall be guided at the top with a combined protection tube cover and spindle guide made of the same materials.

The square end of the extension spindle shall be protected with an adjustable surface box made of ductile iron with a possible maximum extension of 150 mm.

The surface box shall be supported on a 150 mm thick, 300x300 mm² concrete slab.

One T-handled key for operation shall be supplied with every 25 valves.

Surface boxes, extension spindles and protection tubes shall be painted with epoxy coating color blue RAL 5015

All hand wheels, headstocks, foot brackets, guide brackets and thrust tubes shall be of cast iron.

Valves shall carry identification marks and/or plates in accordance with the applicable standards. Those for use on process plant shall carry an additional brass plate carrying valve identification and a brief description of its function.

Valves shall be sized to have the same clear openings as the pipes they are fitted to. They shall have flanges to EN 1092-2 NP 16 and shall be capable of withstanding the same test pressures as the pipeline on which they operate. All nuts and studs subject to vibration shall be fitted with spring washers or locking tabs, unless otherwise specified.

All materials used in manufacture of the valves shall conform to the following minimum standards:

- Cast iron:*		EN 1561	Grade 220,

- Gunmetal:		EN 1982	Grade LG2,

- Aluminum bronze:	EN 12420	Grade CA104,

- Stainless steel:		EN 10250-4	Grade 431S29,

- Manganese bronze:	EN 12167	Grade CZ114,

- O-rings:	Molded rubber.

## Check valves

Check valves shall be of the quick action type, designed to minimize slam on closure and to minimize hydraulic losses.

Swing type check valves for sewage and sludge shall be used. The body of the valve shall be made of cast iron GG25 and the ball or door from cast iron rubber coating.

The door hinge pin/shaft shall extend through a sealing gland on the side of the body, and be fitted with an external lever to permit back flushing. Glands shall be of the “O” ring type.

The valve door shall be weighted to suit the application and the lever shall be of the heavy-duty type, designed for the addition of external weights, should these be required at some future date.

All check valves shall be suitable for operating in the horizontal plane, unless otherwise specified.

Covers shall be provided to allow ample access for cleaning and service and shall be supplied complete with tapped bosses fitted with air release cocks.

Valves above 350 mm bore shall be provided with feet.

The design of the valve body shall be such that there is adequate clearance around and at the back of the door to minimize jamming by rags or debris. Stops shall be provided to limit the back lift of the door; these shall be positioned to prevent fouling.

The hinge pin/shaft shall be stainless steel and preferable square in section, to ensure positive location of the door. If circular shafts are utilized, the back flushing lever shall be located on a squared section, the diagonal dimension of which shall be equivalent to the full diameter of the shaft. Both door and lever shall be positively and securely fixed to the hinge pin/shaft. Grub screws, pins (parallel or taper) or clamps will not be acceptable. All internal fixing devices shall be of stainless steel.

Valves shall carry identification marks and/or plates in accordance with EN 12334.

They shall have flanges to EN 1092-2 PN 10 and shall be capable of withstanding the same test pressures as the pipeline on which they operate. All nuts and studs subject to vibration shall be fitted with spring washers or locking tabs, unless otherwise specified.

All materials used in the manufacture of check valves shall conform to the following minimum standards, unless otherwise specified:

- Cast iron:	EN 1561	Grade 220,

- Gunmetal:	EN 1982	Grade LG2,

- Stainless steel:	EN 10250-4	Grade 431S29,

- O-rings:	Molded rubber.

## Air and gas relief valves

Air and gas relief valves shall be of the double orifice pattern with grey or ductile cast iron bodies. The inlet flange shall be faced and drilled in accordance with EN 1092-2 PN 10.

The valves shall be adequately sized for the release of gas from the pipeline (or other container) without restriction of rate of filling or flow due to back-pressure. Air shall be allowed to enter at a rate sufficient to prevent excessive reduction of pressure in the pipe during pipeline emptying.

Valves shall be designed to prevent the operating elements being in contact with the pipeline liquid (wastewater) by approved means, such as the provision of an auxiliary float and chamber sufficiently large to isolate the orifice valves and seats throughout the rated operational range.

Air valves shall be fitted with an isolating gate valve.

In applications where the pipeline characteristics may lead to column separation with consequent possibility of surge conditions, a vented non-return valve shall be provided which allows air to enter freely on separation but controls expulsion of air/gas as the liquid pole rejoins.

In applications where the hydraulic conditions are such that pressures fall below atmospheric pressure during normal operation, and where air inflow at that time could induce surge conditions, an air inflow check valve shall be incorporated.

All air and gas relief valves and associated isolating valves shall be tested and capable of withstanding the same test pressure as the pipeline or vessel on which they operate.

All materials used in the manufacture of the valves shall conform to the following minimum standards:

Float chamber:				Grey cast iron to EN 1561,

Flange and cover:				Grade 220 or spheroidal graphite iron EN 1563,

Liquid float:				Copper, polycarbonate or approved equivalent,

Air float valve and guide:		Polycarbonate or approved equivalent,

Orifices, guides, mechanisms:	Stainless steel to EN 10250-4 Pt. 4,

Sealing rings:				Molded rubber or suitably approved equivalent.

## Pressure control valves

Pressure control valves for pipe bores of 80 mm diameter and above, used for pressure reduction, pressure sustaining or pressure relief, shall be of the double flanged type, of grey or ductile cast iron. Operation shall be by the use of an integral auxiliary actuating mechanism suitable for the application. For bores of less than 80 mm diameter, a direct spring controlled valve may be used.

Valves shall be adequately sized to control the flow and pressure differential required for the application, with an accuracy of +2.5% of the set value. They shall be capable of operating at a sustained pressure of 20% in excess of the nominal declared working pressure.

Valves shall be sized to ensure that their full capacity will be more than adequate to accept the desired maximum flow at the minimum required differential pressure.

Flanges shall comply with EN 1092-2 and be suitable for the sustained pressure detailed above, but in any case not less than PN 10.

The main valve disc, ported guide and pressure differential piston shall be of high grade cast iron or gunmetal as appropriate. For cast iron discs, the seating face shall be in gunmetal, synthetic or other approved material to suit the application. The piston cylinder shall be fitted with a bronze liner.

The piston shall be fitted with rings suitable for maintaining a pressure seal with the cylinder. These shall be suitable for the maximum designed pressure differential of the valve.

Where specified, an externally projecting indicator rod shall be fitted to the top of the piston to indicate the position of the main valve disc.

The main pressure control valve operation shall be actuated by a hydraulic differential pressure system in balance with a spring loaded bellows type diaphragm, the reference being bled from the inlet and outlet of the main valve.

The diaphragm spring shall be adjusted by a screw to cover the range of pressure adjustment specified for the valve application.

The control circuit connections and application of reference pressure shall be arranged to suit the requirement, whether for pressure reduction, pressure relief or to sustain a constant pressure.

Monitoring orifices shall be protected by suitably fine mesh strainers on the pipeline side, the elements, strainers, pipeworks and fittings being in suitable corrosion-resistant materials.

A pressure gauge shall be fitted to indicate the regulated pressure.

Where required, a needle valve shall be incorporated in the connection from the “relay” valve to the main valve piston cylinder to adjust the rate of change of pressure.

When the main and relay valves are closed, the main valve seating shall be “drop tight” under the inherent hydraulic pressure.

Where specified, an electric or hydraulic servo device shall be incorporated within the valve to adjust the spring screw for remote pressure adjustment.

Before the application of paint or other similar treatment, valves shall be Works tested hydrostatically, the test pressure for the body and disc being 1.5 and for the seat 1.0 times a maximum sustained pressure of 20% in excess of the nominal declared working pressure.

All materials used in the manufacture of the valves shall conform to the following minimum standards:

Body, cover and disc:			Cast iron to EN 1561, Grade 220 or spheroidal graphite iron EN 1563,

Valve guide and rings:			Gunmetal to EN 1982, Grade LG2,

Liner:			Bronze to EN 1172,

Seating face:		Gunmetal to EN 1982, synthetic or other approved material as appropriate,

Indicator rod:			Stainless steel to EN 10250-4, Part 4,

Actuating valve body:			Bronze to EN 1172,

Spindle:			Stainless steel to EN 10250-4, Part 4,

Valve face:			Nylon,

Diaphragm:			Reinforced synthetic rubber or bellows approved equivalent,

Orifice body and plate:	Bronze to EN 1172,

Strainer:			Copper wire cloth,

Spring:			Spring steel.

All detail parts not listed shall be in homogenous corrosion-resistant material.

## Butterfly valves

Butterfly valves shall comply with EN 593 and be of double flanged or wafer type, with metal or resilient seating and grey or ductile cast iron body.

Butterfly vales shall be only used for clean water or air pipelines.

Valves shall be “drop tight” at closure and the diameter not less than that of the nominal pipe bore.

The disc shall be in grey or ductile cast iron with a resilient seating ring in molded rubber, or other material to the approval of the Engineer, located in a landing on the disc and secured by a gunmetal retaining ring fixed with screws made from homogenous corrosion-resistant material.

The shaft may be in one piece or attached as two stub ends on opposite sides of the disc. The means of attachment of the shaft to the disc shall be by using fixings in a homogenous corrosion-resistant material of a pattern which precludes the assembly becoming loose in operational service. Grub screws, pins (parallel or taper) or clamps will not be acceptable.

The shaft shall rotate in bearing bushes fitted with grease lubrication facilities.

For valves exceeding 350 mm bore, a suitable lubricated axial thrust bearing shall be fitted.

Glands shall be of the double O-ring type and shall be fitted on the operational shaft extension to seal the pressure side of the valve. The design shall be such as to facilitate O-rings replacement without removal of the valve from the pipeline.

Unless otherwise specified, each valve shall be provided with a hand wheel and gearbox, proportioned so that the required operating force applied by hand to the rim of the wheel does not exceed 250 N.

The direction of closing shall be clockwise and shall be cast on the hand wheel.

A valve position indicator, to show the position of the disc, shall be provided on the valve operating gear.

Suitable stops shall be incorporated to prevent movement beyond the disc “fully open” and “fully closed” positions.

A gunmetal seat ring shall be secured to the body by screws in homogenous corrosion-resistant material, in a manner which precludes the assembly becoming loose in operational service.

Valves shall carry identification marks and/or plates in accordance with the applicable standards and those for use on process plant shall carry an additional brass plate carrying a valve identification and a brief description of its function.

Valves shall be sized to have the same diameter as the pipes to which they are fitted. They shall have flanges to EN 1092-2 PN 10 and shall be capable of withstanding the same test pressures as the pipeline on which they operate. All nuts and studs subject to vibration shall be fitted with spring washers or locking tabs.

All materials used in manufacture of butterfly valves shall conform to the following minimum standards:

Body and disc:	Cast iron to EN 1561, Grade 220 or spheroidal graphite iron to EN 1563,

Shaft:	Stainless steel to EN 10250-4, Part 4,

Sealing ring:	Molded rubber or suitably approved equivalent,

Retaining ring:	Gunmetal to EN 1982, Grade LG2 and Seat,

O-rings:		Molded rubber.

## Dismantling joints

A sufficient number of dismantling joints shall be incorporated in each pipeline. The dismantling joints shall be made of GGG50 sphero cast iron and shall have an axial adjustment capability of at least  25 mm to facilitate easy dismantling and installation of pumps, valves, non-return valves, measuring devices, etc. Threaded rods and nuts through two opposite flanges shall secure the dismantling joint in the position determined during installation, so that the system represents a rigid connection of two adjoining pipes.

## Support of pipeworks and valves

All necessary supports, including structural steelworks, foundations, hangers, saddles, sliding shoes, slings, expansion pieces, fixing bolts, foundation bolts, fixing and anchor points and all other attachments, shall be supplied to support the pipeworks and its associated equipment in an approved manner. Valves, meters, strainers and other devices mounted in the pipeworks shall be supported independently of the pipes to which they connect.

Wherever possible, flexible joints shall be provided with tie bolts or other means to transfer longitudinal thrusts along the pipeworks as a whole, so that the external anchorages at blank ends, tees and valves may be kept to a minimum. The Contractor shall indicate on his working drawings what thrust blocks are required to anchor pipeworks supplied by him.

All brackets or other forms of support which can conveniently be so designed, shall be rigidly built up of steel sections by riveting or welding, in preference to the use of castings.

No point of passage of pipes through floors or walls shall be used as a point of support, except with the approval of the Engineer.

All brackets and fixings shall be hot-dip galvanized.

# PENSTOCKS AND HAND STOPS

## Penstocks general requirements

Penstocks shall be made of stainless steel 1.4404. The frames, doors, sealing faces and spindles of each type of penstock shall be as specified in the appropriate sections herein.

Unless otherwise stated, each penstock shall be provided with a suitable hand wheel of adequate diameter for the duty required and gearing shall be supplied where necessary to ensure that the required operating force applied by hand to the rim of the wheel does not exceed 250 N. The height of the hand wheel shall be approximately 0.9 m above operating level, unless otherwise stated.

Hand wheels shall have cast on them, the direction of closing which shall be clockwise. Vandal and weatherproof clear polycarbonate tube covers shall be securely fitted to protect the threads of rising spindles. Each tube shall be clearly and permanently engraved to indicate the position of the penstock.

Spindles shall have machine cut robust trapezoidal or square form threads. They shall be of stainless steel or manganese steel or manganese bronze. Extension spindle couplings shall be of the “muff” type and they shall be drilled and provided with a nut and bolt for securing the spindle to the penstock spindle head, which shall likewise be drilled to receive the bolt.

Where extended spindles installations require to be operated at elevated floor level, spindle guides or guide brackets shall be provided close to the floor level. The maximum distance between spindle guides shall not exceed 2.5 m.

Where penstocks are required to be operated by tee keys, spindle caps shall be fitted. The caps shall be drilled and each provided with nut and bolt for securing to the spindle, which shall also be drilled. Where caps are fitted, they shall each be supplied complete with operating tee key.

All hand wheels, headstocks, foot brackets and guide brackets shall be of cast iron. Thrust tubes shall be cast iron.

All penstocks shall be of the non-rising spindle type, unless otherwise stated, and provided with hand wheels or motor driven gears.

Headstocks and foot brackets shall be provided, where the latter are specifically called for. Guide brackets shall be provided where necessary. The spindles shall be fitted with thrust collars and arranged so as to transmit the thrust arising from operation of the penstock directly to the penstock frame. Where headstocks are required, they shall incorporate a penstock position indicator.

Penstocks shall be watertight under the conditions of head and direction of flow as stated in the appropriate sections of the Particular Technical Requirements.

Framework, guides, thresholds, blades and the spindles shall be of stainless steel according to EN grade 1.4404.

All other materials used in the manufacture of penstocks shall conform to the following minimum standards:

Cast iron:	EN 1561		Grade 180;

Gunmetal:	EN 1982		Grade LG2;

Stainless steel:	EN 10250-4, Pt 4	Grade 316 S31;

Manganese steel:	EN 10250-4, Pt 4	Grade 150 M19;

Phosphor bronze:	EN 12167		Grade PB 102.

The metal sealing faces shall be formed from accurately machined gunmetal or bronze strips. The nut in the penstock blades with non-rising spindle shall be of gunmetal.

## Hand stops

Hand stops shall have stainless steel frames with stainless steel doors according to EN grade 1.4404.

Hand stops shall be suitable for channel or wall mounting according to the installation requirements.

Hand stop doors shall be provided with hand-slots to facilitate operation and a peg or chain shall be provided to hold the door in the open position. Pegs or chains shall be of stainless steel or galvanized mild steel.

On deep channels or where specified, hand stop doors shall be provided with lifting handles. Lifting handles shall be of identical material to the doors and guide/retaining brackets shall be provided.

All materials used in the manufacture of hand stops shall conform to the requirements for penstocks specified herein.

# ELECTRICAL ACTUATORS FOR VALVES AND PENSTOCKS

Where required, penstocks and valves shall be operated by means of electrically driven actuators with integral reversing starters.

Each actuator shall be fully weatherproof and fitted with anti-condensation heater, upper and lower limit switches and torque switches.

All local controls shall be protected by a lockable cover.

The electrical supply available is 400 Volts, 3 phases, 4 wire 50 Hz, and the unit shall incorporate a 400/230 to 110 Volts transformer for control circuits.

In area where emission of explosion gases are possible, all motors will be in adequate Ex protection.

Each actuator shall be adequately sized to suit the application and be continuously rated to suit the modulating control required. The operating gear of all penstocks shall be capable of opening or closing the gate against an unbalanced head equal to the maximum working pressure.

The gearbox shall be oil or grease filled, and capable of installation in any position.

Alternative hand operation shall be possible, and the hand wheel together with a suitable reduction gearbox, if necessary, shall be of adequate dimensions for easy operation by two men. The motor drive shall be automatically disengaged when under manual operation. Hand wheels shall be rotated clockwise to close the valves, and shall be clearly marked with the words “Open” and “Close” and arrows in the appropriate directions. The rims of hand wheels shall have a smooth finish.

All actuators, with the exception of rising spindle penstocks, shall be equipped with indicators showing whether the penstock is fully open or closed. A transparent PVC cover shall be fitted to protect the thread of the rising spindle.

All operating spindles, gears and headstocks shall be provided with adequate points for lubrication.

# PRESSURE AND VACUUM GAUGES

Gauges shall be provided for all dry installed pumps on the suction and pressure side and on blowers on pressure side and for all other equipment where necessary.

Pressure and compound gauges of approved manufacture with an accuracy of ±2% shall be provided and fixed directly to and at the same level as the delivery and suction branches of each dry installed pump. The gauges shall be fitted with diaphragm type isolating valves and with siphon pipes. Gauges shall not be connected to air release or auxiliary suction pipes.

All gauges shall have concentric dials of 150 mm in diameter, pressure gauges being graduated in meters head, and compound gauges in cm of mercury and meters head. Gauge graduations shall be such that the gauge is never used continuously beyond 60% of the maximum graduation. The face of the dial shall have a warning label marked in red attached thereto reading in the Serbian language: “Important: Turn off when not in use”.

The gauge mechanism shall be of the Bourdon tube type, having stainless steel movements and shall comply with EN 837-1. It shall be sealed from the liquid being measured by means of a diaphragm or capsule and be filled with silicone oil.

All gauges shall be fitted with a pressure snubber to dampen pressure pulsations.

Before the gauges are delivered to Site, each gauge shall be tested in accordance with EN 837-1 and a test certificate for each gauge, confirming that they are of the required accuracy, shall be sent to the Engineer. Further copies of the test certificates shall be incorporated in the operation and maintenance manuals.

# Lifting equipment

## General

Lifting gear and associated equipment shall comply in general with EN 13001-1, EN 13001-2, DD CEN/TS 13001-3-2, EN 13001-3-1, suitable for class 2 duties.

The assemblies shall be suitable for lifting the heaviest single item of equipment within the working area. The load hook, incorporating a ball swivel joint, shall extend to within 1.0 m of the lowest working level, whilst sufficient headroom shall be allowed below the crane hook to enable the tallest item of machinery to clear the motor floor level by 1.0 m.

## Travelling cranes

Travelling cranes shall be manually or electrically operated and include travelling bridge, crab and hoist, electrical motor gears and plant where applicable, operation and maintenance instructions and all other necessary items like bolts, buffers, fixings, etc.

Cranes, if electrically operated, shall be supplied complete with flat cables on roller suspensions, controls and motor gears giving speeds in both horizontal directions of normal 10 m/min and crawling 1 m/min. The hoisting speed shall be approximately 2 m/min with crawling speed of 0.2 m/min.

Electrical cranes shall be controlled from the floor by a mobile pushbutton master controller movable along with the crab or the hoist to control movements in all directions and speeds.

The single or double girder crane bridges shall be the underslung type and be fabricated from universal beams or high grade steel plate box section girders which, together with end carriages of rolled steel sections, shall form a single welded fabrication adequately braced and stiffened to give a rigid structure capable of withstanding all loads imposed.

Double girder bridge beams shall be fitted with crab rails securely welded to their upper flanges.

The flat-bottomed crane rails to ISO 6305-2 shall be complete with all fixing bolts, holding down bolts, fishplates, end stops, buffers, e. The crane rails shall be supported on steel supports bolted to poles. Allowance shall be made for expansion of the rails.

The end carriages shall be provided with derailment and wheel brake protection, preventing the carriages falling more than 10 mm.

The long and cross travel wheels shall be double flanged and be made of forged or cast steel. The rims of the wheels shall be machined accurately to same diameters and with a form fitting the rails. The wheels shall be fitted with roller bearings and be at least 250 mm in diameter.

The travelling bridge shall be fitted with four buffers as end stops in conjunction with stops at the limits of the travelling. The buffers shall absorb the kinetic energy from the dead load of the crane.

The travelling gears and the hoists for electrically operated cranes shall be driven by electric motors fitted with automatic electro-mechanical brakes for the motors and automatic limit switches for the hoists. The brakes shall be the heavy-duty type, which shall engage automatically when the power supply is cut or fails.

The motors shall be capable of working continuously at full load for one hour and shall have the enclosure protection form IP54. In area where emission of explosion gases are possible, all motors will be in adequate Ex protection.

Safety devices, such as fuses, relays for overloads and limit switches, alarm bells, etc. as well as the main switches for the crane, shall be located in a separate cabinet. This cabinet shall also house the transformers for the control circuits and the fuses.

The rope pulley shall be in accordance with EN 892 and EN 12273.

The crane hook shall be designed for the relevant load and comply with EN 13001-3-5:2016. A ball swivel device shall be incorporated into the hook as specified above.

The gearings shall be totally enclosed in gearboxes and running in oil. The wheel gears may be grease lubricated.

The maximum load of the crane shall be marked on the crane with painted figures in the Serbian language easily readable from the floor.

The complete crane shall be painted in accordance to General Technical Requirements, surface “A”.

Before handing over to the Employer, the crane shall be tested with a load of 125% of the maximum marked load in accordance with the applicable standard. The Contractor will be responsible to obtain all certification and licenses required for lifting equipment by the national regulations and laws.

## Monorail cranes

Monorail cranes will be with electric hoist or manually operated hoist mechanism.

General design features shall be as follows:

- Save working load: two times heaviest piece;

- Lifting speed: > 3 m/min;

- Crane rail: length and profile as required, with supports;

- Crab type: monorail electro cable;

- Standard: acc. to DIN 15020 or equal;

- Design/art: spur gearing overhead crane with chain and chain box for manual/electric operation with push-button unit;

- Power supply: 400/230 V/ 50 Hz by as tow-cable with carrier-tappet, feeder;

- Class of protection: IP 55;

- Ex-protection: E Ex E II T3;

- Material of crane: ST 37 with prime and final coating.

Unit comprising spur gearing overhead crane as common in trade, as applicable with manual or electrical drive unit.

## Lifting Davit

Movable and detachable, manually operated swiveling crane with quiver for submersible mixers, pumps lifting and other equipment.

- Loading capacity: according to weight of mixers and pumps (1.5 times heaviest piece);

- Reach: as required;

- Swivel-angle: 360º;

- Accessories: cable winch with traction rope and davit socket (alternatively chain);

- Material of column/swivel: SST 1.4301 or mild steel, hot dip galvanized, cable sheaves made of PA, connection pieces made of stainless steel.

Crane made of profile steel, with davit socket and swiveling lifting device of easy motion, incl. block and tackle.

# Chemical dosing equipment

## Chemical dosing

Pumps shall be selected taking into account that the chemical being pumped, form of chemicals, wear, resistance to corrosion and, in the case of dosing pumps, the accuracy.

Each pump shall be provided with inlet and outlet isolating valves and where necessary with pressure relief and non-return valves. Dosing pumps shall be provided with backpressure loading valves and pulsation dampeners in the delivery lines depending on the downstream conditions.

A relief valve shall be incorporated in the delivery lines under conditions where the pump discharge pipe can be shut off or where pressure may rise to an excessive point. The relief valve shall be sized to handle the system pressure and to discharge maximum pump output freely, and shall be located in the discharge line between the pump and the first downstream isolating valve or in the case of dosing pumps the back pressure loading valve. Relief valves when used on pumps handling non-hazardous chemicals shall discharge the vented liquid to waste. When used on hazardous chemicals, the valve outlet shall be piped back to the suction supply tank. The open end of the return pipe shall be located where it is visible, so that any relief valve leakage/operation can be detected.

Pumps transferring/dosing chemicals to systems under pressure shall incorporate a pressure gauge on the pump delivery. Air cocks shall be provided for release of air where necessary.

Flushing connections shall be provided at each pump inlet and direct to the delivery lines where so shown on the conceptual schematic diagram of the works; flushing water shall be at least 4 bar operating pressure at the connection.

## Dosing pump

Chemical dosing pumps shall be of the plunger or diaphragm type driven by electric motors. Hydraulically actuated diaphragm pumps will not be acceptable. Pump, motor and driving arrangement shall be mounted on a robust combined baseplate incorporating a drain connection.

The operating range of dosing pumps shall not be less than 6:1 for diaphragm pumps and 10:1 for plunger pumps, with overall accuracy within the following percentages:

| Description | Diaphragm Pumps | Plunger Pumps |
| --- | --- | --- |
| Accuracy of setting | 3 | 1 |
| Repeatability | 1.5 | 0.5 |
| Linearity | 3 | 1 |

Plunger pumps shall have alum-type-ceramic or stainless steel plungers. Diaphragm pumps shall have thermoplastic diaphragms faced with polypropylene, butyl- or polytetrafluoroethylene (PTFE). Pump heads shall be either stainless steel or polypropylene. Mechanical glands shall not be used.

The output of the pump shall be adjustable by varying the effective length of the displacement stroke. Variable stroke mechanisms shall be incorporated which enable the pump is running by means of a micrometer hand wheel or similar device.

Pump motors shall incorporate an integral reduction gearbox drive, which shall be totally enclosed in a lubricated oil bath. The gearbox shall incorporate the cams for the plunger, or diaphragm drive and shall be provided with oil filling, drain connections and visible oil level indication.

If integral gearboxes are not used, the drive shall be external V-belt. V-belt drives shall provide six standard stroking speeds to be selected manually by changing pulleys and which shall cover a range of pump speeds of not less than 3:1. V-belt drives shall have full guards of the type that allow the belts to be observed without the removal of the guards.

The design and location of metering pump heads shall facilitate easy dismantling for removal of any foreign matter.

Dosing pumps shall be provided with means for calibration by direct measurement upstream of the dosing pump. Manually isolated tapping shall be provided on the pump suction for connecting the calibration unit. The Contractor shall provide all necessary equipment and fittings in duplicate for the calibration of the dosing pumps.

Particular attention shall be paid to the layout of the dosing pumps and pipework. All connecting manifold systems shall be permanent and complete with drain connections. When handling chemicals with low vapor pressure, piping shall be designed to eliminate vapor pockets.

## Transfer pumps

Where applicable pumps for the transfer of chemicals from bulk storage tanks to day tanks shall satisfy the general requirements for pumps specified elsewhere as appropriate. These pumps and pumps for delivery of chemicals to the various points of application shall be manufactured from materials that will not be corroded by the chemicals to be handled. The inlet and outlet valves on pumps shall be designed for easy removal or dismantling to allow any foreign matter to be removed.

Pumps shall have stable head/quantity characteristics which fall continuously from the maximum pressure at closed valve conditions and which are steep in order that variations in head shall have a minimum effect on the quantity discharge. Pumps shall be arranged for automatic priming.

Air cocks shall be provided where necessary for the release of air. Gland water supplies shall be free of suspended matter and be non-corrosive. Where necessary, glands, bushes, nuts, studs, etc. shall be of such materials or receive such protection as will prevent their corrosion by the fluid handled.

## Chemical Pipework

Unless otherwise specified, each point of application shall be served by either a rigid pipe or a flexible hose and all hoses and pipes shall be connected to the pump delivery downstream of the last valve. Unless otherwise specified, duplicate standby delivery pipes/hoses are not required, by a spare hose for each chemical point of application shall be supplied and kept in store.

## Chemical Valves

Valves shall be of the diaphragm type with bodies and linings suitable for the chemicals handled. For handling suspension slurries, straight through diaphragm type or full bore valves such as globe or plug type shall be used.

Non-return valves on slurry lines shall be the ball type and shall be mounted on the vertical leg of the pipe.

Guard valves shall be provided for all non-return, pressure reducing, electrically actuated, loading and pressure relief valves.

# GENERAL EQUIPMENT

## Water decanter unit

Off the clearwater decanting phases the Clarified Water Decanter shall be located over the level of the maximum water level and consequently ensures the function of an emergency overflow system.

At the beginning of a clearwater decanting phase the inlet structure will be lowered down to the actual (maximum) water level supported by an electrical winch (i.e. drive force for the winch has to be electromotor, which can provide the winch’s speed of decanting). The inlet structure automatically opens its inlet slot approximately 20 cm under the actual water level.

The depth of immersion shall be adjusted anytime by changing the level of the two floats. At the moment when the wanted depth of immersion has been reached, the bottom plate automatically sinks away from the upper inlet structure and consequently the inlet slot will be opened with its pre-adjusted height. The hydraulic discharge power of the inlet structure at least is a consequence of the combination of the slot height and the depth of immersion.

Because of the horizontally floating of the inlet structure during the complete decanting process, the clear water can be discharged without any energy consumption until the minimum water level has been reached.

After the finalization of the clear water decanting phase the inlet structure will be lifted up to the emergency overflow level and so it can be used as an emergency overflow system until the next decanting phase will be started.

Decanter unit shall comprise, but not limited to:

- Material of the Decanter body and all submersible parts: stainless steel grade 1.4404 (AISI 316L), 1.4401 (AISI 316) and 1.4301/1.4304 (AISI 304/304L),

- Installation of the winch drive: yes,

- Motor protection type, min.: IP 55,

- Decanting system control: by its own PLC.

## Filters (cartridge filters) units

Cartridge filter unit shall be constructed of filter housing, filter cartridges, tube sheet, positive sealing arrangement for cartridge depending upon type of cartridge and choice of end connections. Positive sealing arrangement for cartridge filter assures no particle migration or fiber migration, even after high differential pressures.

Unit shall inter-alia comprise following items:

- Skid-mounted filter unit, completely pre-assembled and tested,

- Performances of 1st stage filter unit:

- Porosity of the cartridge: 0.5 mm,

- Performances of 2nd stage filter unit:

- Porosity of the cartridge: 30 to 50 µm,

- Permanently piped housing shall be opened without special tools and without disturbing the inlet/outlet piping,

- Machined cover gasket groove provides positive O-Ring sealing,

- Easy to clean/replace the cartridge,

- Positive sealing arrangement to avoid bypassing,

- Accommodates 10", 20", 30", 40", 50” & 60” long filter cartridges,

- All housings shall be made from stainless steel grade 1.4404 (AISI 316L), 1.4401 (AISI 316) and 1.4301/1.4304 (AISI 304/304L) are mirror polished & electro polished to resist adhesion of dirt and scale,

- Cartridges shall be made from Polyester, or Polypropylene.

- Gaskets/O ring shall be made from one of following materials: Neoprene, Nitrile, Silicone or Viton.

## Reverse osmosis (RO) units

Treatment on the 3-stage RO units shall be the main treatment, i.e., the main separation under whole LTP facility. It shall consist of three RO units, through which the mechanically pretreated wastewater shall be treated. All RO units shall be connected in the same process line and the permeate from the third stage RO unit will be the final effluent and it shall be discharged into the recipient water body.

Treatment on the 3-stage RO units shall comprise, but not limited to:

- Effective time of operation, min: 85 %,

- Time necessary for CIP cleaning, membrane replacement, other maintenance, max.: 15 %,

- Correction of pH before inlet on the 1st stage RO unit: yes, with possibility of acid or base dosing,

- CIP installation: yes, with base and acid chemical,

- Antiscalant dosing: yes, continuously,

- NaCl rejection in RO membranes, min.: 99.3 %,

- SDI value before 1st stage of RO unit (15 min test): less than 5,

- Material of the RO vessels, incl. feed/concentrate ports: FRP, PVC or equivalent,

- Material of the RO membranes: Polyamide (PA), or Polyamide composite,

- Material of gaskets: grade E (EPDM) suitable for most applications or equivalent.

## Coalescence separators

The type of separators shall be gravity coalescence separator with integrated or with separate settling tank.

Efficiency of separation shall be done on such way that the concentration of oil matters in Effluent shall be max. 5 mg/l.

The separators shall be designed, installed and tested in accordance with standard SRPS EN 858 - Separator systems for light liquids (e.g. oil and petrol).

Material of the Separator unit itself, as well as material of inlet and outlet elements shall be PEHD or GRP. Installation mode shall be buried, with easy access from the top.

Access covers shall be in accordance with standard SRPS EN 124 (Gully tops and manhole tops for vehicular and pedestrian areas), with inscription „SEPARATOR“.

## Air compressor units

The air compressor units shall include air cooled compressors, motors, pressure switches, gauges with pressure snubbers and isolating cocks, pressure tanks with hand holes, relief valves, drain cocks from tanks with pipe taken to nearest gully, line pressure regulators, oil separators and all other necessary controls, pipeworks, etc.

The compressors shall have suction filters, suction and discharge silencers and be mounted on vibration isolators on a common rigid mild steel base plate on top of the receiver. The pipeworks connections to the compressors shall be flexible to avoid vibrations being transferred to the pipes or to any structures.

The compressors shall be manufactured in accordance with EN 1012-1. The acceptance tests for the compressors shall be carried out in accordance with ISO 1217.

The receivers shall be manufactured in accordance with EN286-1 to 4.

The volume of the receiver and the capacity shall be in accordance with the Contractor’s anti-surge analysis if used for the air supply of surge tanks/vessels.

## Lobe-type air blowers

Blowers shall be positive displacement type, designed to give a completely oil-free discharge. Blowers shall be designed for an operating life of 20 years without major overhauls.

Furthermore, blowers shall not need normal maintenance procedures requiring replacement of parts within the first 18,000 hours of operation, except for lubricants and filters.

Components likely to become worn in the course of normal operation shall be capable of replacement, making use of readily exchangeable components.

The blowers shall have high-quality cast iron casing with integral feet. The shafts and three lobe rotors shall be integral construction from spheroidal graphite iron with seals of suitable material. These shall be fully machined and phase maintained through the use of pressure lubricated timing gears, which shall be hardened and profile ground.

Bearings shall be of a single roller grease lubricated type at the driven end, and double row deep groove ball type oil lubricated at the gear end. Labyrinth seals and nitrile “Ο” ring seals shall be fitted inboard the bearings to prevent air leakage and contamination.

Each blower shall be provided with a coupling or belts, guard and electric motor, and the whole assembly shall be mounted on a base plate with vibration isolators.

For direct coupled units, the blower and motor shall be dowelled in position, following satisfactory commissioning, to ensure correct realignment following dismantling.

The base plate frame shall include facilities for lifting the combined blower/motor/base frame assembly.

Each blower shall be provided with:

a)	Suction filter and noise attenuator,

b)	Air filter blocked indicator, including an electronic remote signal,

c)	Discharge noise attenuator,

d)	Pressure relief valve and electrical overpressure shut-off,

e)	Non-return valve and isolating valve,

f)	The pipework connections shall be flexible to avoid transfer of vibrations,

g)	Frequency converter (inverter).

Blowers shall be from within a standard range to meet the requirements of the complete system and provide the range of flows required. They shall be sized for the variations in atmospheric pressure, temperature and relative humidity stated in the following table.

Standard conditions and operating range for lobe-type air blowers

| Parameter | Standard conditions | Standard operating range |  |
| --- | --- | --- | --- |
|  |  | Minimum | Maximum |
| Air temperature | 15°C | 5°C | 35°C |
| Relative humidity | 75% | 25% | 100% |
| Atmospheric pressure | 1,013 mbar | 950 mbar | 1,050 mbar |

The blowers shall be sized to give maximum operating efficiency in standard conditions. The blowers shall be capable of operating over the stated operating range. Blower efficiencies shall be quoted for the minimum and maximum operating conditions.

Each blower shall be a compact unit, equipped with the necessary noise reducing enclosure (acoustic hood) with insulation material. The enclosure shall be easily demountable with snap locks.

Where forced ventilation is necessary in conjunction with acoustic enclosures and oil cooling, the rating of the fan motors used for this purpose shall be determined.

The additional loading represented by forced ventilation fans shall be taken into account when calculating the overall system operating efficiency.

The motor protection class shall be IP55.

The blowers shall be provided with an overpressure safety valve, a pressure gauge, a temperature gauge and a pressure switch that shuts off the compressor in case of too high pressure.

The blowers shall be provided with start relieve, in form of an automated air return valve.

The blowers shall be supplied with oil filling.

The blowers shall comply with the EU Machinery Directive 2006/42/EC.

The blowers shall be driven with V-belts that are provided with an automatic tensioning system. The V-belts shall move within a safety guard.

## Centrifugal blowers

Blowers shall be identical and of the centrifugal type with servo operated variable diffuser and servo-operated variable pre-rotation system for maximum efficiency.

The blower station shall be able to provide air linear in the minimum range of 20% to 120% of required maximum design capacity in terms of flow to the biologic reactors at the actual conditions. Each blower shall operate linear in a range of 45% - 100% of its maximum capacity. Actual conditions are in terms of discharge pressure, ambient temperature range and ambient humidity and altitude at the Site.

The efficiency of the blowers shall be no less than 80% through the entire duty range. The maximum efficiency in the duty range shall be no less than 85%.

Capacity of the blowers shall be determined by the Contractor.

The blowers shall operate fully automatic based on a preset oxygen value, monitored in the biologic reactors.

Blowers shall operate alternating.

The motors shall be provided with bimetal "klixon" switches or PT100 sensors for thermal protection.

The blowers shall be provided with silencer at inlet and outlet and noise reducing covers. Noise level may not exceed 85dBA 1 m away from the blower inside the station. Noise reduction covers shall permit easy dismantling and mounting for maintenance and repair and if necessary facilitated with internal ventilation.

Pipes inside the blower station shall be of stainless steel. Each blower shall be provided with all necessary instrumentation and valves such as: suction filter, pressure relief-valve check-valves, blow-off valves, pressure gauges on suction- and discharge side, inlet filter clog indicator, shut-off valves as well as a flexible connection to the pressure manifold. Lead-in pipes shall be designed to prevent possible damages to the pipes or concrete caused by vibrations and thermal expansions.

The building housing the blowers shall be adequately ventilated to prevent over heating. If air intake is from inside the room, adequate unlock able ventilation ducts e.g. louver openings, shall prevent vacuum creation.

## Positive displacement rotary screw blowers

Blowers shall be positive displacement rotary screw type, designed to give a completely oil-free discharge. Blowers shall be designed for an operating life of 20 years without major overhauls.

Furthermore, blowers shall not need normal maintenance procedures requiring replacement of parts within the first 18,000 hours of operation, except for lubricants and filters.

Components likely to become worn in the course of normal operation shall be capable of replacement, making use of readily exchangeable components.

Each blower shall be provided with a coupling or belts, guard and electric motor, and the whole assembly shall be mounted on a base plate with vibration isolators.

For direct coupled units, the blower and motor shall be dowelled in position, following satisfactory commissioning, to ensure correct realignment following dismantling.

Scope of supply shall be:

- Screw blower with reinforced bearings of driving shaft suitable for belt drive, forced-feed oil lubrication including oil pump, oil filter, oil pressure regulating valve, turbo filter for oil chamber release

- Base support with hinged motor mounting plate

- Intake filter and silencer

- Belt drive with belt guard

- Discharge silencer

- Safety relief valve

- Non return valve

- Expansion joint for pipe connection

- Flexible mountings with anchor bolts

- Electronic control system for protection of machine

- 3 phase motor mounted in the factory

- Acoustic hood

- Start-up unloading valve

- Frequency converter

Blowers shall be from within a standard range to meet the requirements of the complete system and provide the range of flows required. They shall be sized for the variations in atmospheric pressure, temperature and relative humidity stated in the following table.

Standard conditions and operating range for lobe-type air blowers

| Parameter | Standard conditions | Standard operating range |  |
| --- | --- | --- | --- |
|  |  | Minimum | Maximum |
| Air temperature | 15°C | 5°C | 35°C |
| Relative humidity | 75% | 25% | 100% |
| Atmospheric pressure | 1,013 mbar | 950 mbar | 1,050 mbar |

The blowers shall be sized to give maximum operating efficiency in standard conditions. The blowers shall be capable of operating over the stated operating range. Blower efficiencies shall be quoted for the minimum and maximum operating conditions.

Each blower shall be a compact unit, equipped with the necessary noise reducing enclosure (acoustic hood) with insulation material. The enclosure shall be easily demountable with snap locks.

Where forced ventilation is necessary in conjunction with acoustic enclosures and oil cooling, the rating of the fan motors used for this purpose shall be determined.

The additional loading represented by forced ventilation fans shall be taking into account when calculating the overall system operating efficiency.

The motor protection class shall be IP55.

The blowers shall be provided with an overpressure safety valve, a pressure gauge, a temperature gauge and a pressure switch that shuts off the compressor in case of too high pressure.

The blowers shall be provided with start relieve, in form of an automated air return valve.

The blowers shall be supplied with oil filling.

The blowers shall comply with the EU Machinery Directive 2006/42/EC.

The blowers shall be driven with V-belts that are provided with an automatic tensioning system. The V-belts shall move within a safety guard.

## Ventilators

Axial flow fans shall comprise a single impeller and direct coupled motor housed within a common ring.

The fan impeller shall have aerofoil section blades die-cast in aluminum alloy with adjustable pih and limiting power characteristics. Impellers may be of injection molded plastic, reinforced with chemically anchored fiberglass, UV stable. The impeller shall be statically and dynamically balanced and carried on the extension shaft of a totally enclosed, continuously rated squirrel cage induction motor in accordance with IEC 34-1. The rotor shall be dynamically balanced in accordance with ISO 1940. The fan casing shall extend over all the length of the motor and impeller and be constructed in heavy-duty hot-dip galvanized steel sheet. The manufacture shall be according to EN 10142, EN 10143, EN 10147, 89/38777 DC, 90/39695 DC.

The working temperature shall be for class F and the thermal overload protection shall be incorporated in the winding with connections to the terminal box situated on the motor.

The motor shall have a steel wire finger proof guard.

## Jet aerators

Jet aerators shall be used for the combined aeration and mixing of wastewater in tanks.

The venturi jet aerator is based on the injection principle that produces an effective air-water mix which results in optimum aeration and suspension of solids. The velocity of the primary flow of liquid from the pump is accelerated when pumped through the smaller nozzle inlet, lowering the internal pressure which draws in the secondary flow of air through the air inlet pipe. The liquid and air flows are then mixed in the turbulence of the diffuser pipe and ejected as a jet of fine air bubbles into the tank.

Jet Aerators shall be delivered with stand and pedestal, air inflow pipes and fittings, elbows and flanges made from stainless steel 1.4404.

Together with jet aerators, submersible pumps for standalone version in the tanks will be delivered with suitable hydraulic characteristics to fit the purpose.

## Mixers

For homogenizing of water or sludge and in order to prevent sedimentation of suspended solids, submersible agitators shall be applied. Agitators shall be equipped with cast iron or polyurethane blades with self-cleansing hydraulics.

General design features shall comprise, but not limited to:

- Unit with direct starting, design according to DIN 19569 or equal;

- Drive motor shall be submersed in the media and of protection class IP 68 with insulation class F, minimum 80% efficiency, leakage control;

- The bearings are to be sized to guarantee a service life of 50,000 hours;

- Low speed mixer with large diameter installed in the middle axis of the basin with its driving gear in horizontal position for maintaining complete suspension and low-shear mixing of the wastewater during low load periods (i.e. night-time during winter season);

- Mixer with parallel shaft helical spur gear suitably dimensioned for direct start and a starting frequency of 10/h;

- Drive with double acting mechanical seals (SiC/SiC) with seal liquid supervision in the oil chamber;

- Mixer with non-clogging propeller made of high-quality, fibre-glass reinforced plastic, completely coated with biologically neutral gel coat;

- Mixer units shall be lifted or lowered on sliding rails mounted in the tanks, incl. shock-absorbing guide rail, directly installed on the tank bottom;

- Technical data:

  - Motor speed 	 		1,450 rpm

  - Maximum, periphery speed  	< 8 m/s

  - Explosion protection 		EExd Il B T4 if applied for sludge, septage and raw sewerage. For the water, Explosion protection is not necessary.

- Sealing Motor: Cast-in cable entry, longitudinally water tight, cable plug-in connection in motor chamber. Mechanical seal propeller side mating of material silicon carbide/silicon carbide.

- Materials specification:

  - Casing motor-gear  	grey cast iron 25

  - Propeller 	 	grey cast iron 25 / Polyurethane

  - Propeller shaft  		1.4021

  - Bolts and nuts  		1.4432

The mixer system shall be complete with a local terminal box with emergency stop push button; On/Offkey-switch; Manual/O/Automatic-switch.

Materials specification describes the minimum required qualities. Each mixer shall be complete with all necessary ancillary equipment to render the unit complete and immediately ready for service.

## Vertical aerators

A slowly running, solid, durable steel impeller as a hollow structure fitted with shaft and flange (floating when drive unit is dismantled).

With regard to flow aspects, the aerator shall have a specific design in order to be capable of thoroughly mixing the contents in the deep tank even at the lowest speed, and to ensure a sufficient velocity of flow at the tank bottom (0.2 – 0.3 m/s).

The circulation capacity must be large enough so that it is possible to maintain circulation (mixture) even if one of the aerators fails. Solid matters or bunches of fibrous matter contained in the sewage are to be satisfactorily conveyed through the open impeller without its clogging.

The aerators shall mix and entrain oxygen in the tank contents by mechanical means alone. The aerators shall completely mix the tank contents, holding essentially all organic mixed liquor solids in suspension when operating at either the low or high speeds.

Each aerator shall transfer the required rates of oxygen per hour to the basin contents, when operating in conjunction with the other aerator in the basin at the design criteria. The peripheral speed shall not exceed 5 m/s to prevent excessive formation of aerosols.

- Aeration equipment shall be furnished by recognized experienced manufacturers, only;

- Each aerator shall include a turbine type aeration impeller drive shaft, couplings, speed reducer, drive motor, baseplate and steel supporting frame and flow stabilization baffle;

- All aerators shall be supplied with clockwise rotation, directions suggested by the manufacturer for the best performance, subject to approval of the Engineer;

- The turbine shall be designed in such way that ensures a non-pulsating torque on the drive unit;

- Each aerator shall be completed by the following accessories:

  - Automatic oil circulation lubrication for the gear reducer input shaft;

  - Sound protection hood for covering the motor-drive-unit, comprising SST-sheet construction with humidity resistant lining, provided with ventilation apertures;

- Each aerator with its driving motor, speed reducer and turbine shall be designed as an integrated unit maintaining proper alignment and spacing between motor and turbine. The motor shall be designed, manufactured and tested regarding following items:

  - Efficiency and rated load at rated voltage for each speed;

  - Power factor at rated load at rated voltage for each speed;

  - Full-load current at rated voltage for each speed;

  - Full-load current at 110 percent voltage for each speed;

  - Starting current at rated voltage for each speed;

  - Full-load speed for each speed;

- Design requirement: The installation bridge/structure shall be provided on such way that prevent excessive formation and emission of aerosols as well as noise and odour emissions.

Vibration switches shall be provided for each aerator and shall be acceleration sensitive to forces perpendicular to its base. The switch shall have a trip set point externally adjustable. Switch shall be single phase, double pole 5 Amp, 240 VAC., with an external manual reset button. Enclosure shall be IP 67 watertight. Switches shall meet the requirements of the situation and be of high industrial quality.  Aeration tank aerator speed reducers shall be sized and selected with a minimum service factor of two times the motor nameplate horsepower, in accordance with applicable European gear manufacturer's association standards.

Each aerator shall be furnished with an adjustable baseplate for mounting of the speed reducer on a concrete platform. The Aerator baseplate shall rest on at least four stainless steel anchor bolts, complete with jack and stainless steel lock nuts. The baseplate assembly shall provide an overall aerator impeller submergence adjustment of 10 cm minimum.

If it is necessary under the aerator, there shall be installed a flow control device to be mounted on the tank bottom. The cross-like device shall provide a stabilized flow pattern in the aeration tank or. Aeration tank compartment suppressing hydraulic pulsation, induce a vertical flow to aerator and ensure a completely circulating flow through the entire tank and thus prevent settling of mixed liquor suspended solids; material: galvanized steel with epoxy-tar coating in accordance to these specifications.

## Compressed Air Aeration

Compressed air distribution pipework upon the tank walls comprising stainless steel (up to 1 meter above tank bottom), including pipe supports, sectional valves and fittings. Maximum air flow velocity shoul be under range from 13 to 16 m/s under operating conditions (nominal air flow per system). Also, part of the works should be connecting pipework to aerators inside the tanks and air distribution grids on tank bottom with fine bubble membrane aerators for intermittent operation and drains.

## Membrane diffusers

Non-clogging type membrane diffusers suitable for continual (or intermittent) aeration shall be arranged above the concrete slab of the basin. It shall be arranged as line- or plane-aeration, therefore membrane diffusers shall be assembled to a necessary number of aeration grids comprising installation and distribution pipeworks.

Membrane aerators shall comprise, but not limited to:

- Supporting pipe made of water resistant PP or other resistant plastic material; outside diameter shall be max. 300 mm with connection piece to distribution pipework (in the case of circular or disc shape); parts made from PP or other plastic material of the diffusers without uplift;

- Aerators shall be in non-clogging design for intermittent operation;

- Perforated membrane of the diffuser made of EPDM or silicon rubber;

- The max. pressure loss of the aerator shall be less than 50 mbar after 2 years operation;

- The max. length of the diffuser shall be 1.0-1.5 m (in the case of tubular shape);

- The guaranteed service life of the aerator shall be more than 5 years under operation conditions;

- The loading of the aerator must be at least under range of 2 – 10 Nm³/h x m;

- The capacity shall be ≥ 18 g O2/Nm³air x m immersion depth under operation conditions;

The distributors, on which the aerators are fixed, shall be made of stainless steel or HDPE. The minimum wall thickness of the pipework shall be 3 mm. The distributors must be vertically adjustable and be fixed on the floor of the basin.

Each distributor must have an own dewatering unit. The diameter of that unit must be not less than 50 mm and is in the same material like the distributors made. The dewatering unit starts at the deepest point of the distributor and ends directly above the water level in horizontal direction with a ball valve.  Disk or plane aerators must fulfill analogous requirements and will be subject to the approval of the Engineer.

## Upgrade of existing sorting line

Upgrade of existing Macpresse sorting line shall be performed through design and installation of new units at the front of the existing line:

- Bag opener;

- Conveyors;

- Disc separator.

A bag shredder of minimum capacity specified in the Employers Requirements of waste shall be installed, prior to the disc separator. The specification shall be the same as the one required within the new sorting line.

A chain conveyor, with infeed hopper of minimal dimensions specified in the Employers Requirements, shall be used for the transport of MSW from bag shredder to disc screen. The specification shall be the same as the one required within the new sorting line.

A disc separator of minimum capacity specified in the Employers Requirements of waste shall be installed, after bag opener/shredder. The specification shall be the same as the one required within the new sorting line.

In addition, two slide roller conveyors shall be installed under disc screen/disc separator for collection of under-screen waste and its transport to the containers/out of MRF Hall where it will be loaded on truck and transported to Bio-drying plant.

## New sorting line

The new sorting line shall include the following units as minimum:

- Bag opener/shredder;

- Transporter to disc separator;

- Disc separator;

- Transporter of underflow from disc separator;

- Transporter for sorting cabin;

- Sorting cabin with steel stairs, with 14 workplaces;

- Separator of ferrous metal (magnet);

- Transporter for recyclables (for heavy materials);

- Transporter for recyclables (for light materials).

## Bag opener/shredder

The Bag opener shall work on the principle of a tear shredder. It shall have opening with an infeed hopper. The bag opener shall be a robust machine operating at low rotational speeds and hereby reducing wear of the hammers and energy consumption. The bag opener shall be equipped with a control system, avoiding and even resolving blockages if they occur.

The MSW shall be fed by front loader directly into the hopper of the shredder. The material falls on a drum, which is equipped with hammers that are mounted in a helical manner. The slow rotating drum shall be equipped with adjustable counter plate and robust wear-resistant counter hammers. Counter plate shall be adjusted from the outside of the door to set the opening between the rotating and counter hammers, regulating in this way flowrate and particle sizes of the output.

This side of the machine shall be easily hydraulically opened for the maintenance and cleaning purposes. The hydraulic system shall be a part of the machine.

The hammers on the drum and the counter hammers shall be made of bendable and weldable abrasion-resistant steel, a hard abrasion and wear-resistant steel. It shall be easy to refit the hammers with a hard-facing layer without replacing the hammers.

The bag opener shall be equipped with both an electric control and a hydraulic control to prevent overload. As soon as an overload occurs, the feeding conveyor shall stop. The drum shall turn in opposite direction for some time and try again. When the blockage repeats, the machine shall give a signal and the door of the machine can be opened hydraulically to remove the blockage. The closing force of the door shall be hydraulically adjustable. When it opens, by over-force, the machine shall stop without damaging.

If the drum is blocked by wrapping of material such as plastic films, this shall be detected, and the drum shall drive backwards where a scraper shall cut the wrappings. This step shall go fully automatic. The drum shall be directly driven by a gear motor for a maximum impact, the drum rotates in extremely strong self-aligning double spherical roller bearing. The number of revolutions shall be adjustable. The drum shall be dismantled through the front side of the machine.

The drum shall be equipped with a labyrinth on the side. Any material passing the labyrinth will drop down. This shall prevent any wrapping around the shaft.

The switch box shall be equipped with a PLC with touch screen control. The drum shall be driven by a frequency control with electrical brake and torque control. The machine shall be equipped with an emergency stop circuit. In the switch box there shall be a potential free contact for an external / extra emergency stop and remote start stop. At the machine itself, there will be a small control panel with functions, start/stop, rotate forward, backward and door open close.

The self-supporting construction shall be executed with four base plates, which can be attached to the floor or to a frame. Number of measures for vibration isolation or sound reduction are necessary.

A bag shredder of minimum capacity as specified in the Employers Requirements shall be installed at the beginning of sorting line.

## Disc separator

The open bags with MSW shall be transported by a conveyor to a large roller-screen.

Disc separator shall have the following characteristics as minimum:

- High throughput with precise selectivity,

- Aggressive material handling,

- Intermediate grain screened properly,

- Simple speed control to change particle size in seconds,

- Flexibly tailored solutions for specialized user applications,

- Screens can be simply mounted in a series, several grainsizes can be sieved in a single line,

- Disc screens shall not be affected by vibrations, they shall not shake or vibrate.

Disc separator shall include the following technical data:

- Oversized bearings - longer service life,

- Oversized gears - longer working life,

- Maintenance-friendly motor suspension – easily greasing chains etc.,

- Separately replaceable star shafts,

- Integrated conductors for electrical installations,

- Lasered side plates for accurate lateral placement of bearings - longer service life,

- Labyrinth sealing between side plates and star shafts to protect bearings,

- Includes platform for maintenance on both sides.

## Permanent belt magnet with steel support

The ferrous materials separation shall be carried at the end of sorting belt conveyor line by means of electromagnet over bands. A permanent magnet with steel support shall be installed over sorting belt conveyer and shall transport ferro metals to the container. The magnet shall be placed on its own substructure with a chute to guide the material into a container.

## Sorting cabin

The workplaces shall be located within a cabin on the sorting platform and with stair access according to the relevant labour Health and Safety regulations. The sorting cabin shall be made of prefabricated panels manufactured from a galvanised metal sheet and shall be properly lighted, soundproofed, thermos- insulated and air-conditioned in order to ensure suitable work conditions for workers. All panels shall be self-supporting. The floor shall be thermal insulated as well. An air exchange/renewal system shall be designed in order to generate a lower pressure in the sorting chutes/hoppers and avoid unpleasant smells. The cabin shall have transparent windows on both sides.

Ventilation system

A healthy and comfortable climate shall be provided in the air tight and well insulated cabin, required for energy efficiency. Electric heater battery can be placed. Anti-vibration feet shall be supplied with a drop towards condensation spigot for vertical units.

Summer operation

To supply cool air in warmer periods, the unit shall be equipped with a summer kit as standard. Simple exchange for heat exchanger. Split air coolers shall be used for cooling the air in summer. There should be at least four units, two on each side of the cabin length, symmetrically positioned.

Fans

- Low noise and energy saving centrifugal fans shall be provided, maintenance free and easily removable for cleaning if necessary.

- The cabin shall always have overpressure to ensure fresh air inside the cabin.

Filters

- Supply of clean air by minimum two filters.

- All filters shall be easily removed for cleaning and changing.

Heater battery

- With very low temperatures the intake air shall be warmed up additionally with a heater.

- Electric heater shall be controlled by built-in, adjustable thermostat.

- The ambient temperature in the cabin shall be controlled between 16 and 21deg C.

Condensation connection

- Condensation spigot at the bottom of a front side, shall be connected to a drainpipe on the site.

The cabin shall be inclusive heating, electricity and air-conditioning.

## Boxes with conveyers for separated raw materials discharging

Separation of MSW shall be performed manually on the belt of sorting conveyor placed on sorting platform of sorting cabin. The raw materials sorted on sorting conveyor shall be put into the different drop chutes of the conveyor and thrown, gravitationally, into the boxes, 7 pieces, below the sorting conveyor/sorting cabin. The back and front side of the boxes should have movable blinds.

Each of 7 boxes shall be equipped with conveyor and filled with different type of waste. Conveyors shall take each of them, toward the existing evacuation conveyor. Evacuation conveyor shall transport the separated recyclables to the existing infeed conveyor for raising secondary raw materials into the existing hopper of existing baler press, MAC 105. Pressing shall be done sequentially according to the type and quantity of each of the different valuable materials in order to produce bales of each one of the different types of valuable materials.

Chain conveyors shall be used for the transport of heavy raw materials sorted at sorting conveyor. Description of chain conveyors is provided hereinabove. Dimensions provided herein below are indicative.

## MBT-Bio-drying plant

The waste bio-drying process shall be carried out in tunnels/chambers made as reinforced concrete boxes. The temperature of the process shall be between 50 and 60°C. Each tunnel shall be equipped with sliding door, at the place of the second transverse wall, for feeding the waste material into the tunnel.

Each tunnel shall have its own intensive aeration system comprising of fans and piping for air intake and evacuation of excess air. This excess air shall be treated prior to its release into the environment.

Each tunnel shall have an individual air handling system placed at the back of the tunnel. The air shall be blown into a manifold which is placed at the back of the tunnel as well. Each individual tunnel shall be equipped with a single-inlet centrifugal fan for bio-drying designed for tunnel bio drying, including all parts. Centrifugal fans shall be pre-assembled as far as transport allows.

The centrifugal fans shall have the following features:

    - execution according to DIN EN 12255, where applicable

    - Fan to be of the high-performance radial fan-type with reduced pulsation and noise level

    - performance in excess of actual demand at least 10 %

    - rotor dynamically balanced according to VDI 2060, quality grade 6.3

    - impeller with backwards bended blades

    - ball/roller bearings designed for a service life of 80,000 operating hours

    - Fan and motor assembled on common base frame. Frame supported on flexible machine mountings

    - frame welded steel channel construction complete with fastening bolts

    - flexible hose connection on intake and discharge side

Drive:

    - three-phase induction motor according to IEC-Standard combined with a V-belt drive including guard or with a directly coupled motor

    - type of protection IP 54

    - insulation class F

    - designed for operating mode S1

    - thermoelement in coil for motor protection

Electrical Power and Control Equipment:

The electrical power and control equipment has to be installed in accordance with Employer’s Requirements-Electrical works and shall comprise:

    - fan completely cabled

    - power input components for all electrical consumers

    - all required switch and control equipment including fastener and accessories, continuous measurement of process data. Output signal 4 - 20 mA

    - potential-free contact points for all operational, fault and emergency-stop messages

    - emergency stop push button

    - local key-operated switch for “manual-0-automatic“ operation

    - all required ancillaries, such as limit/overload switches, alarms, indication lamps, running-hour meter, time switch for automatic sequence control, etc.

    - switch and control board (section) including all equipment, for instance circuit breakers, contactors, relays, current transformers, transducers, meters, components of PCS, wiring, terminals, etc.

Each composting tunnel shall be equipped with an “aerated floor”. An air distribution system shall be integrated in the reinforced concrete floor. This system shall be constructed from PVC air tubes and air-jet nozzles. Each individual tunnel shall be equipped with an air distribution system, including all parts listed:

- PVC tubes with mounted spigots, complete

- HDPE manifold

- Collector to connect the tubes to each other at the end of the tunnel

- Water lock arrangement (1x per 2 tunnels)

The holes shall be drilled into the spigots after being poured into the floor. The percolate draining of the system shall be integrated in the air distribution system. This must be connected via a water lock to the central drainage system of the plant or separated for processing.

Each tunnel shall be connected with an air exhaust duct which will be connected to the central exhaust. The central exhaust duct leads to the air treatment system.

Air for the bio drying process shall be extracted from Bio-drying Hall and from the RDF Hall. The air is extracted from the areas where odour generation is expected. To maintain good working conditions in the Bio-drying Hall, the number of air changes per hour shall be set at 3 times as minimum.

In order to control odour emissions, the Bio-drying plant shall contain an acid scrubber followed by a biofilter. The scrubber reduces ammonia and dust of the exhaust process air. By means of a fan the process air is sucked through the scrubber and blown directly into the biofilter. The scrubber shall be equipped with acid tank, dosing pump and filling station.

The air from the acid scrubber shall be blown into the biofilter floor by a centrifugal fan. The air from the acid scrubber is pressure and temperature controlled. Each biofilter shall be equipped with an “aerated floor”, i.e. with air distribution system in the floor. Also, each biofilter shall have cover/canopy. In order to keep the biofilter moist, fresh water shall be sprayed on the material. A bypass shall be incorporated into the exhaust system which makes it possible to take in fresh air. In this way the process air can be cooled down in order to prevent biofilter damage, due to overheating.

Due to the strict rules for odour emissions, a chimney shall be installed on the roof (canopy) of the biofilter. Exhaust air from the biofilter shall be blown through the chimney which ensures a good dispersion of the exhaust air.

The bio-drying process shall be fully automated and controlled via a control unit (PLC) and SCADA. The following parameters shall be monitored as part of the process:

- Drying temperature;

- Air temperature at the entrance;

- Oxygen concentration;

- Temperature of recirculating air;

- Air pressure at the entrance and exit points.

The control panel shall be a pre-installed and pre-assembled control system, based on a PLC system. The panel shall be made of stainless steel and so prepared for a long lifetime. The tunnel controller controls the drying process of a tunnel from the start of drying until the finished product. Also, Important management data shall be sampled, processed and presented in a clear way and stored.

## MBT-RDF preparation plant

After the bio-drying process, the material shall be removed from the tunnels using a wheel loader and transported to the RDF preparation facility, where the final sorting of dried waste shall be performed, in order to obtain the cleanest possible product.

RDF preparation facility shall consist of the following units, as minimum:

1. Hopper shredder;

2. Conveyor belt towards fine sieve;

3. Fine sieve 50 mm/15 mm;

4. Container for fine fraction (0-15 mm) under the sieve;

5. Conveyor belt from sieve towards air separator for mid fraction;

6. Conveyor belt from air separator to optic separator;

7. Fe-metal separators above the conveyor belt (Magnet for separation of magnetic materials);

8. Containers for separated Fe metals;

9. Ballistic (air) separator {separation of lightweight (plastic, paper) and heavy (stone, glass) based on density (weight) and shape};

10. Container for inert material under the ballistic separator;

11. Conveyor belt from sieve towards optic separator for oversized fraction;

12. Optic NIR separator (separation of special plastic polymers based on diffraction);

13. Container for separated PVC;

14. Mill / Granulator;

15. Conveyor belt towards RDF container;

16. RDF container;

17. Conveyor belt towards baling press;

18. Baling press;

19. Bale wrapper.

The sorting line for dried waste (for producing the RDF from dried waste), must comprise all units, all equipment needed for fully automatic and independent work.

Only smooth-surfaced belt conveyors guided by pulleys are permissible, to allow complete lateral material guidance with generously sized belt width (if other systems, such as drag link conveyors or apron conveyors are offered, this shall be justified in detail). Belts shall be of sufficient width, so that no conveyed material will spill sideways from them. The conveying devices shall be of robust design in order to cope with the anticipated difficult operating conditions.

## MBT-Biogas plant

MBT biogas plant facility shall consist of the following units, as minimum:

- In-feeding system-Screw press

- In-feeding system-Cyclone for separating plastic and stones from wet fraction from the press

- In-feeding system-Infeed pump for liquid phase

- Digester

- Screw-press separator

- Pump for water for dilution

- Digestate transport pump

- Pump for liquid phase

- Filter for liquid phase

- Pump for water for filter for liquid phase

- Transporter of dry fraction of digestate

- Tank for water

- Polymer dosing system

- Biogas analytical device

- Pipeline installation

- Technical Container for Plant control

- Technical Container for CHP unit

- Biogas pipeline system

- Gas purification system

- Torch

- Water tank

- Sludge tank

In-feeding system-Screw press

This preparation of raw materials for biogas production shall be carried out in the so-called the extrusion chamber, i.e. the screw press, where the liquid part of the bio-waste / organic material shall be separated from the solid part. This liquid part is the raw material/substrate for the biogas plant, while the remaining dry mass/solid part shall be sent to the bio-drying tunnels together with the solid part of the digestate. The substrate shall be pumpable and can be diluted by adding process water, if necessary.

The inlet bio-waste is homogenized in the feeding hopper by means of two counter-conveying mixing screws. The drive units of the mixing screws shall be dimensioned for frequent reversing. In this way material in packages or waste in bags can be opened in the area between the mixing screws by shear stress, avoiding an unnecessary reduction of the packaging material into too small pieces. Therefore, the substrate extracted during the solid-liquid-separation shall be particularly clean in regard of such contaminants. The addition of water leads in most cases to a washing effect and enables the extraction of more organics, leaving the solid residues dryer than without the addition of water. The volume flow rate from the feeding hopper to the pressing screw shall be adjusted by means of a dosing gate. This way continuous and batchwise processing is possible. A partially opened dosing gate lowers the throughput and to some extent increases the dewatering degree. The lower the throughput, the longer the residence time and the better the material drainage. The pressing screw surrounded by a screening basket transports the material towards the pressing cone. Due to the decreasing flight pitch and the increasing inner diameter of the screw shaft the material is compressed in transport direction and the substrate/filtrate is discharged through the screening basket into the reception basin. The reception basin feeds the substrate / filtrate into an eccentric screw pump which is well suited for highly viscous liquids with a high content of dry matter to maximize the gas yield per cubic meter. The screening basket shall be composed of four separate parts in order to facilitate a possible basket change. Furthermore, it shall permit combination of different mesh sizes in longitudinal direction.

The operating pressure shall be regulated. An optimum pressure shall be set for a large range of input materials thus achieving the required degree of dewatering. Solid parts with diameter of up to 80 mm in the input material shall be processed without failure. Plastic parts and plastic films shall be transported through the machine without any risk of wrapping or jamming and discharged as part of the solid part. The press shall be equipped with cyclone for separating plastic and stones from the wet fraction from the press.

The in-feeding system shall comprise also a pump which recirculates liquid coming from the end storage tank, and a hopper feed pump which uses this liquid phase to homogenize the material it has previously pressed/shredded. This hopper feed pump has the characteristic that together with a laterally attached liquid phase, it mashes coarse solids into a homogeneous suspension. The suspension is then distributed to the pump chamber, which passes it to the digester, all in one step. Co-substrates shall be introduced after they are well mashed and treated, resulting in higher gas yield.

In-feeding system-Cyclone for separating plastic and stones from wet fraction from the press

The requirements for In-feeding system-Cyclone for separating plastic and stones from wet fraction from the press shall be as set in the Employer’s Requirements.

In-feeding system-Infeed pump for liquid phase

The requirements for In-feeding system-Infeed pump for liquid phase shall be as set in the Employer’s Requirements.

Digester

Digester shall comprise tanks, comprising gas tight buffer / hydrolysis tank and separate horizontal tanks/fermenters. These tanks shall be placed in one building. Digester building shall be made of a reinforced concrete closed on all side. It is divided transversely by partition walls into independent horizontal chambers/tanks, that serve to accommodate the liquid from which the gas is extracted and equipment.

The ceiling of the digester forms a double-shelled carrier air roof. Double membrane shall be mounted on the upper part of the digester and serves as a gas tank. It shall be equipped with filling level sensor.

The digester shall be heated via heat exchangers installed in the digester. A horizontal agitator, with a geared motor as a drive, with shaft seals, a main shaft bearing on the tank inlet and outlet, ensures that the substrate is thoroughly mixed. The agitator drive shall be protected from overload by the flow monitor.

Technology building for holding the substrate pumps as well as the substrate lines shall be provided. The heat distributors/exchangers for heating the digesters shall be installed in technology building. The control cabinet for the biogas plant shall be installed in the technology building. This building shall be supplied with ventilation.

Digester shall also be equipped with the following as minimum:

- Inspection window,

- Temperature sensor Pt100 with immersion sleeves to measure temperature of digester,

- Horizontal agitator with a geared motor as a drive, with shaft seals, a main shaft bearing on the tank inlet and outlet,

- Metered injection of fresh air into the biogas for biological desulfurization of the biogas,

- Set of heat exchangers in the digester,

- Overpressure and under pressure protection,

- Fill level measurement,

- Cleaning opening in the digester with pressure door,

- Desulfurization unit with air pump and metering unit,

- Central lubricating station for the agitator shaft bearings.

After the press/purification step, the clean liquid organic fraction shall be pumped to a gas tight buffer / hydrolysis tank. This tank shall have the capacity to store up to 2 days substrate intake. The hydrolysis stage of this material shall begins in this tank, which also contains heating elements with a target substrate temperature of 25°C. A safety service box shall be installed on the roof of the buffer / hydrolysis tank to facilitate operational adjustments to the mixing system, retrieval of the mixer for service /maintenance and for gas collection. Gas shall be delivered to the primary fermenter to be mixed with gas from the fermentation process. Following a request by the plant controller, a pump system shall remove the substrate fully automatically from the storage tank and supplies it to the digesters/ fermenters, with large horizontal mixers, which enables work with a high percentage of dry matter. After the pressing and cleaning of the infeed substrate the structure of the substrate shall be broken, and the gas drops out very fast.

The fermentation residue/digestate shall be removed from the digester and sent to a screw separator for dewatering by means of a hose pump. The liquid phase shall retained in the final tank/digester, which is hermetically sealed and equipped with mixers, in order to homogenize the digestate and use it in the process.

The liquid fertilizer shall be stored temporarily in a final storage tank/digestate. To minimize door emissions, the tank shall be provided with a gas-tight cover on the top of the tank. Agitators enable the fermentation residue to be agitated and homogenized. To be able to perform inspection work without difficulty, final storage tanks and digesters shall be fitted with large-scale pressure doors.

Air, which shall be metered into the digester, biologically desulfurizes the biogas and supplies it to the CHP via a pipeline system.

All substrate pipelines, pumps which shall transport digested material from the digestors to the cleaning system, heating pipelines including pipelines which transport heat from CHP unit to digestors, biogas pipelines from the digesters to the condensate separator, and from condensate separator to the CHP unit, shall also be supplied, including all other small parts of the biogas plant.

Screw-press separator

The screw press shall be designed specifically for the dewatering / separation of fermentation residue from dry fermentation plants. The pressure in the press builds up by a conical screw with adjusted rib heights and a special spiral design. The press zone length can be adjusted at a standstill and adapted to the particular characteristics of the supply. The reduced torque level shall allow simplified damping as a combination of the press zone length and pneumatically engageable fins.

The screw press shall have the screw applicable for high flow rates, closed hood system, optimized wear protection as well. The possibility of manual adjustment of the plug length to the characteristic of the substance shall be also applied. Screw conveyors, between the screw press and digestate bunker shall be also included.

Pump for water for dilution

This pump shall transport the water from water storage tank to the digester. The requirements for pump shall be as set in the Employer’s Requirements.

Digestate transport pump

Pump for the transport of digestate, with the associated pipeline, shall be supplied. The requirements for pump shall be as set in the Employer’s Requirements.

Pump for liquid phase

This pump shall transport the liquid phase from screw press to the sludge tank. The requirements for pump shall be as set in the Employer’s Requirements.

Filter for liquid phase

The requirements for filter shall be as set in the Employer’s Requirements.

Pump for water for filter for liquid phase

The requirements for pump shall be as set in the Employer’s Requirements.

Transporter of dry fraction of digestate

The requirements for transporter shall be as set in the Employer’s Requirements.

Tank for water

After the screw press process, the water is pumped into the final storage tank. The recirculation to the main digester takes place via a progressive cavity pump.

The tank shall be made of stainless steel and equipped with all necessary piping. The requirements for tank shall be as set in the Employer’s Requirements.

Polymer dosing system

System for dosing polymer powder has to be supplied with all associated equipment, including pumps for dosing and transporting the solution, water connection, mixers, tanks for preparing the solution, and hopper for powder material with level sensors.

Biogas analytical device

Digester shall also be supplied with Biogas analytical device which shall provide monitoring of the following:

- Methane:		0-100 % Vol. +/- 1%

- Carbon dioxide:		0-100 % Vol. +/- 1%

- Oxygen:		0-25 % Vol. +/- 2%

- Hydrogen Sulphide:	0-10.000 ppm +/- 15%.

Device shall have 2 measuring point. The protection class is IP42 and the interface shall be in accordance with adopted communication protocol. The pump of appropriate capacity shall be provided. The connection material and small compressor, in order to control the valve sets, shall also be provided.

Technical Container for Plant control

Technical Container for Plant control

The plant control shall include the following equipment as minimum:

- Electric cabinets;

- PLC;

- Horizontal panel coupled with weighing cells;

- Metrology;

- Electrical installations, including material and cable laying;

- CHP coupled.

Technical Container for CHP unit

Two CHPs shall be placed into a container. The Contractor shall supply Biogas CHP container with all adjacent and accompanying equipment and associated installations for obtaining electrical and thermal energy, including meters for the amount of gas produced and the ventilation system, included an open skid unit with gas blower and gas heater, and gas quantity measurement instruments.

CHPs, shall include, among others, the engines accessories, engines gas train and combined gas booster, engines and adjacent equipment control panel, engine exhaust gas system with exhaust gas heat exchanger and exhaust stainless steel pipes, engine Low Temperature dump cooling system, High Temperature water system of the unit, other equipment (pumps dump coolers regulation valves) including dump cooling for the full Low Temperature and part wise for the HT system.

Biogas pipeline system

Complete system of biogas pipelines and biogas purification devices have to be supplied. The biogas pipeline system consists of stainless steel pipes (1.4571) DN250 in the above-ground level, while plastic pipes PE100, SDR11, DN250 are foreseen in the underground level. The biogas pipeline system consists of:

- biogas pipeline that transports biogas from the digesters (each digester has the corresponding biogas storing sack on the roof; the sacks are at the same time covered by a pitched roof which protects them from negative effects) and digestate storage to the condensate separator, including electric valves for biogas sampling,

- biogas pipeline that transports biogas from the condensate separator to the technical container in which the biogas engine (CHP) is installed.

Gas purification system

The gas purification system shall consist of:

- condensate separator made of PE, with an eccentric pump for condensate with a 3-phase AC motor (EEx eIIT3). It shall include sufficient condensate pipeline to make the necessary connections. It comprises, among others, dewatering vessel made of stainless steel 1.4571, level switch, supporting structure, etc.

- biological desulfurization comprising, among others, the following:

- 1 Instrument nozzle made out of 1.4571 material and including a spherical valve DN 50, PN 10.

- A conical suspended matter analyser made out of stainless steel and borosilicate glass with the effective range of 20-120 liters of air per minute and with an accuracy of 2.5% the end value. It can work up to 20 bars.

- Small compressor with a voltage of 220 V, a frequency of 50 Hz and a power input of 215 W. The operation pressure is 0.2 bar and has a range of pressures between 0.05-0.3 bar; at the operation pressure, the fan efficiency is 200 l/min.

Torch

The hearth of torch shall be made of refractory stainless steel 1.4893 covered with refractory bricks. Stainless steel tube shall be coated with ceramic fiber to sustain temperature up to 1260 0C. External covering shall be from stainless steel 1.4031.

Torch shall be equipped with:

- Temperature regulator:		by controlling the combustion airflow using 230V servomotor

electric motor

- Emergency manual control

- Flame temperature control: 	Type S thermocouple with casing

- Flame presence control:		UV radiation detection cell

- Ignition: 			by 2 electrodes under a tension of 7.5 kV

Water tank

The requirements for water tank shall be as set in the Employer’s Requirements. Water tank shall be placed on the concrete foundation and shall be made of steel. Thermal insulation of tank shall be provided.

Sludge tank

The requirements for sludge tank shall be as set in the Employer’s Requirements. Sludge tank shall be placed on the concrete foundation and shall be made of steel. Thermal insulation of tank shall be provided.

## Wheel washing equipment

The wheel washing plant shall be suitable for trucks which are contaminated slightly or to a medium degree. When entering the plant, the truck automatically triggers the washing operation via light barriers. While the truck is moving slowly across the washing plant, nozzles spray water from below and from the side on the wheels for cleaning the dirt from the treads. The water returns to a water tank to be recycled.

The dirt settles and remains in the area before the dirt separation walls. The washing water passes through the dirt separation walls to flow to the water pump which is located behind the walls. The recycled water is re-used for the next washing operation. The missing water quantity is refilled automatically by a float-type switch.

The wheel washing system shall consist of two subsystems:

- the washing subsystem in which the washing equipment is located and

- subsystem for water recycling and removal of excess sludge: a tank with clean water and for the separation of solids.

## Spraying guns

A portable. hand operated, spraying guns shall be used for spraying of recycled water on landfill. Spraying gun shall be mounded on the movable trailer with hose. The length of the flexible hose shall be suitable to cover landfill cassette. A portable spraying gun shall be suitable for connection to hydrants network placed around the landfill.

## Screw Conveyor

Screw conveyors may be used for to transmit both digestate, screenings, dewatered sludge and other waste from the discharge of other conveyors and process machines. They shall be of a proven non-clogging design.

General design features of the conveyors shall be as follows:

- The supporting framework is to be fabricated from stainless steel profiles or stainless steel tubes and is to be of fully welded construction. Sufficient connection pieces for mechanical stiffening are to be provided;

- The trough shall be U-shaped with bolt on cover plates of stainless steel of quality 1.4301 according to DIN 17 440 with plastic or rubber wear liners and incorporate a fully enclosed discharge chute;

- The shaftless spiral shall be of special steel;

- Geared motor; EExd Il B T4 (where necessary), insulation class F.

Unit to be arranged under machine discharge chute, incl. chute adapter for connection of the discharge to the media chute of the screw conveyor, incl. overload protection and local terminal box and emergency stop breaker.

## Belt Conveyor

Belt conveyors shall be of the modular trough belt type for conveyance of waste, screenings, dewatered sludge or other debris.

General design features of the conveyors shall be as follows:

- The conveyor frame and sub-frame shall be hot dip galvanized mild steel, all fixings shall be hot dip galvanized mild steel or stainless steel;

- Geared motor; EExd Il B T4 (where necessary), insulation class F;

- The conveyor belt shall be plain 2-ply nitrile rubber 800 mm wide running at 0.8 m/s;

- Belt idlers shall be twin roll 50mm diameter roller bearing through set at 600 mm centers bolted into slots to allow belt tracking adjustment. Belt return rollers shall be drop in disc type to give reduced belt contact;

- Drive and idler drums shall be fully guarded;

- The conveyors shall be fitted with side plates to ensure that the screenings are retained on the belt and suitable arrangement shall be made to drain the belt of any excess liquid on the channels;

- There shall be fitted under the driving discharge drums a counter balanced type belt scraper with renewable rubber blade to remove all matter which remains clinging to the belt;

- The conveyor shall be equipped with a splash-guard with drainage connection mounted underneath over the whole length.

Unit to be arranged under machine discharge chute, incl. chute adapter for connection of the discharge to the media chute of the conveyor, incl. overload protection and local terminal box and emergency stop breaker.

## Chain Belt Conveyor

The chain belt conveyor consists of a drive- and a tail-section. Between these 2 sections the conveyor is built from sectional modules. The modules shall constructed of strong sheet metal. At the infeed the conveyor is provided with side plates. These side plates shall be equipped with hatches for cleaning. The left –and right side frames shall be connected with each other with steel supports plating. The steel cleats, the rubber belt, support and transport chain shall be integrated in one system. The rubber belt shall be supported with steel square profiles. At both ends of these steel square profiles special plates shall be welded that are bolted to the chains. Together with the sidewalls it works as a Labyrinth seal. The rubber belt shall be placed between the steel cleats and the steel square profiles. The steel cleats shall be fastened to the profiles.

At all in feed positions of the conveyors there shall be chutes to guide the material away from the side of the belt.

The conveyor belt shall be driven by a High-end quality drive motor which shall be mounted directly on the drive drum shaft.

The number of rollers per meter shall be sufficient to reduce wear and force per roll and provide smoother running of the belt.

The chain tensioning shall be equipped with a spring to prevent tension peaks on the chain.

All bearings shall be self-adjusting to prevent misalignment of the bearings.

The motor shall be equipped with an electric brake to prevent running backwards

## Slide roller belt Conveyor

The slide roller belt conveyer shall have rubber surface slides over steel roller in the middle. At both sides the rubber belt slides over a sheet metal plate. These sheet metal plates shall be bended, which shapes a trough form. The transported material lies in the middle of the conveyor and shall not flow under the side-sealing. He construction of the conveyor shall prevent material to drop off the belt.

The Construction of the conveyor shall be completely modular. That means that it shall be built from sections of several lengths. By adding or subtracting sections the length could be altered in time.

## Sorting belt conveyor and sorting platform

Over-screen MSW shall be transported from disc separator directly to sorting conveyor. Conveyor starts in the incline part as a slide roller belt conveyor. In the horizontal section the side guiding shall be changed in a low side guiding straight down with rubber side seal and at the sorting positions a wood layer is on top of the guiding to make the sorting more comfortable. The speed shall be adjustable between 20 and 40m/minute. Side walls shall be placed over the complete length of the conveyor. Cover plates of steel plates shall be mounted under the conveyor for safety till 2400 mm high. Support, infeed chute, and plough scraper are included. The frame of sorting conveyor shall be composed of profiled and folded sheets. The belt shall be made of rubber, resistant to scratches and oily and greasy substances.

Sorting conveyor shall be placed above sorting platform, inside the sorting cabin.

The platform around the sorting conveyor shall be divided into 7 (seven) working segments – position, inside the cabin. Each segment - work position has 1 workplace on both sides of the belt (1×2), total 7x2 workplaces. Left and right from the conveyor 7x2 sorting chutes shall be located. Two PET perforators shall be installed on two sorting chutes placed on one workplace. Capacity of PET perforator shall not be less than 600 Kg/hr per one shredder.

The platform shall be made of steel profiles, supported on steel columns. Nine segments of steel platform shall be divided by 10 transverse partitions (walls) made by the panel placed in the steel frame. 7 segments of nine shall be prepared as boxes for temporary storage of sorted raw materials. These seven boxes shall be provided with partitions walls, movable blinds, on front and back side (7x2), which can be raised when needed.

At the end of sorting conveyor, out of sorting cabin, sorting platform shall have 2 more segments for collection of ferro metal scrap and for discharging of remaining mixed waste into container.

## Container

Commercially approved waste container, with strengthened bottom sheet and tilting bearings for service truck and drain with connection to the sewage system.

- Container in accordance to DIN 30720 or equal European Standards;

- Material: sheet steel St 37, sandblasted SA 2,5 with 1 prime + 2 final coatings;

Containers form the type used by the municipal services shall be preferred.

## Rotostrainer

Self-cleaning screen with rotary screen cylinder comprising a continuously wound wedge wire of stainless steel installed in a sheet steel machine body, completely made of stainless steel 1.4301 (AISI 304) with sieve cylinder made of 1.4432. Unit comprising following items:

- Stainless steel housing with supports and stand, ventilation, inlet and effluent flange connection;

- Screen gap width: from 5 to 7 mm;

- Scraper mechanism made of special steel and discharge chute in order to discharge retained solids into a container, a screenings press or onto a conveyor, etc.;

- Internal spray system with solenoid valve for screen cylinder flushing;

- Two speed gear motor; 685/1410 min-1, EExd Il B T4 (where necessary), insulation class F;

- Ultrasonic level control for works operation;

- Electrical control equipment for automatic operation, with 2-speed drives by ultrasonic/electronic water level sensor system;

- Local control panel, IP 65, with main switch of supply circuit, with emergency shutdown function, motor protection, main current protective device, Voltage 24 V/DC;

- PLC control with a remanent run and monitoring program, including also the working periods for automatic operation. Manual switch for slow and fast speed, pre-selection for automatic operation, signalling lamps for operation and failure conditions, running time recording;

- Overload protection for the electric drive and local switchbox acc. to VDE regulations, c/w. local emergency-OFF-switch, wiring and assembling accessories.

Unit comprising Rotostrainer with influent and effluent pipework, incl. measurements and local control box.

## Heating plant

General

An appropriate heating plant or plants, consisting of boiler, burner, pump, radiators, piping and accessories, may be installed for heating of building where people work permanently (i.e. offices, personnel rooms, control room, laboratory, etc.).

All materials used for heating installations and the water boiler equipment shall be resistant against aggressive sewage water substances, airborne substances and other atmospheric impacts. Such resistance shall be ensured by means of non-corroding materials. All underground pipe conduits shall be equally corrosion resistant.

Heat shall be generated as requested in the Employers Requirements. Where there is gas fuel forseen, the boiler should be of the dual fuel type. Such heat generation equipment shall be protected and equipped according to national norms or equivalent standards, codes, manuals or regulations.

Chimneys shall be calculated, designed and built according to national or equivalent and more stringent international standards, codes, manuals or regulations.

Pumps, fittings, accoutrements and accessories

Circulation pumps shall be complete with differential pressure control, manometers, measuring lines and all necessary devices.

The heating distribution network shall be subdivided into segments, according to the actual utilization of the buildings, which shall be controlled individually.

Radiators and accessories

Radiators shall be planned according to the requirements of the heat generating plant.

Overall heat requirements shall be calculated, and the design of the plant shall be according to national or equivalent and more stringent international standards, codes, manuals or regulations. In general, room heating shall be according to standard indoor temperatures. In rooms where people might stay from time to time, the temperature shall be 15°C.

On principle, all radiators shall be equipped with thermostatic control valves. Furthermore, there shall be lockable and drainable backflow union pieces with filling devices and all air-relief valves required.

Heating pipes, distributors and accessories

The network of heating tubes shall be calculated under due consideration of hydraulic requirements in compliance with the national or equivalent and more stringent international standards, codes, manuals or regulations. In principle, pipes shall be laid out in a frost-protected manner.

There shall be adequate provisions to air-bleed and drain pipes, sliding stops, pumps and vessels. All pipe fastenings shall be equipped with dampening covers to provide against excessive sound transmission.

## Weighbridge

The weighbridge shall be an electro-mechanical weighbridge, suitable for loads up to a maximum 60 tonnes. It shall consist of a load receiver, a measuring cell and an electronic measuring terminal, monitoring system. Weights and other important data about arriving garbage vehicles and accepted waste will be registered in the logbooks in electronic form. Total weight of the loaded truck/vehicle as well as weight of the unloaded truck/vehicle are measured on the weighbridge and registered.

All data related to the Client shall be registered: name, place, date, vehicle plate number, time of both weightings, type and quantity of the waste, driver’s name, etc. Data shall be stored in the central database.

Design Minimum Requirements:

  - The weighbridge shall be suitable for 24 hrs. of operation per day 365 days in year.

  - The weighbridge shall be suitable for operation during rainy season.

  - The weighbridge shall be capable of withstanding dynamic load imparted by the vehicle movement and braking.

  - The weighbridge shall calibrate automatically the variation due to rains and other errors.

  - The weighbridge shall be equipped with system for detection of radioactive waste.

  - The weighbridge shall be equipped with automatic ramp.

  - The weighbridge equipment shall be electronic load cell with micro-processor-based type.

  - Approximately 100 weighments per day are expected to be made in each TS complex, using the weigh bridge.

# SPARE PARTS

Spare parts, sufficient for operating the complete Plant, for a period as specified in the Employer’s Requirements, shall be handed over by the Contractor. The Tenderer/Contractor shall, based on the manufacture’s recommendation, determine the required spare parts for all equipment and prepare a list of spare parts. The list shall be included in the offer (Contractor’s Proposal). The Contractor’s and manufacture’s selected spare parts shall serve as supplement to the spare parts listed hereunder, which only comprise the minimum required mandatory spare parts:

General:

Touch up paint for all equipment.

Screens:

- 5% extra bars if appropriate

Pumps:

- 1 set of gaskets for each pump

- 1 set of mechanical seal for each type of pump

Blowers, for each item:

- 1 set of inlet filters for each blower

- 1 set of oil filters for each blower

- 1 set of hydraulic cylinders, if applicable, controlling pre-rotation and diffuser position

Submerged mixers:

- 1 set of gaskets for each mixer

- 1 set of mechanical seal for each type of mixer

Aeration grids:

- 5 % spare diffusers

Screw conveyors:

- Complete set of liners for all screw conveyors

MEICA = Mechanical-, Electrical-, Instrumentation-, Control & Automatisation 2 For main equipment, such as pumps, blowers, mixers, etc.

For main equipment, such as pumps, blowers, mixers, etc., on request of the Engineer