LOT 1

VOLUME 3

SECTION 2A

GENERAL TECHNICAL SPECIFICATIONS FOR CIVIL AND BUILDING WORKS

LOT 1: GENERAL TECHNICAL SPECIFICATION FOR CIVIL

AND BUILDING WORKS

1	GENERAL DATA	18

1.1	Introduction	18

1.2	Objective of the Works	18

2	SETTING OUT OF THE WORKS	19

2.1	General	19

2.2	Execution and Workmanship	19

3	STANDARDS	21

3.1	Standard Specification	21

3.2	Standards on Site	22

3.3	Matters not Covered by Standards	22

4	DESIGN DOCUMENTATION	23

4.1	General	23

4.2	Working Drawings and Calculations	24

4.3	Record Drawings	26

4.4	Procedure for the Working Drawings and Calculations	26

4.5	Operation and maintenance cost	27

4.6	Criteria for design personnel	27

5	DESIGN CRITERIA	28

5.1	Design Life	28

5.2	Structural Design General	28

5.3	Earthworks and Foundations	29

5.3.1	Design	29

5.3.2	Durability	29

5.3.3	Fill Materials	29

5.3.4	Excavations to be refilled with granular material	30

5.3.5	Embankment Design	30

5.3.6	Foundation design	30

5.3.6.1	Shallow Foundations	30

5.3.6.2	Deep Foundations	30

5.3.6.3	Bored Piles - HW	31

5.3.7	Water Loading	31

5.4	Structural Concrete	31

5.4.1	Codes and Standards	31

5.4.2	Water Loading	32

5.5	Structural Steel – Codes and Standards	32

5.6	Wooden construction - Codes and Standards	32

5.7	Architecture and Buildings	32

5.7.1	General	32

5.7.2	Masonry	34

5.7.3	Roofs	34

5.7.4	Walls	34

5.7.5	Windows and Doors	34

5.7.6	Facades	34

5.7.7	Internal Works	34

5.8	Roads, Hard standings and Footpaths	35

5.8.1	General	35

5.8.2	Design of Roads	35

5.8.3	Design of Drainage	35

5.1	Pipelines	35

5.1.1	Load Cases	35

5.1.2	Anchorages and Thrust Blocks	36

5.1.3	Chambers	36

5.1.4	Air Valves	36

6	EXECUTION AND COMPLETION OF THE WORKS	38

6.1	Materials	38

6.2	Preliminary Works	38

6.3	Execution of Concrete and Reinforced Concrete Works	38

6.3.1	General	38

6.4	Other Works	39

7	DEMOLITION AND PROTECTION OF WORKS	40

7.1	General	40

7.2	Disposal of Demolition Materials	40

7.3	Refilling and Finishing	40

7.4	Permission	40

7.5	Protection of Existing Objects	40

7.6	Filling and Sealing of Abandoned Pipelines	40

7.7	Temporary Fences and Barriers	41

7.8	Traffic Requirements	41

8	CLEARING AND GRUBBING	42

8.1	Clearance of Sites	42

8.2	Protections	42

8.3	Road Furniture	42

8.4	Disposals	42

8.5	Blasting	42

8.6	Notice of Commencement	43

9	EARTHWORKS	44

9.1	General	44

9.1.1	Notice of Commencement	44

9.1.2	Earthworks to Lines and Levels	44

9.1.3	Extent of Excavations	44

9.1.4	Backfill	45

9.1.5	Borrow Areas	45

9.1.6	Preliminary Tests for Compacted Fill	45

9.1.7	Compaction of Fill	46

9.1.8	Excavation of Unsound Material	47

9.1.9	Replacement of Soil	47

9.1.9.1	Replacement of Soil with Non-Cohesive Soil	48

9.1.9.2	Soil Replacement with Concrete	48

9.1.10	Foundation on Improved/Reinforced Subsoil	48

9.1.10.1	Compaction	48

9.1.10.2	Soil Stabilization	49

9.1.11	Slips, Falls and Excess Excavation	49

9.1.12	Excavation to be Kept Free from Water	50

9.1.13	Embankments and Site Grading	50

9.1.14	Stripping of Topsoil	52

9.1.15	Trial Holes	52

9.1.16	Inspection by the Engineer	52

9.1.17	Crossing Watercourses	52

9.2	Structures and Pipelines	52

9.2.1	Dewatering	52

9.2.2	Excavation	53

9.2.3	Tests on Groundwater	53

9.2.4	Tests on Formation Level	53

9.2.5	Disposal of Surplus Excavated Material	53

9.2.6	Over-Excavation	54

9.2.7	Excavation for Pipes	54

9.2.8	Hand Trimming at Formation Level	54

9.2.9	Filling to not Endanger Structures	55

9.2.10	Selection and Compaction of Backfill	55

9.2.11	Filling of Excavations beneath Roads	56

9.2.12	Reinstatement of Public Highways	56

9.2.13	Levelling of Areas	57

9.3	Sheeting and Bracing	57

9.4	Additional Site Investigation	57

9.4.1	General	57

9.4.2	Soil Investigation Report	58

9.4.3	Design of Structures	58

9.4.4	Limit States	58

9.4.5	Durability	59

9.4.6	Ground Treatment	59

9.4.7	Geotechnical Design Report	60

10	CONCRETE	61

10.1	General Requirements	61

10.2	Standards	61

10.2.1	Production control	61

10.2.2	Classes of Concrete Strength	62

10.2.3	Properties of concrete in special environmental conditions	62

10.2.3.1	Watertight concrete	62

10.2.3.2	Freeze-resistant concrete	62

10.2.3.3	Freeze-resistant and sulphate-resistant concrete	63

10.2.3.4	Wear-resistant concrete	63

10.2.3.5	Resistance of concrete to chloride migration	63

10.2.4	Aggregates	63

10.2.5	Water for Concrete	64

10.2.6	Cement	64

10.2.7	Concrete	64

10.2.8	Concrete prefabricated elements	66

10.2.9	Concrete Repair	66

10.2.10	Admixtures / Additives	67

10.2.11	Fibres	67

10.3	Design Concrete Requirements	67

10.3.1	Classes of Concrete	67

10.3.2	Crack Control under Working Load	67

10.3.3	Testing of Tanks	68

10.3.4	Minimum Elements Thickness	68

10.4	Organization of Concrete Production at the Site	69

10.5	Ready Mixed Concrete	69

10.6	Materials and Testing	69

10.6.1	General	69

10.6.2	Cement	69

10.6.2.1	Type of Cement	69

10.6.2.2	Tests of Cement	70

10.6.2.3	Delivery and Storage of Cement	70

10.6.2.4	Cement Measured by Weight	71

10.6.2.5	Rejection of Cement	71

10.6.3	Quality of Water	71

10.6.4	Aggregate	71

10.6.4.1	Fine and Coarse Aggregates	71

10.6.4.2	Granulometric Composition of Aggregate	71

10.6.4.3	Storage of Aggregates	72

10.6.4.4	Tests on Aggregates	72

10.6.5	Delivery of Samples	72

10.6.6	Admixtures for Concrete	72

10.6.7	Fibres	72

10.7	Mixing and Testing	72

10.7.1	Concrete Classes	72

10.7.2	Proportions of Materials	72

10.7.3	Concrete Mix Design	73

10.7.4	Preliminary Mix Tests	73

10.7.5	Trial Mixes of Concrete	73

10.7.6	Concrete Testing	74

10.7.7	Compliance Requirements for Concrete	74

10.7.8	Mixes Not Approved	74

10.7.9	Additional Testing of Concrete	75

10.7.10	Water Content	75

10.7.11	Weigh Batching and Mixing	75

10.7.12	Ready-Mix Concrete	77

10.7.13	Transporting Concrete	77

10.7.14	Sand-cement Mortar	77

10.8	Placing and Compaction of Concrete	77

10.8.1	Depositing in Layers	79

10.8.2	Concrete Placed in Water	79

10.8.3	Production and Placing of Concrete under Special Conditions	79

10.8.4	Test Blocks	80

10.8.5	Compaction of Concrete	81

10.8.6	Bonding of Old and New Concrete	82

10.8.7	Protection and Curing of Concrete	82

10.8.8	Record of Concreting	82

10.8.9	Faulty Work	83

10.8.10	Blinding Concrete (Sub-base)	83

10.8.11	Loading of Concrete Structures	83

10.9	Joints	83

10.9.1	Construction Joints	83

10.9.2	Expansions Joints	84

10.9.2.1	Filler Boards	84

10.9.2.2	Dowel Bars	84

10.9.2.3	Sealing Grooves and Sealant	84

10.9.3	Water-stops	85

10.9.4	Metal Components Cast in Concrete	86

11	SHUTTERING AND CONCRETE FINISHES	87

11.1	General	87

11.2	Drawings and Calculations	87

11.3	Materials for Shuttering	87

11.4	Fixing of Shuttering	87

11.5	Back Shuttering	87

11.6	Internal Ties	88

11.7	Coating to Prevent Adhesion	88

11.8	Access Holes	88

11.9	Cleaning and Re-use of Shuttering	88

11.10	Removal of Shutters	88

11.11	Finish to Concrete Surfaces	89

11.12	Dimensions and Surfaces of In-Situ Concrete	89

11.13	Remedial Treatment of Concrete Surfaces	90

11.14	Dry-pack Mortar	90

11.15	Concrete Injection	91

12	STEEL REINFORCEMENT	92

12.1	General	92

12.1.1	Reinforcement Supply and Testing	92

12.2	Types, Quality and Storage	92

12.3	Prestressing Steel	93

12.4	Bending and Cutting Schedules	94

12.5	Protection and Cleaning	94

12.6	Bending of Bars	94

12.7	Cutting of Wire Fabrics	94

12.8	Lapping of Bars and Wire Fabrics	94

12.9	Fixing of Reinforcement	95

12.10	Approval before Concreting	95

13	PRESTRESSED CONCRETE	96

13.1	Sustainability of Prestressed Concrete Structures	96

13.2	Tendons	96

13.2.1	General	96

13.2.2	Tendon Fabrication and Supply	96

13.2.3	Storage and Cleaning	97

13.2.4	Testing Requirements for Tendons	97

13.2.4.1	Manufacturer's Test Data	97

13.2.4.2	Field Tests to Confirm Stressing Calculations	97

13.2.5	Corrosion Protection of Unbounded Tendons	98

13.2.6	Anchorage	98

13.2.6.1	Types of Anchorage	98

13.2.6.2	Anchorage for Bar Tendons	98

13.2.6.3	Anchorage for Multiple Strand Tendons	98

13.2.6.4	Anchorage for Multiple Wire Tendons	99

13.2.6.5	Requirements	99

13.2.6.6	Anchorage Reinforcement	100

13.2.7	Sheathing	100

13.2.7.1	Specific Requirements	100

13.3	Installation of Pre-Tensioning Systems	101

13.3.1	Pre-Tensioning Anchorages Installation	101

13.3.2	Pre-Tensioning Tendon Installation	101

13.4	Installation of Post-Tensioning Systems	102

13.4.1	Grout Holes Installation	102

13.4.2	Tendon Installation	102

13.5	Stressing Equipment	102

13.6	Stressing Records	103

13.7	Pre-Tensioning Stressing	104

13.7.1	Pre-Stressing	104

13.7.2	Single Straight Strand Stressing	104

13.7.3	Multiple Straight Strand Stressing	104

13.7.4	Draped Strand Stressing	104

13.7.5	Wire Breakage	105

13.7.6	Strand Chucks and Splice Chucks	105

13.7.7	Cleanliness of Prestressing Steel	106

13.8	Detensioning	106

13.8.1	Method of Stress Transfer	106

13.8.2	Trimming Strands	107

13.9	Post-Tensioning Stressing	107

13.9.1	Stressing Procedure	107

13.9.2	Tensioning with one Jack	108

13.10	Grouting	108

13.10.1	Preparation of the Duct before Grouting	108

13.10.2	Grout Materials and Properties	108

13.10.3	Mixing and Pumping Equipment	109

13.10.4	Grouting	109

13.10.5	Trimming	110

14	PRECAST CONCRETE UNITS	111

14.1	General	111

14.2	Concrete Quality and Tests on Concrete	111

14.3	Cast-in Parts	112

14.4	Transport, Storage and Erection	112

14.5	Installation of Precast Concrete	112

14.6	Manufacturing in a Factory	112

14.7	Work Programme and Method Statement	113

15	CONNECTIONS TO CONCRETE STRUCTURES, TEMPORARY HOLES AND OPENINGS	114

15.1	General	114

15.2	Building-in Pipes and other Items	114

15.3	Cutting or Displacement of Reinforcement	114

15.4	Cleaning	115

15.5	Grouting in Narrow Spaces	115

15.6	Joint between Old and New Concrete	115

15.7	Grouting under Hand-railings	115

16	COATINGS ON CONCRETE SURFACES	116

16.1	General	116

16.2	Preparation of Surface	116

16.3	Application	116

16.3.1	Priming Coat	116

16.3.2	First Coat	116

16.3.3	Second and Subsequent Coats	116

16.3.4	Number of coats	117

16.3.5	Holidays or Skips	117

16.3.6	Quantity and Curing	117

16.3.7	Coating underside of Structures	117

17	STRUCTURAL STEELWORK	118

17.1	Standards	118

17.2	Basic Steel Materials for Structure	122

17.2.1	Special Requirements	123

17.2.2	Takeover of Material	123

17.3	Construction procedure	123

17.4	Welding	124

17.4.1	Quality Control of Welded Joints	124

17.5	Screws	124

17.6	Fabrication of structure in the workshop	125

17.6.1	Storage of Materials	125

17.6.2	Actions Preceding Fabrication of Structure	125

17.6.3	Workshop Fabrication	126

17.6.4	Acceptance of Structure in the Workshop	127

17.6.5	Delivery of the Structure	127

17.7	Erection of the structure	127

17.8	Temporary scaffolding and construction aids	128

17.9	Protection against corrosion	128

17.10	Galvanising	129

18	STEELWORK COATING SYSTEMS	130

18.1	General	130

18.2	Coating System 1	130

18.3	Coating System 3	131

18.4	Coating System 4	132

18.5	Coating System 5	132

18.6	Coating System 6	133

18.7	Coating System 7	133

18.8	Coating System 8	134

19	MASONRY WORKS	135

19.1	General	135

19.2	Standards	135

19.3	Masonry units	135

19.4	Mortar	136

19.4.1	Sand	136

19.4.2	Cement	136

19.4.3	Hydrated lime	136

19.4.4	Water	136

19.4.5	Mortar Mix	136

19.5	Workmanship	136

19.6	Wall ties	137

19.7	Miscellaneous	137

19.8	Plastering	137

19.8.1	Mortar	137

19.8.2	Decorative mortar	137

19.8.3	Workmanship	138

19.9	Floor Screed	138

19.9.1	Standards	138

19.9.2	Workmanship	139

20	INSULATION WORKS	140

20.1	Moisture protection	140

20.1.1	Description of work	140

20.1.2	General requirements	140

20.1.3	Materials	140

20.1.3.1	Standards	140

20.1.3.2	Damp proof Course	141

20.1.3.3	Polythene Membrane	141

20.1.3.4	Bitumen and Bitumen Solution	141

20.1.3.5	Building Paper	141

20.1.3.6	Waterproofing Felts	141

20.1.4	Workmanship	142

20.1.4.1	Generally	142

20.1.4.2	Preparation of Surfaces	142

20.1.4.3	Laying the Felts	142

20.1.5	Steel Sheet Flashing	143

20.2	Thermal Protection	143

20.2.1	Description of Work	143

20.2.2	General Requirements	143

20.2.3	Materials	143

20.2.3.1	Standards	143

20.2.4	Workmanship	144

20.2.4.1	General	144

20.2.4.2	Preparation of Surfaces	145

20.2.4.3	Fixing the Boards	145

21	DRY WALL PARTITIONS AND SUSPENDED CEILINGS	146

21.1	Drywall Partitions	146

21.2	Suspended Ceilings	146

22	CARPENTRY WORKS	148

22.1	Generally	148

22.2	Materials	148

22.3	Protection of wood structure	148

22.4	Workmanship	148

22.5	Glued wood structures	149

22.6	Restrictions during wood structure execution	150

23	ROOFING	151

23.1	General	151

23.2	Roof Panel	151

23.3	Profiled trapeze Steel Sheet	151

23.4	Membrane Roofing System	151

23.5	Roof Domes	152

23.6	Canopies	152

23.7	Steel Sheet Flashing and External Roof Gutters	153

23.8	Roof Accessories	153

23.8.1	Rainwater Outlets	153

23.8.2	Vent pipes	153

23.9	Galvanized Steel Sheet	153

23.10	Movement Joint Sealant	153

24	FAÇADE WORKS	154

24.1	Metal cladding facade system	154

24.1.1	Facade thermal panel	154

24.1.2	Profiled trapeze Steel Sheet facade system	154

24.2	Contact thermal facades	155

24.3	Scaffold	155

25	WINDOWS AND DOORS	156

25.1	Materials	156

25.2	Standards	157

25.3	Glass	158

25.4	Roller Shutter Doors	158

25.4.1	Materials of Construction	159

25.4.1.1	Door Curtain	159

25.4.1.2	Accessories	159

25.4.1.3	Miscellaneous	159

25.5	External Doors and Frames	159

25.6	External Windows	160

25.7	Flush Doors	160

26	IRONMONGERY	161

26.1	Generally	161

26.2	Metal Doors	161

26.2.1	General	161

26.2.2	Construction	161

26.2.3	Erection	161

26.2.4	Metal Frames	161

26.3	Fire Rated Doors	162

26.4	Metal Lathing, Expanded Metal and Wire Mesh	162

26.5	Indoor and outdoor Fences	162

27	FINISHING WORKS: WALLS, CEILINGS	163

27.1	Paintings works	163

27.2	Wall- tiling	163

28	INTERNAL FLOORING	165

28.1	General	165

28.2	Ceramic tile flooring	165

28.3	PVC Flooring	166

28.4	Anti-static Flooring and Computer Room Flooring	166

28.5	Textile flooring	166

28.6	Aluminum entrance mat	167

28.7	Industrial flooring with additive spread	167

28.8	Granolithic Flooring	168

28.9	Workmanship	168

29	SIGNS	169

30	SANITARY SYSTEM	170

30.1	Scope of Work	170

30.2	General	170

30.3	Pipes and Fittings	170

30.4	Joints and Connections	170

30.5	Unions	170

30.6	Hangers, Spacing and Support	170

30.7	Manholes and Inspection Pits	171

30.8	Sleeves	171

30.9	Protection and Cleaning	171

30.10	Installation of Pipes	171

30.11	Inspection, Storage and Connections	171

30.12	Main Cold Water Supply Pipe	172

30.13	Water Distribution and Plumbing	172

30.14	Testing of Sanitary System	172

30.15	Pressure Tests of Drainage	173

30.16	Pressure Tests of Water Supply Pipes	173

30.17	Flow Test	173

30.18	Cleaning and Disinfection of the Pipelines	173

30.18.1	Preliminary Flushing	173

30.18.2	Cleansing	174

30.18.3	Disinfection	174

30.18.4	Bacteriological Testing	174

31	ROADWORKS	175

31.1	Geodetic Works	175

31.2	Demolition and removal of road facilities	176

31.3	Top Soil Stripping	176

31.4	Bulk Excavation of Soil	176

31.5	Distribution of Earth Quantities and Stockpiles	177

31.6	Treatment of Subsoil	177

31.7	Construction of the Fill – Replacement Layer	178

31.8	Quality Control Concerning the Fill	179

31.8.1	Criteria for assessment of quality of material for the fill	179

31.8.2	Control of treated and compacted layer of the fill	179

31.9	Mechanically Stabilized Underlying Load-Bearing – Subbase Layer	180

31.9.1	Materials	180

31.9.1.1	Quality of Stone Material	180

31.9.2	Execution	183

31.9.2.1	Supply of Materials	183

31.9.2.2	Preparation of road foundation surface	184

31.9.2.3	Transportation of material for the underlying load-bearing layer	184

31.9.2.4	Adding of material	184

31.9.2.5	Mixing and Trimming	184

31.9.2.6	Compaction	184

31.9.2.7	Depositing of materials	184

31.9.3	Method of Control and Criteria for Quality Assessment	185

31.9.3.1	Compaction	185

31.9.3.2	Layer Evenness	185

31.9.3.3	Levels	185

31.9.4	Acceptance of Constructed Load-bearing Layer	186

31.10	Asphalt Pavements	186

31.10.1	General	186

31.10.2	Bituminous Works	186

31.10.3	Weather Limitations	186

31.10.4	Preparation	186

31.10.5	Transportation	187

31.10.6	Placing	187

31.10.7	Compaction of Mixtures	187

31.11	Kerb Laying	188

31.12	Construction of shoulders	189

31.13	Footpaths	189

32	TECHNICAL CONTAINERS	190

32.1	The floor and bottom frame	190

32.2	Roof container frame	190

32.3	Container columns	190

32.4	External walls of the container	190

32.5	Anti-corrosive protection	190

32.6	The door	190

32.7	Windows on the container	191

32.8	Electrical installation:	191

33	FENCES AND LANDSCAPING	192

33.1	Submissions	192

33.2	Materials	192

33.2.1	Fences and Gates	192

33.2.2	Top Soil	192

33.2.3	Grasses	192

33.2.4	Trees and Shrubs	192

33.2.5	Gravel	193

33.3	Erection of Fences and Gates	193

33.4	Landscaping	193

33.4.1	Tree Felling	193

33.4.2	Inspection of Retained Trees	193

33.4.3	Protection of Retained Trees	193

33.4.4	Maintenance of Retained Trees	194

33.4.5	Replacement of Damaged Trees	194

33.4.6	Preparation of Ground	194

33.4.7	Cultivation of Ground	194

33.4.8	Time for Planting	195

33.4.9	Leaching	195

33.4.10	Grassing	195

33.4.11	Irrigation	195

33.4.12	Maintenance	195

33.4.13	Replacement	195

33.4.14	Soil Testing	196

34	Landfill Cassette	197

34.1	Compacted soil (2 x 25 cm) (k = 1.0×10-6 – 1.0×10-8 m/s)	197

34.2	Geo-synthetic clay – GCL (к <≤1.0×10-11 m/s)	197

34.3	HDPE membrane integrity grid of sensors	199

34.4	HDPE membrane d ≥ 2.5 mm thick	199

34.4.1	Control of the liner base	200

34.4.2	Delivery and storage of the HDPE liner	201

34.4.3	Installation of the HDPE liner	201

34.4.4	Anchoring	202

34.4.5	Welding of the HDPE liner	202

34.4.6	Installation of drainage layer	202

34.4.7	Performance Report for HDPE liner works	203

34.4.8	Quality control on welding works	203

34.4.9	Monitoring of the quality of HDPE installation	206

34.5	Geotextile of minimum 1,200 g/m2 and of minimum 300 g/m2	206

34.5.1	Delivery and storage	207

34.5.2	Installation	207

34.5.3	Anchoring	207

34.5.4	Control of installed material	207

34.6	Geosynthetic leachate drainage liner	208

34.7	Drainage gravel	208

35	PIPEWORK	209

35.1	General	209

35.2	Standards	210

35.3	Quality Certificates	217

35.4	Wall Passing	218

35.5	Support of Pipework and Valves	218

35.6	Adapters	218

35.7	Rubber Compensators	219

35.8	Ductile Iron Pipes, Laying and Testing	219

35.8.1	General	219

35.8.1.1	Norms and Standards	219

35.8.1.2	Quality of Pipes, Fittings and Accessories	219

35.8.1.3	Socket and Spigot Pipes and Fittings	219

35.8.1.4	Flanged Pipes and Fittings	219

35.8.1.5	Coatings and Linings	220

35.8.1.6	Transport and Storage	220

35.8.2	Laying and Jointing	220

35.8.2.1	Re-rounding and Cutting of Pipes	220

35.8.2.2	Excavation of Trenches	220

35.8.2.3	Bedding of Pipes	220

35.8.2.4	Laying and Jointing of Pipes	221

35.8.2.5	Thrust and Anchor Blocks	221

35.8.2.6	Locking Joints	221

35.8.2.7	Surround to Pipes	222

35.8.2.7.1	Selected Fill Surround	222

35.8.2.7.2	Concrete Bed and Surround	222

35.8.2.7.3	Pipe Supports	223

35.8.2.7.4	Backfilling	223

35.8.3	Accessories	223

35.8.3.1	Mechanical Couplings	223

35.8.3.2	Dismantling Joints	223

35.8.3.3	Flanged Anchoring Sleeves	223

35.8.3.4	Surface Boxes	223

35.8.4	Corrosion Protection	223

35.8.4.1	Sleeving of Pipelines	223

35.8.4.2	Protection of Bolted Joints	224

35.8.5	Testing of Pipelines	224

35.8.5.1	Testing of Pressure Pipelines	224

35.9	Steel Pipes, Laying and Testing	225

35.9.1	General	225

35.9.2	Materials	225

35.9.3	Manufacture	225

35.9.4	Dimensions	226

35.9.4.1	Electric Resistance Welded Pipes	226

35.9.4.2	Submerged Arc Welded Pipes	227

35.9.5	Pipe lengths	228

35.9.6	Sampling, Inspections and Tests	228

35.9.7	Internal Lining	229

35.9.7.1	Large Diameter Pipes	229

35.9.7.2	Small Diameter Pipes	229

35.9.8	External Coating	229

35.9.9	Marking, Tolerance Class and Certification	230

35.9.10	Transport, Storage and Stringing of Pipes	230

35.9.11	Bends	231

35.9.11.1	General	231

35.9.11.2	Elastic Bends	231

35.9.11.3	Field Bends	232

35.9.11.4	Factory Made Bends	233

35.9.11.5	Tees and Y’s	233

35.9.12	Welding of Pipelines	233

35.9.12.1	Materials	234

35.9.12.2	Welding Processes	234

35.9.12.3	Welding Procedure Qualification	234

35.9.12.4	Qualification of Welders and Welding Operations	234

35.9.12.5	Welding Preparation	235

35.9.12.6	Welding	235

35.9.12.7	Cleaning after Welding	235

35.9.12.8	Post Weld Heat Treatment	235

35.9.12.9	Identification of Weld Seams	235

35.9.12.10	Closing of Pipe Ends	236

35.9.13	Welding Inspection	236

35.9.13.1	General Requirements	236

35.9.13.2	Extent of Examination	236

35.9.13.3	Acceptance Criteria	237

35.9.13.4	Production Testing	237

35.9.13.4.1	Document Requirements	237

35.9.14	Coating of Weld Seams	238

35.9.15	Pipe Lowering	238

35.9.16	Other Jointing Methods	238

35.9.16.1	Threads	238

35.9.16.2	Flanged Joints and Mechanical Couplings	239

35.9.17	Pipe Laying and Pressure Testing	239

35.9.17.1	Excavation of Trenches	239

35.9.17.2	Bedding of Pipes	239

35.9.17.3	Thrust Blocks	239

35.9.17.4	Surround to Pipes	239

35.9.17.4.1	Selected Fill Surround	239

35.9.17.4.2	Concrete Bed and Surround	239

35.9.18	Cathodic Protection System	239

35.9.18.1	General	239

35.9.18.2	Standards	240

35.9.18.3	Specification of the Works	240

35.9.18.4	Material Specification	240

35.9.18.4.1	Ancillary Anodes	240

35.9.18.4.2	Anodes for Ground Installation	241

35.9.18.4.3	Anode Bed Material	241

35.9.18.4.4	Transformer/Rectifier Unit	241

35.9.18.4.5	Measuring Posts	241

35.9.18.4.6	Installation	241

35.9.18.4.7	Pre-Commissioning	242

35.9.18.4.8	Operation and Maintenance	242

35.9.19	Isolating Flanges	242

35.10	Stainless Steel Pipework	243

35.11	Mild Steel Pipework	243

35.12	Galvanized Steel Pipes	244

35.13	Copper Pipes and Fittings	244

35.14	Concrete Pipes, Laying and Testing	244

35.14.1	General	244

35.14.2	Pipe Laying and Testing	245

35.14.2.1	Excavation of Trenches	245

35.14.2.2	Bedding of Pipes	245

35.14.2.3	Surround to Pipes	245

35.14.2.4	Pipe Supports	245

35.14.2.5	Backfilling	245

35.14.2.6	Testing	245

35.15	Plastic Pipes, Laying and Testing	246

35.15.1	Unplasticized Polyvinyl Chloride (PVC) Pipes	246

35.15.1.1	Jointing	246

35.15.2	HDPE Pipes	247

35.15.3	GRP Pipes	247

35.15.4	General Requirements	248

35.15.5	Pipe Laying and Testing	248

35.15.5.1	Excavation of Trenches	248

35.15.5.2	Bedding of Pipes	248

35.15.5.3	Thrust and Anchor Blocks, and Locking Joints	248

35.15.5.4	Surround and Protection to Pipes	248

35.15.5.4.1	Selected Fill Surround:	248

35.15.5.4.2	Concrete Slab Protection:	248

35.15.5.4.3	Concrete Bed and Surround:	249

35.15.5.4.4	Pipe Supports	249

35.15.5.4.5	Backfilling	249

35.15.5.4.6	Testing of Non-Pressure Pipelines	249

35.15.5.4.7	Testing of GRP Pressure Pipelines	249

35.15.5.4.8	Testing of Thermoplastic Pressure Pipelines	249

35.16	Cable Conduits	249

35.17	Flanges, Bolt, Nuts and Washers	250

35.18	Joints	250

35.18.1	Bolted Gland Joints	250

35.18.2	“Push-In-Type” Joints	250

35.18.3	Flanged Joints	250

35.18.4	Welded Joints	251

35.19	Fittings and Accessories – General	251

35.19.1	Tees and Wyes	251

35.19.2	Bends	251

35.19.3	Dismantling Joints	251

35.19.4	Flexible Couplings	252

35.19.5	Anchoring Sleeves	252

35.20	Valves, Penstocks and Actuators	252

35.20.1	Valves and Penstocks - General	252

35.20.2	Spindle Operation	253

35.20.3	Hand wheels	253

35.20.4	Sluice Gates	254

35.20.5	Sluice Valves	254

35.20.6	Gate Valves	254

35.20.7	Reflux Valves	255

35.20.8	Penstocks	255

35.20.9	Air and Gas Relief Valves	256

35.20.10	Butterfly Valves	256

35.20.11	Pressure Control Valves	258

35.20.12	Flap Valves	259

35.21	Manholes and Chambers	259

35.21.1	General	259

35.21.2	Construction details	259

35.21.3	Manhole Accessories	259

35.22	Bricks	260

# GENERAL DATA

## Introduction

These Specifications are to be read in conjunction with the rest of Volume 3 and in particular with the Employer’s Requirements.

## Objective of the Works

The main objective of this Contract is design and construction of Regional Waste Management Centre (RWMC) in the City of Novi Sad, in order to establish a long-term sustainable regional waste management system.

# SETTING OUT OF THE WORKS

## General

The Works shall be set out and tied to the National Co-ordinate System. The Contractor shall establish temporary benchmarks and survey stations at suitable locations on the Site of the Works and during the progress of the Works shall periodically check the levels of the benchmarks and the co-ordinates of the stations against the original points lines and levels of reference given by the Engineer. Temporary benchmarks and survey stations shall be located clear of the construction Works, unless otherwise approved.

The Contractor shall submit to the Engineer for approval drawings in duplicate showing the locations and levels or co-ordinates as appropriate of each and every temporary benchmark and survey station used for the setting out of the Works.

The Contractor shall before commence execution of any given section of the Works submit to the Engineer complete setting out details with supporting calculations and drawings (including drawings showing the locations and co-ordinates of the reference points used) in duplicate for approval.

The Contractor shall identify setting out dimensions for all structures by relating them to existing Works and by interpretation of the Drawings. The gradients of sewers and pipelines and the levels of weirs, inverts of channels and other hydraulic structures shall be as shown on the drawings unless otherwise required or approved by the Engineer.

The locations of structures to be constructed as part of the Works shall be identified by reference to steel pins set in concrete or other approved markers set up by the Contractor, who shall also determine the coordinates of the markers and their distances from adjacent existing structures.

The Contractor shall establish reference co-ordinate points at intervals of not more than 500 m along all sewers and major pipelines and these points shall be located and clearly marked at approved locations either on existing buildings or by means of steel pins fixed in concrete.

The Contractor shall set out sections of the Works at such times as may be directed by the Engineer to enable Service Authorities to carry out temporary or permanent alterations to their equipment or buried services.

## Execution and Workmanship

The Contractor shall employ well-qualified and experienced surveyors approved by the Engineer for the execution of the survey work and setting out as described in the Contract.

Geodetic works include:

- setting- out the route and buildings,

- all measurements related to the transfer of data from design documentation to nature or from nature to appropriate technical documentation,

- survey of completed foundations

- measurement and placement of formwork, reinforcement and other elements in the prescribed and required position,

- procurement and installation of benchmarks, i.e. progress measurements as part of geotechnical investigations during construction, as well as preparation of auscultation study, all in accordance with the Survey design.

- maintenance of setting-out on the location during the entire period from the beginning of the works to the handover of all works to the Employer.

The Survey design during construction and during exploitation has to be developed, all in accordance with the Rulebook on content and manner of technical inspection of buildings, composition of the commission, content of proposed decision of the commission regarding the usability of the building, survey of soil and the building during construction and use, and minimum guarantee periods for different types of buildings ("Official Gazette of RS", No. 27/2015 and 29/2016).

The surveyor should inform the Engineer about all works in a timely manner, as well as enable him to cooperate with them.

The scope of geodetic works should in all respects meet the needs of construction, control of works, calculations and alike that constitute the conditions for realization of works.

Geodetic works include preparation of technical documentation of the finally set-out and constructed road and/or building.

The survey instruments to be used by the Contractor shall be of the modern type and make, and suitable for the work to be executed and shall be maintained in a first class condition. The instruments and/or equipment shall be subject to the approval of the Engineer.

For all survey, instruments used in the Works the Contractor shall submit recent calibration certificates issued by competent authorities. Further calibration of the instruments shall be carried out every six months.

All field-books, calculations, maps, etc. of the survey activities mentioned above shall be handed over to the Engineer immediately after the completion of the survey work.

The Contractor shall provide the necessary skilled and unskilled labour and materials to the Engineer to enable him to check and approve the levels and setting out of the alignments and positions of structures.  The Contractors shall record the progress of the Work on electronic photos.

The Contractor shall provide, for State Quality Control Inspection, a schedule of the main phases of the construction.

# STANDARDS

## Standard Specification

Wherever in the Employer’s Requirements and General Technical Specifications is referred to specific standards and codes to be met by the materials, plant and other supplies to be furnished, and work performed or tested, the provisions of the latest current edition or revision of the relevant standards and codes in effect shall apply, unless otherwise expressly stated in these documents. Where such standards and codes are national, or relate to a particular country or region, other authoritative standards which ensure a substantially equal or higher performance than the standards and codes specified will be accepted subject to Engineer’s prior review and written approval. Differences between the standards specified and the proposed alternative standards must be fully described in writing by the Contractor and submitted to the Engineer at least twenty-eight (28) days prior to the date when the contractor desires the Engineer’s approval. In the event the Engineer determines that such proposed deviations do not ensure substantially equal performance, the Contractor shall comply with the standards specified in the documents.

The conditions specified in these general specifications are minimum requirements for all deliveries and performances. If special requirements are given for particular items they apply only to these particular items. The Contractor shall propose Standards for the execution of the works, which shall be approved by the Engineer. A list of Standards is included in these TR (Employer’s Requirements and General Technical Specifications).

In referring to the Standard Specifications the following abbreviations are used:

| ATV | Abwasser Technische Vereinigung - German Association for Water, Wastewater and Waste, see DWA |
| --- | --- |
| BS | British Standard |
| BSCP | British Standard Code of Practice |
| CEE | International Commission of Rules for the Approval of Electrical Equipment |
| DIN | Deutsches Institut für Normung e.V. - German Institute for Standardisation |
| DVGW | Deutsche Vereinigung des Gas- und Wasserfachs e.V. - The German technical and scientific organisation on Gas and Water |
| DWA | Deutsche Vereinigung für Wasserwirtschaft, Abwasser und Abfall - German Association for Water, Wastewater and Waste (former ATV) |
| EN | European Standards |
| IEC | International Electrotechnical Commission |
| ISO | International Organization for Standardization |
| SRPS EN | Serbian standards harmonized with EN |
| UVV | Unfall-Verhütungs-Vorschriften (Regulations of Accident Prevention) |
| VDE | Verband Deutscher Elektrotechniker – German Association for Electrical, Electronic & Information Technologies |

## Standards on Site

The Contractor shall purchase and keep on Site at least one copy of each of the relevant Standards, Codes and Manuals or approved National Standards which are referred to in the Specification. In addition, the Contractor shall keep on Site a copy of any other Standard, Code, Manual, or National Standard, which applies to materials supplied.

Copies of the standards shall be made available for reference at all times at the office of the Engineer. If the Engineer requires an English or Serbian translation of any of the Standards or Manuals the Contractor shall provide a typed copy of the translation within 7 days of receiving a written request from the Engineer.

## Matters not Covered by Standards

Any materials and workmanship not fully specified herein, or covered by the Standards, Codes or Manuals, shall be of such type and quality so as to produce a first-class work. In such circumstance, the Engineer shall determine whether all or any of the materials offered or delivered to the Site are suitable for use in the Works and the Engineer’s decision in this respect shall be final and conclusive.

# DESIGN DOCUMENTATION

These Specifications are to be considered also for electrical and mechanical design documentation!

## General

Design documentation (Design for Construction Permit/Projekt za gradjevinsku dozvolu and Design for Execution/Projekat za izvodjenje) shall be prepared in accordance with the actual Serbian Law on Planning and Construction published in the Official Gazette of the RoS.

Design for Construction Permit shall be approved by the Technical Control according to the Serbian Law on Planning and Construction. Also, the Designs (Design for Construction Permit and Design for Execution) shall be checked by the Engineer in order to have approval that the Design has been prepared in accordance with the tender dossiers.

The Contractor is obliged to adhere to all valid laws and bylaws, valid regulations, standards and technical recommendations in the Republic of Serbia.

If any changes in relevant technical standards, rules and regulations occur during the construction process, they should be respected.

Technical documentation shall be prepared in accordance with the Location Conditions, as well as in accordance with other conditions of the competent authorities.

The Contractor is obliged to prepare the design documentation, which is the subject of the Contract, in accordance with the following legislation (but not limited to):

- Law on planning and construction ("Official Gazette of RS", No 72/2009, 81/2009 - correction, 64/2010 – decision of the CC, 24/2011, 121/2012, 42/2013 – decision of the CC, 50/ 2013 – decision of the CC, 98/2013 – decision of the CC, 132/2014, 145/2014, 83/2018, 31/2019, 37/2019 - other law, 9/2020, 52/2021 and 62/2023),

- Rulebook on the content, manner and procedure of preparation and manner of control of technical documentation according to classes and occupancies of buildings ("Official Gazette of RS", No. 73/2019),

- Law on Fire Protection ("Official Gazette of RS", No. 111/2009, 20/2015, 87/2018 and 87/2018 - other laws),

- Rulebook on technical norms for installations of hydrant fire extinguishing network ("Official Gazette of RS", No. 3/2018),

- Rulebook for building structures with Annex 1 and Annex 2 (“Official Gazette of RS”, No. 89/2019, 52/2020, 122/2020),

- Rulebook on technical fire safety requirements for exterior walls of buildings (“Official Gazette of RS”), No.59/2016, 36/2017 and 6/2019),

- Rulebook on technical standards for planning, designing and erection of buildings, which ensure unhindered movement and access for people with disabilities, children and the elderly ("Official Gazette of RS", No. 22/201,

- Rulebook on classification of buildings ("Official Gazette of RS", br. 22/2015),

- Rulebook on content and manner of technical inspection of buildings, composition of the commission, content of proposed decision of the commission regarding the usability of the building, survey of soil and the building during construction and use, and minimum guarantee periods for different types of buildings ("Official Gazette of RS", No. 27/2015, 29/2016 and 78/2019),

- Rulebook on energy efficiency of buildings ("Official Gazette of RS", No. 61/2011)

- Law on construction products ("Official Gazette of RS", No. 83 of October 29, 2018, as well as all regulations in this area.),

- Law on Environmental Protection,

- Law on nature conservation,

- Landscape architecture standards.

The Contractor shall, at his own cost, prepare:

- Design for construction permit (Projekat za građevinsku dozvolu - PGD),

- Design for execution (Projekat za izvođenje- PZI),

- As-Built Design (Projekat izvedenog objekta - PIO),

- Subdivison plan (Etažni elaborat posebnih delova)

- Survey design during construction and use, completely in accordance with Rulebook on content and manner of technical inspection of buildings, composition of the commission, content of proposed decision of the commission regarding the usability of the building, survey of soil and the building during construction and use, and minimum guarantee periods for different types of buildings ("Official Gazette of RS", No. 27/2015 and 29/2016)

Reports and studies that shall be enclosed with the Design for construction permit:

      - Report of geotechnical conditions for construction;

      - Fire protection study, establishing the fire protection measures,

      - Energy efficiency study, for buildings for which the establishment of energy properties is prescribed, in accordance with the regulations governing the field of energy efficiency;

      - Environmental Impact Assessment Study - to be submitted by the Employer.

Elaborates and studies that shall be attached to the Design for execution:

- Preventive measures plan, which is prepared in accordance with the regulations governing safety and health at work on temporary or mobile construction sites;

- Main fire protection design (Glavni projekat zaštite od požara)

- Quality control and assurance program that includes an overview and specification of performance of all construction and other products, assembly elements that are to be installed in the building, as well as a description of the required tests and required results that prove the required quality and fulfilment of main requirements.

If necessary, the Contractor shall develop the Preliminary works design (Projekat pripremnih radova), which shall include the Demolition design, Foundation pit protection design, Design for maintaining the groundwater level, etc.

In order to conduct the building demolition on the site, it is necessary to prepare the Demolition design in accordance with Serbian legislation. This design shall be subject to technical control and it shall be necessary to obtain approval/positive technical control opinion to the same.

Based on the Demolition design, it shall be necessary to obtain a Decision on approval for demolition from the competent authorities.

## Working Drawings and Calculations

The Contractor shall prepare and submit all Working Drawings and calculations including details for the construction and completion of the Works. These drawings and calculations shall be produced and submitted to the Engineer for his approval, and shall comprise the following:

Civil and Structural:

- Layout plans

- General arrangement and foundation drawings complete with dimensions, for all buildings, tanks, plant and associated equipment.

- Structural calculations and drawings including foundation design.

- Reinforced concrete details, structural steelwork and masonry drawings.

- Reinforcement drawings and calculations for in-situ and pre-cast concrete.

- Calculation of construction physics (within Energy efficiency study):  thermal, acoustic etc,

- Calculation of fire load of building and drawings according to the Law on fire protection and Law of Planning and Construction.

- Bending schedules.

- Fabrication drawings (shop drawings) for any structural steelwork.

- Installation plans of steel and pre-cast concrete structures,

- Architectural and building works drawings including masonry, cladding, roofing, etc, and all specified fixtures and finishes both externally and internally.

- Details of protective coating design.

- Layout plans of roads and levelling plans,

- Computation of pavement structure with construction drawings including kerbing and drainage details.

- Drawings of fencing details and arrangements.

- Landscaping, land drainage, sub and top soiling and all ancillary works.

Pipelines:

- Site plan and general arrangement drawings.

- Pipeline profiles.

- Drawings and schedules showing all pipework, fittings, chamber and trench details and thrust block arrangements.

- Reinforcement drawings and calculations for thrust blocks to pipework.

- Drawings, calculations and method statements for all road, rail and river/channel crossings and connections to existing pipework.

Hydraulic calculations:

- Hydraulic calculations, including determination of test pressures.

- Water levels

- Velocity in pipes and constructions.

Table 1: Minimum velocity in pipes and constructions

| Minimum velocity | m./sec. |
| --- | --- |
| Water containing sand | > 0,40 |
| Water containing active sludge until 4kg/m3 | > 0,20 |
| Water containing (active) sludge > 4 kg/m3 | > 0,30 |
| Influent without sand | > 0,20 |
| Effluent | > 0,10 |

Table 2: Maximum velocity in pipes and constructions

| Maximum velocity | m./sec. |
| --- | --- |
| Design velocity | 0,80 to 2,00 |
| Under special circumstances in consultation with the Engineer | > 2,00 |

## Record Drawings

The Record Drawings shall basically comprise the Contractor’s Working Drawings as listed above, showing the Works as-constructed.

The Contractor shall provide paper copies and digital copy of each computer generated drawing.

## Procedure for the Working Drawings and Calculations

The drawings and calculations, which have to be produced by the Contractor, shall be made and submitted in accordance with the following requirements.

Sheet sizes shall be in accordance with international sizes unless otherwise agreed by the Engineer

The drawings of all parts of the construction shall be clear and complete. The choice of scale will depend on the kind of drawing and/or details to be presented.

The recommended scales are as follows:

Table 3: Recommended scales for drawings

| Drawing subject | Recommended scales |
| --- | --- |
| Pipeline plans | 1:500 |
| Site plans/layouts | 1:500 to 1,000 |
| General arrangements | not less than 1:100 |
| Details | 1:50 to 1:10 |

The preferred format for drawings is A1 or A2 size (A0 if essential), with a further set reduced at A3 size.

Drawings at non-standard scales (e.g. 1:331/3 and 1:75) are unacceptable.

The Contractor shall submit three copies of all drawings and calculations to the Engineer when seeking his approval and the Engineer will return one copy of the drawings and calculations to the Contractor with his comments.

Alterations and/or remarks made by the Engineer on the drawings or calculation shall be incorporated immediately and the drawings and/or calculations re-submitted in three copies until final approval is obtained.

Four copies of each set of the approved drawings and calculations shall be submitted to the Engineer. The drawings shall be clearly rubber stamped as “WORKING DRAWING APPROVED BY THE ENGINEER” in English.

The Contractor shall obtain approval of third parties to the design of any permanent Works for which he is responsible. This shall include approval from the Technical Auditor for civil construction and infrastructure and operating safety in accordance with Serbian Law, or subsequent revisions.

Commencement of work on any part of the Works construction will only be permitted after the approval by the Engineer of the Contractor’s drawings and calculations.

Engineer's approval of the Contractor's drawings and calculations including any alterations made by the Engineer shall not relieve the Contractor of his obligations to execute the Works in accordance with the Contract.

All modifications requested by the Engineer shall be carried out without any additional charge.

## Operation and maintenance cost

The influence of the proposed pipes (material, diameter) and equipment on the operational cost should be estimated.

Outline calculations of maintenance cost of all works over a ten years period, separated into fixed and variable cost, should be provided. This should include details:

- Energy and chemicals;

- Likely replacement of equipment (flow meters, water meters) and the running cost of the various electrical components.

## Criteria for design personnel

The Design Personnel shall be suitably qualified to undertake the work and shall be expert in their areas of work and should fulfil criteria in accordance with the current Serbian Law on Planning and Construction.

A Professional Indemnity insurance policy shall be in place to protect the Employer/Investor from inadequate or imperfect design. Details should be submitted with the tender.

# DESIGN CRITERIA

## Design Life

All works shall be designed to provide the design life as specified in Employer’s Requirements.

## Structural Design General

The works shall be designed in all respects to conform to the latest current engineering practice.

During the structural design development, the following standards and their valid national annexes shall be adhered to:

- Eurocode 0: Fundamentals of Structural Design, SRPS EN 1990

- Eurocode 1: The Role of Structures, SRPS EN 1991

- Eurocode 2: Design of Concrete Structures, SRPS EN 1992

- Eurocode 3: Design of Steel Structures, SRPS EN 1993

- Eurocode 4: Design of Steel-Concrete Mixed Structures, SRPS EN 1994

- European 5: Wood Structure Design, SRPS EN 1995

- Eurocode 6: Design of Masonry Structures, SRPS EN 1996

- Eurocode 7: Geotechnical Engineering Design, SRPS EN 1997

- Eurocode 8: Seismic Design of Structures, SRPS EN 1998

All structural elements of the building shall be calculated for the purpose of approving the reliability of the structure: load capacity, stability, usability and durability.

The design for execution must include all stages and has to analyse the impact of measures on the environment and safety and health at work. It shall also include, but not be limited to:

- Calculation of scaffolding

- Calculation of temporary and auxiliary buildings

- Stiffening calculation during the lifting / installation phase

- Calculation of temporary connections and behaviour of steel elements during lifting,

- Calculation of cables, lifting capacity of cranes, loads, etc.

- Calculation of all phases during construction, etc.

Structural Design: all foundations, structural concrete, steelwork, wooden construction shall be designed in accordance with International and Serbian standards as stated in the following chapters.

Calculations shall be performed by recognized licensed software with the drafted report (data exported from the software) in English or Serbian language. The Contractor should enable insight in the software calculation for the members of the technical control team and the Engineer team responsible for the independent review of the Design. The Contractor must hold a sufficient number of licenses.

## Earthworks and Foundations

### Design

For construction of access roads and structures, require the execution of earthworks, such as, removing of shrubs and trees, clearance of Site, relocation of existing utilities, excavation, filling and embankment construction, compaction, drainage during execution of works, and levelling layer formation, the Contractor shall follow the guidelines of SRPS EN 16907-1- Earthworks - Part 1: Principles and general rules for planning, design and specification of earthworks.

The Design shall be in accordance with SRPS EN ISO 13793 - Thermal performance of buildings - Thermal design of foundations to avoid frost heave.

Design shall take into account the most extreme conditions that will occur during construction and the life of the works, including inter alia, highest and lowest water levels and water pressure, construction methods, etc.

Design shall in general take into account the provisions presented in Paragraph “Structural Design General”, and the specifics outlined in this Paragraph and Paragraph “Earthworks”.

The possibility of reduced soil properties during and after earthquake loading shall be considered in design (e.g. liquefaction of loose sand).

### Durability

For all geo-technical design, the internal and external environmental conditions shall be estimated at the design stage to assess their significance in relation to durability and to enable provisions to be made for the protection or adequate resistance of the materials.

### Fill Materials

The criteria for selecting material as suitable for use as fill shall be based on achieving adequate strength, stiffness and permeability after compaction. These criteria shall take account of the purpose of the fill and the requirements of any structure to be placed on it.

The following aspects shall be considered when selecting a fill material:

- grading

- resistance to crushing

- compactibility

- organic content

- chemical aggressivity

- susceptibility to volume change (swelling clays and collapsible materials)

- the effects of frost

- resistance to weathering

The fill material shall not contain foreign matter as snow, ice or peat in any significant amount.

Compaction criteria shall be established for each zone or layer of fill, related to its purpose and performance requirements. The compaction works shall be checked by inspection or testing in order to ensure that the nature of the fill material, its placement water content and the compaction procedures are consistent with those prescribed.

### Excavations to be refilled with granular material

A drain system to dissipate hydrostatic uplift forces shall be incorporated into the design of a tanks. The area excavated outside the tank walls to provide working space shall be backfilled with free draining granular material, extending the finished ground level down to the base of the wall.

Should the width of the excavated working area exceed 1.0 m (measured horizontally, perpendicular to the wall face) then only the 1.0 m wide vertical strip adjacent to the wall must be backfilled with granular material.

All fill material beneath structures shall be clean, coarse grained, free draining granular material.

### Embankment Design

Placement and compaction of fill shall be carried out as outlined in “Structural Design General”, “Preliminary tests for compacted fill”, “Compaction of fill” and “Embankments and site grading”.

### Foundation design

All spread foundations shall be designed in accordance with the “Rulebook for building structures with Annex 1 and Annex 2” (“Official Gazette of RS”, No. 89/2019, 52/2020, 122/2020).

All spread foundations shall be founded on original undisturbed ground or on structural fill compacted to an average of 100% Proctor density and a 97% Proctor density as a minimum, and at such depth as to provide adequate protection against frost damage to the formation/foundation.

The effects of air temperature and fluctuations in air temperature shall be taken into account in the designs.

The Contractor shall apply SRPS EN 1997-1 and SRPS EN 1997-2 as well as accompanying National Annexes (NA) of Republic of Serbia in 2020.

For the structural design, the Contractor must determine in which geotechnical category the structural foundations are to be classified.

The significant soil properties and characteristic values of geometrical parameters shall be determined through geotechnical testing according to above-mentioned SRPS EN.

The Contractor must carry out a survey before starting the foundation works.

For foundation excavations, the method of calculating excavation depth and dimensions shall be specified in the Technical Specifications and shall be submitted to the Engineer for approval before the Commencement of Works.

#### Shallow Foundations

Shallow foundations shall be designed and executed in accordance with SRPS EN 1991-2 and SRPS 1992-2, together with National Annexes in force in 2020 in the Republic of Serbia.

#### Deep Foundations

Contractor shall design and execute piles in accordance with the following standards: SRPS EN 1536, SRPS EN 12699, SRPS EN 12794 and SRPS EN 14199.

Single piles or single-row pile groups under abutments or girders with longitudinally fixed bearings are only permitted with the integral construction method.

For structural reasons, the pile cap must be at least 30 cm over the piles in the case of displacement and bored piles. The pile cap must be at least 60 cm thick.

#### Bored Piles - HW

In derogation of SRPS EN 1536 for the manufacture of bored piles a maximum eccentricity of 0.05 x D (D = pile diameter) and a slope deviation of 0.015 m per meter of pile length with regard to the nominal value is permitted.

The above manufacturing variations must be taken into account when measuring bored piles, regardless of actual variations. The load-distributing effect of pile-plate foundations or equivalent may be taken into account.

A higher strength class than C30/37 may not be taken into account in calculations.

Uncased holes for piles are only permitted in rocks and only with the approval of the Engineer.

The Contractor must demonstrate to the Engineer that the piles comply with the guidelines in the calculation and dimensioning approaches taking into account the soil conditions and/or the information in the geotechnical report by submitting the site records as set out in SRPS EN 1536.

In-situ concrete piles must be concreted to at least 50 cm above the lower edge of the pile cap. This overhang must be cut back after digging the excavation pit for the pile cap to 5 cm.

The longitudinal reinforcement must be distributed evenly along the perimeter. Contractor shall take all necessary measures to ensure that the concrete cover is in compliance and to secure the position of the longitudinal reinforcement.

### Water Loading

It shall be checked that the principles used in design are appropriate for the groundwater features that are encountered.

Structures shall be designed to resist water loading due to external water level. Uplift forces on structures, tanks and pipes shall be calculated assuming they are empty.

Structures that are to be water tested before backfilling shall be designed accordingly.

Determination of the design water pressure on soil retaining structures shall take account of the water levels above the ground and the groundwater table. For structures retaining soil of medium or low permeability (silts and clays), water pressures shall be assumed to act behind the wall corresponding to a water table assumed to be no lower than the top face of the material with low permeability unless a reliable drainage system is installed or infiltration is prevented.

Permanent vertical anchors adopted in design against uplift of structures shall take into account all circumstances during the foreseeable design life of the anchorage including considerations related to corrosion and creep. The load carrying resistance of an anchorage shall be evaluated from test results and from local experience.

## Structural Concrete

### Codes and Standards

All types of concrete constructions must be designed in accordance with the standards from series SRPS EN 1990, SRPS EN 1991, SRPS EN 1992, with corresponding National Annexes and other standards referred to by these standards. Loads on structures are calculated in accordance with Eurocode 0: Basis of Structural Design, SRPS EN 1990 with National Annexes. For earth-quake resistant structures, Eurocode 8: Seismic Design of Structures, SRPS EN 1998, with national Annexes shall be applied.

Concrete is determined (characteristics performance, requirements etc…) in standard SRPS EN 206 (Concrete- Specification, performance, production and conformity) and the provisions related to concrete production of Rulebook on Technical Standards for Concrete and Reinforced Concrete (PBAB 87) too, while for materials and construction products,  they are listed in the SRPS EN 1992-1-1 standard with National Annexes (concrete, reinforcing steel, prestressing steel, prestressing devices, prefabricated concrete elements).

### Water Loading

Structures shall be designed to resist water loading caused by external water level. Uplift forces on structures, tanks and pipes shall be calculated assuming they are empty.

Structures that require being water tested before backfilling shall be designed for no external pressure during testing. The design of walls for structures and tanks shall allow for accidental filling to freeboard by water to the top of main walls (i.e. above freeboard level).

## Structural Steel – Codes and Standards

The Contractor is obliged to comply with Eurocode 3 and the provisions of all parts of the SRPS EN 1993 standard when designing the main steel structure and the latest version of the National Annexes thereof.

Loads on structures shall be calculated in accordance with Eurocode 0: Fundamentals of Structural Design, SRPS EN 1990 with national annexes. For earth-quake resistant structures, Eurocode 8: Seismic Design of Structures, SRPS EN 1998, with national Annexes shall be applied.

Materials and construction products listed in the SRPS EN 1993 series standards shall be used for steel structures, whose performance shall be in accordance with the appropriate technical specifications referred to in these standards. The selection of the main material for supporting steel structures shall be conducted on the basis of the Serbian SRPS EN 1993-1-10 and the relevant National Annexes.

Additional standards are listed in the chapter “Structural steelwork”.

## Wooden construction - Codes and Standards

The Contractor is obliged to comply with Eurocode 5 and the provisions of all parts of the SRPS EN 1995 standard when designing the main steel structure and the latest version of the National Annexes thereof.

Loads on structures shall be calculated in accordance with Eurocode 0: Fundamentals of Structural Design, SRPS EN 1990 with national annexes. For earth-quake resistant structures, Eurocode 8: Seismic Design of Structures, SRPS EN 1998, with national Annexes shall be applied.

Loads on structures shall be calculated in accordance with Eurocode 0: Fundamentals of Structural Design, SRPS EN 1990 with National Annexes. For seismic resistant structures, Eurocode 8: Seismic Design of Structures, SRPS EN 1998, with national annexes is applied.

Materials and construction products listed in the SRPS EN 1995 series standards shall be used for wooden structures, whose performance shall be in accordance with the appropriate technical specifications referred to in these standards. The selection of the main material for supporting steel structures shall be conducted on the basis of the Serbian SRPS EN 1995-1-2 and the relevant National Annexes.

## Architecture and Buildings

### General

Architectural Design shall be developed completely in accordance with legislation of the RS and the issued Location conditions and any additional Planning Authority requirements.

The design shall be developed in accordance with the process requirements, established occupancy, number of functional units, vertical and horizontal regulation and position on the plot, access to buildings, capacity and method of connection to communal and other technical infrastructure, for each building on the location:

- Which are to be demolished,

- New building (planned for construction),

- The existing building that shall be adapted/reconstructed/rehabilitated.

When shaping and determining the program and functional characteristics of the building, the Contactor is obliged to design buildings with the following characteristics:

a)	Mechanical resistance and stability. All structures shall present as low a profile as possible;

b)	Fire safety;

c)	Hygiene and environmental health. The use of natural light for internal illumination, augmented by electrical lighting shall be carried out where practical;

d)	Safety and accessibility during exploitation;

e)	Noise protection;

f)	Energy saving and heat retention;

g)	Sustainable use of natural resources.

h)	External finishes shall be durable and resistant to the weather conditions;

i)	The general form, colour and fenestration of the building shall be simple.

The design of thermal protection must be prepared on the basis of standards for heat engineering in civil engineering, specifically (but they are not limited to):

- SRPS EN ISO 6946 – Building components and building elements - Thermal resistance and thermal transmittance - Calculation method (ISO 6946:2017)

- SRPS EN ISO 13788 - Hygrothermal performance of building components and building elements Internal surface temperature to avoid critical surface humidity and interstitial condensation - Calculation methods (ISO 13788:2012)

- SRPS EN ISO 12572 - Hygrothermal performance of building materials and products - Determination of water vapour transmission properties – Cup method (ISO 12572:2016)

- SRPS EN ISO 13786 - Thermal performance of building components - Dynamic thermal characteristics - Calculation methods (ISO 13786:2017)

- SRPS EN ISO 15927 - Hygrothermal performance of buildings - Calculation and presentation of climatic data - Part 1: Monthly means of single meteorological elements (ISO 15927-1:2003)

- SRPS EN ISO 10211 - Thermal bridges in building construction - Heat flows and surface temperatures - Detailed calculations (ISO 10211:2017)

- SRPS EN ISO 13370 - Thermal performance of buildings - Heat transfer via the ground - Calculation methods (ISO 13370:2017)

- SRPS EN ISO 13789 - Thermal performance of buildings - Transmission and ventilation heat transfer coefficients - Calculation method (ISO 13789:2017)

- SRPS EN ISO 10077 - Thermal performance of windows, doors and shutters - Calculation of thermal transmittance - Part 1: General (ISO 10077-1:2017)

- SRPS EN ISO 12567 - Thermal performance of windows and doors - Determination of thermal transmittance by the hot-box method - Part 1: Complete windows and doors (ISO 12567-1:2010)

### Masonry

Generally, Structural Masonry shall be designed in accordance with the SRPS EN 1996 - Eurocode 6 - Design of masonry structures.

### Roofs

All roofs shall meet the recommended standard for heat and sound insulations, fire rating and loading for building.

### Walls

All walls shall meet the recommended standard for heat and sound insulations, fire rating and loading for building.

Expansion joints shall have an approved filler built in as the Works proceed, ensuring no projections into the cavity.

### Windows and Doors

All windows and doors shall meet the recommended standard for heat and sound insulations, fire rating and loading for building.

External doors and windows shall be made of the thermally insulated profile according to the calculation of Energy efficiency study. Opening shall be glazed with insulated low-e glass units (U factor according to EN, has to be compliant with the Energy efficiency study). The buildings entrance doors shall be safety doors.

All interior doors shall be dry-installed, made of aluminium sections and solid leaf filled with aluminum or glazed with flat glass.

### Facades

All facades shall meet the recommended standard for heat and sound insulation, fire rating and shall be durable and resistant to the weather conditions.

### Internal Works

Internal walls shall be made of brick blocks, plastered and finished, or carried out with drywall systems made of gypsum boards, finished. The surfaces of the reinforced concrete structure in the halls shall be prepared and finished.

The interior walls shall be painted or coated with ceramic tiles, according to the functional requirements of the space.

Concrete floors shall have an approved chemical hardener applied 14 days after curing if floor surfaces are to be left uncovered. If industrial vinyl flooring is to be used, it shall have a non-slip finish. All items of plant shall be raised above the floor level on concrete plinths a minimum of 100 mm.

The flooring systems, shall be designed in accordance with functional and process requirements. The floors shall be finished with: ceramic tiles, PVC coverings, anti-static coverings, textile coverings, or concrete floors/ industrial floor (shall have top layer made of mineral granular grit).

All flooring systems must be durable, non-slip, easy to maintain, fire rating and other characteristics shall be in accordance with the fire protection requirements of the design.

Stairs shall have in built non-slip treads and risers. Constructions to be such as will facilitate easy cleaning.

Aluminum handrails shall not be painted.

The ceilings, shall be plastered and finished or they shall be carried out as suspended ceilings made of mineral tiles (finished) or gypsum tiles and finished.

The painting specifications (including surface preparation) shall be such to provide a long-term protection to the applied surface and shall have a minimum 15-year maintenance free life on all steelwork. Future maintenance painting of steelwork must be considered.

All Internal finishes should be simple and durable.

## Roads, Hard standings and Footpaths

This section covers the design of roads, and their surface water drainage.

### General

Road, hard standings, footpaths and associated drainage shall be laid out to plans prepared by the Contractor to the approval of the Engineer.

Road, hard standings, footpaths and associated drainage shall be designed in compliance with the group of Serbian standards ICS 93.020 and ICS 93.080.

A traffic management scheme incorporating all traffic signs (regulatory and informative) and road markings shall be proposed by the Contractor for the approval of the Engineer. This scheme shall be designed to limit the maximum vehicular speed to 20 km/hour within the boundary of the new works.

All roads shall be kerbed.

### Design of Roads

Carriageway widths and turning circles shall be as specified in the Particular Requirements.

Pavement design for roads and hard standings shall be in accordance with the Local Authority Road Regulations. The design shall be based on a design life of 50 years and traffic volumes envisaged for operation of the works, unless otherwise specified.

The Contractor shall make his own assessment of the traffic and the subgrade CBR at the site and accordingly design the thickness of the road base and surfacing.

Carriageway construction and surfacing to hard standings shall be resistant to diesel and other chemical spillage.

### Design of Drainage

The Contractor shall design and construct drainage system to carry away rainwater from roofs and paved areas regarding Serbian standards ICS 93.080.30. The drainage shall consist of gutters, downpipes, gullies, pipes and open ditches and shall be laid out with adequate falls. Where roads are edged with upstanding kerbs on both sides, the roads shall be drained to gullies provided with gratings and connected into the drainage system.

## Pipelines

### Load Cases

Pipework and pipelines shall be designed for all foreseeable load cases including the following:

- Maximum working pressures on completed pipelines;

- Field test pressure on completed parts of the pipeline and the whole of the pipeline (field test pressures);

- Required hydrostatic test pressure on individual pipes and fitting at the place of manufacture (works hydrostatic test pressures).

The works hydrostatic test pressures and the field test pressures shall be as given in the Specification or as required to demonstrate adequate factors of safety.

Notwithstanding the foregoing and taking into consideration the Specification’s requirements for the class of bedding for rigid and flexible pipes, all pipelines, fittings and pipeline appurtenances shall be designed to give adequate factor of safety against:

- Maximum internal forces developed from working pressures, field test pressures;

- Minimum and maximum surge pressures arising under any operational conditions;

- Maximum external forces arising from external loading conditions including forces arising from self weight, flotation, superimposed loads and temperature variations;

- External corrosion having regard to the protection specified and the nature of the ground and groundwater likely to be encountered;

- Forces arising when pipes and fittings are handled and laid.

### Anchorages and Thrust Blocks

Anchorages and thrust blocks for pressure pipelines shall be designed to resist any pulls or thrusts to which they may be subjected. If there is unacceptable movement at a thrust block or anchor, the Contractor shall redesign and rebuild the structure with such increased factors of safety as are necessary to provide adequate resistance.

### Chambers

All chambers shall have lockable access covers. Chambers that require man entrance (generally greater than 900 mm deep) shall be provided with minimum access area of 900 mm x 750 mm. Step irons shall be installed in all chambers. Step ladders shall be installed in all chambers over 1.5 m deep. Where vertical ladders are installed in chambers over 2.5 m deep they shall be provided with hoop safety cages.

### Air Valves

The Contractor shall provide large orifice valves installed in such numbers and at such locations as will:

- Prevent the entrapment of large volumes of air at any high point of the pipeline during its filling;

- Permit lengths of pipeline between valves to be safely filled with water and emptied of all air in a time not exceeding 4 hours.

- Prevent negative pressures exceeding 3 m vacuum occurring anywhere along the pipelines during surge conditions or emptying.

Small orifice valves shall be installed at every high point in a pipeline length (except where the high point is an open end within a structure with a free water surface) for the purpose of releasing air under normal operating conditions. A high point in a pipeline length shall be defined as any of the following:

- Any top access manhole cover or any abrupt rise of the pipeline, such as to cross an obstacle or similar;

- Any point to which the pipeline rises steadily in the direction of normal flow for a length greater than 750 m and to an average grade steeper than 1 in 500 and thereafter is level or falls below a level grade or long horizontal lengths greater than 750 m.

As a minimum requirement the size of air valves required should be such that the inlet area of the valve is not less than 1.25% of the pipeline cross sectional area. If the design requires a larger size, the design requirement shall apply.

Table 4: Air valves - Minimum requirements

| Diameter of main [mm] | Air valve diameter [mm] | Flange diameter |
| --- | --- | --- |
| Up to 600 | 80 | 80 |
| 650 and over | 100 | 100 |

All large orifice air valves shall be mounted on tees above the pipeline. Extension pipes shall be used to ensure that air valves are close to the ground level and can be easily reached for maintenance. The air and isolating valves shall be located above any potential ground water.

All air valves shall be mounted in a chamber and installed with an isolation valve to enable servicing, including the removal of the air valve without shutting off the main. All air valves shall be fitted with a drain plug to be used for testing, drainage or leak detection. Air valves shall be adequately insulated and protected from the likelihood of freezing.

# EXECUTION AND COMPLETION OF THE WORKS

## Materials

Generally, for materials that are to be installed in the facility:

- Submit the entire description literature for each type of material or components of materials that are to be installed in the building. Provide sufficient data to demonstrate compliance with specified requirements.

- Before the materials delivery, certified copies of reports, quality proofs, certificates... and all the necessary tests according to regulations, ordinances, rulebooks and the mentioned publications, shall be submitted to the Employer and approved by him in writing.

- The tests have to be conducted in an independent accredited laboratory approved by the Engineer. Additional tests shall be conducted if the source of the material is changed.

## Preliminary Works

The Contractor is obliged to perform Preliminary works that precede the building construction and are related to securing the foundation pit, adjacent buildings and public areas, securing the groundwater levels during the works execution, earthworks with special reference to the preparation of the subsoil and the quality of the excavation material, etc.

It is important to point out that before commencement of any work on securing the foundation pit, existing services/utilities, adjacent buildings and public areas, the Zero condition study has to be developed covering the adjacent buildings, existing services/utilities and public areas with textual and photo documentation with special reference to cracks, damages, deflections, defects in services/utilities. The above-mentioned documentation has to be prepared by an accredited and authorized institution for that type of work. In addition, the preliminary works refer to: construction and positioning of temporary buildings and services/utilities required for works execution – the Contractors representative and Engineer, provision of area for delivery and storage of construction material and all other works ensuring safety of adjacent buildings, rehabilitation of the terrain and ensuring smooth flow of traffic and use of surrounding areas.

Preliminary works include fencing the construction site, provision of connections, construction of temporary  roads, installation of warning signs, assembly and disassembly of temporary protective metal fence (according to the Rulebook on occupational safety during construction works ("Official Gazette of RS", no. 53/97) ) that shall be mounted until the completion of the building, installation of the construction information board in accordance with the regulations, installation of the gate and warning sign for passers-by, temporary lighting of the construction site and entrance.

## Execution of Concrete and Reinforced Concrete Works

### General

All structures of concrete shall be made in accordance with SRPS EN 13670 (Execution of concrete structures). Where additional concrete beyond normal structural design needs is introduced for the purpose of gaining dead weight to counter the effects of buoyancy, any such additional concrete shall, so far as possible, be uniformly distributed among the substructure members.

The control of concrete before installation in a concrete structure shall be carried out in accordance with the standards SRPS EN 206, SRPS.M1.206, SRPS EN 13670 and the Rulebook for building structures with Annex 1 and Annex 2 ("Official Gazette of the RS", No. 89/ 2019, 52/2020, 122/2020)

The installation of concrete, reinforcement and prefabricated concrete elements in a concrete structure shall be carried out according to the SRPS EN 13670 standard.

Control of reinforcing steel, prestressing steel, reinforcement and prefabricated concrete elements before installation, shall be carried out in accordance with the Serbian standard SRPS EN 13670 and the Rulebook for building structures with Annex 1 and Annex 2 ("Official Gazette of RS", No. 89 /2019, 52/2020, 122/2020).

## Other Works

Other works shall be carried out as it is specified in this GTS.

# DEMOLITION AND PROTECTION OF WORKS

## General

In order to demolish buildings on the site, it is necessary to prepare a Demolition design in accordance with Serbian legislation. This design shall be subject to technical control.

Permission for demolishing existing buildings and structures which issued by competent authorities shall be obtain by Contractor.

Details of the buildings and structures to be demolished by the Contractor shall be ascertained during the construction of the Works and shall be to the approval of the Engineer.

No demolition of any existing building or structure shall be carried out until it has been approved by the Engineer in writing.

The complete demolition shall be carried out including the foundations, unless otherwise specified or directed by the Engineer.

## Disposal of Demolition Materials

All materials arising from the demolition and clearance of the building, structures and other objects mentioned above shall be disposed of off Site.

## Refilling and Finishing

All voids shall be refilled with soil compacted to the same density as the surrounding soil and the surface shall be finished to the existing ground level and to the satisfaction of the Engineer.

## Permission

Permission for demolishing existing buildings and structures shall be applied in writing to the Engineer and shall be accompanied with a demolition programme. No demolition shall take place before obtaining the Engineer's permission and the area has been provided with all necessary relevant temporary Works and/or diversions, which have been either requested or authorized by the Engineer.

## Protection of Existing Objects

The Contractor shall not demolish or remove any existing buildings, structures or other objects including trees, whether indicated on the Drawings or not, unless on a specific instruction from the Engineer. The Contractor shall take every care and precaution to protect from damage any of these objects, including houses, buildings, fences or trees, which are situated on or near the Site(s).

Any property situated in close proximity to the Works shall be protected against any damage which could be caused by vehicles, subsidence, vibration, etc. Any damage caused shall be repaired by the Contractor to conform to the condition of the property prior to damage and to the satisfaction of the Engineer.

## Filling and Sealing of Abandoned Pipelines

Where existing pipelines (sewers, water pipelines, etc.) are connected to the new systems, the length of the sewer downstream to the connection, which is not incorporated into the new system, shall be abandoned.

Buried sewer pipelines to be abandoned shall be sealed with mass concrete plug of minimum length 1,000 mm at either ends and between manholes.

Manholes on abandoned pipelines shall be demolished to a depth of 500 mm below final ground level and the void filled with hard core or other approved fill material and surface reinstated to a finish similar to that of the surrounding area.

## Temporary Fences and Barriers

All boundaries of the Contractors offices, work yards, workshops, depots and stores shall be agreed with the Engineer. A proper fencing, including lockable gate, shall be provided by the Contractor along the agreed boundaries.

The Contractor shall erect similar fences around all construction sites before commencing work, and dismantle them after the Works has been completed.

The fencing shall be in close-boarded timber, aluminum or steel corrugated sheets 2400 mm high fixed on timber, concrete or steel posts. All fenced areas shall be provided with lockable gates. In some of the areas agreed with the Engineer, the Contractor may provide chain link fencing or galvanized wire netting.

## Traffic Requirements

Before any work in, or affecting the use of, any highway or road is commenced, the Contractor’s proposed method of working, including any special traffic arrangements, shall be agreed with, and confirmed in writing to, the Engineer and the Highway or Roads Authority, and Police Authority.

Throughout the Contract, the Contractor shall cooperate with the Highway or Roads, and Police Authorities concerning works in, or access to, the highway or road. The Contractor shall inform the Engineer, of any requirements of, or arrangements made with, the Highway or roads, and Police Authorities.

Barriers shall be fixed around trenches in streets and pedestrian areas and properly sign posted. All barriers on roads and pedestrian areas shall be lit with warning lights during night time or when there is poor visibility.

Where the diversion or closure of any existing carriageway, footway or public right of way is temporarily necessitated by the Works, the Contractor shall provide and maintain an alternative, which shall be operational before interference with the existing way.

Where ramps are required, they shall be provided and maintained to a standard suitable in all respects for the class or classes or traffic or pedestrians requiring using them.

# CLEARING AND GRUBBING

## Clearance of Sites

The Contractor shall clear the reservation widths for pipelines and the Sites of structures free of all vegetation, including trees up to 0.50 m girth measured 1.00 m above ground level, and all superficial obstacles such as road surfaces, kerbs, bricks, rubbish and/or other objectionable matter.

When ordered by the Engineer in writing, the Contractor shall also clear the Sites of trees over 0.5 m girth, buildings and/or structures.

The extent of Contractor's clearing and grubbing operations shall be the minimum practicable necessary in the opinion of the Engineer for the construction of the Works.

## Protections

Trees and/or other vegetation designated on the Drawings or directed by the Engineer for preservation shall be kept free from clearing operation and be protected from injury during execution of the Works.

## Road Furniture

The Contractor shall re-install any road furniture (such as street lighting, traffic signs or traffic lights) that has to be removed during the progress of the Works.

Installation of the road furniture shall take place at its original location, in a condition at least equal to that prior to removal and as soon as practicable after completion of pipe laying at a particular location.

## Disposals

All vegetation, trees, etc. arising from the clearing and grubbing operations shall be dumped at a depot within a radius of approximately 15 kilometers to a location directed by the Engineer. Remnants of vegetation, including trees, stumps and roots, shall be disposed off Site by the Contractor unless otherwise directed by the Engineer.

## Blasting

No blasting shall be carried out without the written permission of the Engineer.

When necessary, blasting for clearing boulders and/or rock masses will be permitted only on written approval of the Engineer and when proper precautions are taken for the protection of all persons, the Works and public and private properties.

Blasting shall be carried out in a controlled manner and to the required depth, amount and extent necessary and by using only explosives of such quantity and strength and in such locations as will not structurally damage the material to be blasted outside the prescribed limits. Any damage to the Works or properties arising from the blasting shall be repaired by the Contractor to conform to the condition existing prior to damage.

Before any blasting is carried out, the Contractor shall ensure that adequate measures that are necessary for the safety and protection of persons and property against injury or damage has been provided and warning signs and signals has been installed, all to the satisfaction of the Engineer and other authorities concerned with safety and public order.

## Notice of Commencement

The Contractor shall give to the Engineer written notice of his intention to commence the clearing and grubbing and/or blasting operations. The works shall not be commenced until written approval has been received from the Engineer.

The Contractor shall ensure that all clearing, grubbing and blasting are carried out far enough in advance of other construction operations within the relevant areas in order to avoid delays.

# EARTHWORKS

## General

All earthworks must be carried out in accordance with the Elaborat on geotechnical investigations.

The Contractor shall prepare a method statement of his proposal for earthworks operation for each particular part of the Works to be constructed at any one time, detailing the location, programme of excavation, temporary supports and the placing and handling of the soil.

This specification shall apply to all types of earthworks and excavations.

### Notice of Commencement

The Contractor shall give to the Engineer written notice of his intention to commence earthworks on any part of the Site and shall furnish the Engineer with all ground levels and other particulars he may require for the purpose of carrying out measurements.

Earthworks shall not be commenced until written approval has been received by the Contractor from the Engineer.

### Earthworks to Lines and Levels

The whole of the earthworks for the several parts of the Works shall be carried out to the dimensions and levels shown on the Drawings or to such other dimensions and levels as may be ordered by the Engineer.

For the purpose of the Specification, the term “ground level” shall refer to the ground surface before the start of earthwork operations, but after the operations of clearing and grubbing. The expression “formation level” where used in the Specification shall mean the foundation level of the structure concerned including the blinding concrete.

### Extent of Excavations

The extent of excavations shall be the minimum necessary or practicable in the opinion of the Engineer for the construction of the Works.

The construction of open trenches shall be, at any one time, limited to lengths previously approved by the Engineer, in writing. Unless otherwise approved by the Engineer in writing, work on each approved length shall be completed to the satisfaction of the Engineer before work on any new length is commenced.

The maximum trench width shall be restricted to that shown on the approved pipeline design and drawings. In the event of any trench for pipelines being excavated with battered or stepped sides that portion of the trench which extends from the formation level to a point 300 mm above the crown of the pipe when laid in its correct position shall be formed with vertical sides to the dimensions shown on the Drawings unless otherwise approved by the Engineer.

Excavations for all other structures, measured at formation level, shall be limited to the contour-line of the structure plus 1 m on all sides.

No excavations with battered sides will be permitted in public highways, private gardens or within 30 meters of any building or other structure. In the event of the Contractor adopting the method of excavation with battered sides his obligations for providing supports shall be as specified in the Paragraph herein entitled “Slips, Falls and Excess Excavation”.

### Backfill

Backfill includes generally loading and transport of materials from intermediate stockpiles, placing of fill material in layers, adjusting of moisture content, compaction to the specified density and trimming of compacted surfaces.

Except where otherwise specified, the Contractor shall be responsible for the location of suitable sources of natural materials for the execution of the Works, whether such sources are on the Site or not, and for obtaining all necessary permissions, including certificates of occupancy, quarry licenses and water rights.

Materials available on the Site shall be used for the execution of the Works if the quality of such materials is sufficient.

The material shall be mechanically compacted in horizontal layers thickness not over 300 mm. Each layer shall be thoroughly compacted by mechanical tampers. The bearing modulus at the construction areas shall be at least E1 > 40 MPa and E2 / E1 ≤ 2.2 measured with plate bearing tests. The number of tests shall be at least 1 per 300 m2. The density shall be >92 % compared to the density obtained with modified Proctor Compaction Test.

The bedding zone below, lateral and above the pipe or cable shall be filled and carefully compacted by a method approved by the Engineer to avoid change in alignment and level of the pipes or cables.

Unless specified otherwise the excavation for pipes or cables shall receive a minimum layer of approved bedding material below the pipe or cable of depth in the trench according to SRPS EN 1610

Areas around or on top of structures shall be levelled to the required levels as indicated on the Drawings or instructed by the Engineer. The Contractor shall take due precautions to prevent any damage to the structures during the levelling. The levelling of areas around structures shall be carried out by approved methods. Any damaged item shall be replaced or repaired at the Contractor’s expense and to the satisfaction of the Engineer.

### Borrow Areas

It is the Contractors responsibilities to locate borrow areas for all kind of materials and obtaining, transporting and placing them when needed for the execution of the Works. The Contractor shall obtain the approval of the Engineer for the areas as well as for materials he proposes to use.

Where specified or ordered by the Engineer, fill material for incorporation in the Works shall be obtained from approved borrow areas after the completion of any tests to confirm the suitability of the material. On completion of excavation, the Contractor shall trim, grade or leave the borrow area in a tidy condition to the satisfaction of the Engineer and if ordered shall carry out without charge any further earthworks necessary to prevent accumulation of water in the area.

### Preliminary Tests for Compacted Fill

Quality control of materials for the fill should be exercised according to the following standards (but they are not limited to):

| - SRPS EN ISO 22475-1 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 1: Technical principles for the sampling of soil, rock and groundwater |
| --- | --- |
| - SRPS CEN ISO/TS 22475-2 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 2: Qualification criteria for enterprises and personnel (ISO/TS 22475-2:2006) |
| - SRPS CEN ISO/TS 22475-3 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 3: Conformity assessment of enterprises and personnel by third party (ISO/TS 22475-3:2007) |
| - SRPS EN ISO 17892-1 | Geotechnical investigation and testing - Laboratory testing of soil - Part 1: Determination of water content |
| - SRPS EN ISO 17892-3 | Geotechnical investigation and testing - Laboratory testing of soil - Part 3: Determination of particle density |
| - SRPS U. B1.016 | Testing of soils - Determination of density of soil in place by rubber-balloon method |
| - SRPS EN ISO 17892-4 | Geotechnical investigation and testing - Laboratory testing of soil - Part 4: Determination of particle size distribution |
| - SRPS EN ISO 17892-12 | Geotechnical investigation and testing - Laboratory testing of soil - Part 12: Determination of liquid and plastic limits |
| - SRPS U.B1.024 | Testing of soils – Determination of the combustible and organic matter content of a soil) |
| - SRPS EN 13286-1 | Unbound and hydraulically bound mixtures – Part 1: Test methods for laboratory reference density and water content – Introduction, general requirements and sampling |
| - SRPS EN 13286-47 | Unbound and hydraulically bound mixtures - Part 47: Test method for the determination of California bearing ratio, immediate bearing index and linear swelling |

Testing shall be carried out for every change of materials.

On stretches along the route where the fill shall be executed over previously treated, compacted, and accepted subsoil, materials that meet the following criteria may be applied:

- Maximum bulk density according to standards Proctor test Wopt 25 %.

- Liquid limit W must be below 65 %

- Plasticity index JP must be below 30 %.

### Compaction of Fill

Compacted fill shall consist of approved material, spread and compacted in layers approximately horizontal and of uniform thickness with a slight outward slope and of a compacted depth not exceeding 0.20 m after compaction.

Soil lumps larger than 0.10 m in size shall be broken before compaction. The moisture content of the soil shall be carefully controlled either by natural drying or wetting with a fine spray before filling.

Compaction shall be carried out by mechanical rollers, power rammers, vibro-tampers, vibrating plate compactors or other.

Control of treated and compacted layer of fill shall be done by determining the level of compactness at every 50 m according to the following regulations:

| - SRPS EN ISO 22475-1 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 1: Technical principles for the sampling of soil, rock and groundwater |
| --- | --- |
| - SRPS CEN ISO/TS 22475-2 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 2: Qualification criteria for enterprises and personnel (ISO/TS 22475-2:2006) |
| - SRPS CEN ISO/TS 22475-3 | Geotechnical investigation and testing - Sampling methods and groundwater measurements - Part 3: Conformity assessment of enterprises and personnel by third party (ISO/TS 22475-3:2007) |
| - SRPS EN ISO 17892-1 | Geotechnical investigation and testing - Laboratory testing of soil - Part 1: Determination of water content |
| - SRPS U.B1.016 | Testing of soils - Determination of density of soil in place by rubber- balloon method |
| - SRPS U.B1.046 | Testing of soils - Determination of compression modulus by circular slab method |

### Excavation of Unsound Material

If any material not complying with design requirements occurs in the foundations of structures, the Contractor shall remove it and dispose of it to the satisfaction of the Engineer. Unless otherwise specified or ordered by the Engineer, the Contractor shall fill the voids in the foundations so formed with Concrete Class C8/10.

If any material not complying with design requirements occurs in pipeline trenches, the Contractor shall remove it and dispose of it to the satisfaction of the Engineer. Unless otherwise specified or ordered by the Engineer, the Contractor shall fill the voids in the foundations so formed with Concrete Class C8/10. If the Contractor encounters any material which in his opinion may be material not complying with design requirements, he shall immediately inform the Engineer who will then instruct the Contractor in writing as to whether or not the said material shall be treated as unsound.

The cost of dealing with the material not complying with design requirements shall be borne by the Contractor if, in the opinion of the Engineer, the cause of unsoundness is due to failure of the Contractor to comply with the Specification, including keeping the excavation free from water.

Waste materials, i.e. excavated material classified as unsatisfactory soil material, waste, CDW, and surplus of satisfactory soil material shall be loaded and taken to the approved city landfill.

Waste generated during construction works should be handled in accordance with provisions of the Rulebook on waste handling, i.e. with the Law on Waste Management ("Official Gazette of RS", no. 36/2009, 88/2010 and 14/2016).

### Replacement of Soil

If any material not complying with design requirements occurs in the foundations of structures, the Contractor shall remove it and dispose of it to the satisfaction of the Engineer.

Soil may only be replaced with the agreement of the Engineer. The suitability of the soil replacement must be demonstrated by the Contractor.

Before the soil is replaced, the excavation base must be tested for compliance with the calculation or design methods and/or the information in the geotechnical report. In the case of replacement under water appropriate measures must be taken.

#### Replacement of Soil with Non-Cohesive Soil

Replacement of soil with non-cohesive soil can be performed only on a broad excavation basis. The suitability of the non-cohesive soil must be demonstrated by the Contractor through the taking of at least one sample per 500 m3 and by changing the removal pit.

Soil must be replaced on all sides of the excavation area with an overhang on the foundation area. The overhang must correspond to the layer thickness of the soil replacement.

Non-cohesive soil must be piled in layers.

#### Soil Replacement with Concrete

Soil replacement with concrete may be carried out on an extensive excavation basis, in a linear manner (ditch-shaped) and on a one-off basis (pillar-shaped).

Soil replacement with concrete must be carried out according to structurally required surface and depth dimensions.

### Foundation on Improved/Reinforced Subsoil

The technical specifications must be followed for subsoil improvement and reinforcement.

#### Compaction

Surface Compaction

The surface of the in-situ subsoil can be compacted using different rollers and vibrators to achieve the compaction requirements.

The Contractor shall provide Technical Specifications (degree of compaction and air space ratio where applicable) to the Engineer for approval. Contractor shall submit to the Engineer evidence of the required compaction.

Deep Compaction

The subsoil load-bearing capacity may be improved using deep vibrations or vibro-displacement. Information on deep compaction procedure may be taken from SRPS EN 14731. Deep vibration may also be carried out using energy input of vibratory compaction equipment.

The subsoil's load-bearing capacity may also be improved using drop weights or falling weights.

In the case of deep compaction, the compaction procedure must be described by the Contractor and timely submitted to the Engineer before commencement of works.

The Contractor must draw up a plan of the location and number of vibrating points.

The evidence required to determine the effectiveness of any remedial measures taken during deep compaction (air or water flush) must be set out in the Contractor’s Technical Specifications.

The Contractor must supply proof of suitability of the soil material to be installed during vibro- displacement before construction work starts.

A subsoil improvement factor must be provided in the Contractor’s Technical Specifications.

Before construction works start the Contractor must draw up a quality assurance plan in agreement with the Engineer to specify how the subsoil improvement factor is to be demonstrated.

The working level must be at least 50 cm above the scheduled foundation level of the structure and at least 50 cm above the groundwater level.

The Contractor must provide evidence of the required compaction.

After completion of the deep compaction, work surface compaction must be carried out.

#### Soil Stabilization

Soil stabilization remains within the foundation area. It is compacted through the addition of hydraulic binders or through the injection of appropriate chemical substances.

Stabilization Using Binders

Fixing the soil with limestone is not allowed in the construction phase of foundation construction. The Contractor must provide evidence of reinforcement, set up test areas and test mortars.

Stabilization Using Jet Grouting

Contractor shall apply SRPS EN 12716 requirements for soil cement stabilization with jet grouting.

Stabilization Using Injection and Compaction Grouting

The Contractor must provide evidence of the environmental impact and strength properties of the injection material in accordance with SRPS EN 12715. The Contractor using individual tests (e.g. boreholes) must test the injection result (e.g. strength, compacted volume).

Before construction works start, the Contractor must provide to the Engineer plan of the location, distance and alignment of the injection sites.

In the case of compaction grouting, the pressure and volume of the mortar to be pressed must be tested by setting up test areas and determining the distance from the corresponding injection site.

The pile manufacture documentation must be forwarded to the Engineer per working day.

Structural and lifting tests may be required to preserve evidence of where jet injection and injection compaction are used.

In addition to the piles, additional tests are required. The Contractor shall propose testing plan for the Engineer’s approval to demonstrate the integrity of each pile.

The Contractor shall for all his concrete works submit for the Engineer’s approval concrete mix designs where, beside its structural properties, special attention will be brought to concrete corrosion, frost resistance and durability. The Contractor’s batching plant(s) shall be subject the Engineer’s approval. This approval will depend on the batching plant’s equipment, personnel, general and specific experience.

A constant supply of materials for concrete works which will provide a high quality finish of the same shade shall be sought by the Contractor and approved by the Engineer.

### Slips, Falls and Excess Excavation

Every precaution shall be taken by the Contractor to prevent slips and falls of earth and other material in the excavations. In the event of slips or falls occurring or in the event of excavation being made in excess of the minimum necessary or practicable for the construction of the Works the voids so formed shall be filled. In all cases where the voids so formed when backfilled would provide support for the permanent Works or adjacent structures and services then such voids shall be filled solid with Concrete Class C8/10 at the Contractor's expense. In all other cases the voids shall be packed with selected excavated material or approved fill material and thoroughly compacted to the Engineer's approval.

In the event of any trench for pipelines exceeding the maximum allowable widths as specified or shown on the Drawings, the Engineer will order the restoration of the trench width or the use of an alternative bedding material or such other remedial action as in his opinion is necessary. The Contractor shall then carry out the measures so ordered by the Engineer and shall have no claim against the Employer for any additional costs resulting from such instructions.

### Excavation to be Kept Free from Water

The Contractor shall keep excavations free from water and wastewater, whether caused by ground water, tides, floods, storms or otherwise, so that the Works shall be constructed in dry conditions. The Contractor shall keep the sub-soil or accumulated water or wastewater at a level lower than the bottom of the Permanent Works for such a period as the Engineer shall direct.

In the event of the Contractor requiring drainage pipes, channels or subdrains the Engineer may permit these to be constructed below the level of and within the width limits of the permanent Works, provided the Engineer has approved the details of the Contractor’s proposals. No sub-drainage pipes shall be left in, unless they are filled with Concrete Class C8/10 or other approved material. Any sub-drainage that the Contractor constructs below the Permanent Works shall if left in place provide support at least equal to that which would have been available if the sub-drain was not present.

No water shall be discharged into any watercourse or sewer without the Contractor having first obtained all necessary consents and the permission in writing of the Engineer. Such permission shall not be granted unless the Contractor shall have provided to the satisfaction of the Engineer an efficient settling basin or sand trap through which all such water shall pass before discharge into the said watercourse or sewer.

### Embankments and Site Grading

The material used in the formation of embankments and bunds and in filling low areas of the site shall be either selected or general fill.

The areas where selected fill is to be used are specified herein. Selected fill shall be used in the formation of the bases (where applicable) and beneath roads. The fill in all other embankments shall be general fill.

The fill materials shall be obtained from excavations or be similar material obtained by the Contractor from sources approved by the Engineer.

In areas where raft foundations are to be constructed the selected fill shall be placed and compacted to 300 mm above the underside of any blinding concrete and then removed by machine and hand to leave no scarred surface just before the concrete is placed.

Special measures must be taken in compacting material laid immediately adjacent to a structure to ensure that the material is well compacted. Hand operated vibrating plate compactors, vibro-tampers or power rammers are to be used. In other cases, compaction shall be carried out by vibrating compactors, smooth wheel or pneumatic tyre rollers of types approved by the Engineer.

In trimming and forming bunds and embankments the Contractor shall make allowance in the height and width of these for consolidation and shrinkage. The dimensions of bunds and embankments shall be to the profiles shown on the Drawings with any necessary allowance being made for the surface finish.

The Contractor is obliged to examine the material for the construction of the embankment.

When testing soils for their suitability for embankments, materials from every cut and borrow pit shall be tested, and at every change of material. Tests shall be performed on at least two samples for every type of material.

The determination of content of organic and combustible matter, as well as changes in soil volume shall be resorted to only in specific cases (suspicious materials).

Every layer of embankment shall be compacted in full width with an appropriate mechanical device, while tamping, as a rule, from the edge toward the centre. All places inaccessible for machines, or places where the use of heavy tamping devices would be unsuitable for other reasons (filling behind structures, retaining walls, etc.) shall be tamped with other suitable devices or methods, the use of which shall be subject to the approval by the Engineer.

Every layer of embankment shall be wetted or dried to optimum moisture in compliance with preliminary tests, using the type of material that can be tamped to the required degree of compaction. If after tamping and quality control, the filling of the next layer is not undertaken immediately, but after a longer period, under different weather conditions, before filling it is necessary to re-check the quality of compaction. In such case, the works may start only when the test proves, once again, the quality of compaction.

Filling shall be carried out so that layers are, longitudinally, as horizontal as possible, and to avoid any sudden changes in height between layers of different height, constructing them at a gradient that could still allow a proper compaction work.

The filling works shall be stopped at any time when it is impossible to achieve satisfactory results, particularly because of rain, high groundwater, or some other atmospheric disasters.

The filling material is not incorporated on icy surfaces, nor on snow and ice.

Quality Control for Incorporation of materials

- Standards for Control of Quality of Materials

- SRPS EN ISO 22475-1 – Sampling

- SRPS CEN ISO/TS 17892-1– Determination of soil moisture

Scope of Regular Control Tests

The moisture of material shall be tested daily. The construction of the next layer may not start until the required quality of the previous layer has been proven and approved by the Engineer.

If, in control tests, the Engineer determines major variation of results from the specified values, he may subsequently change the scope of testing. In agreement with the Engineer, the quality of incorporated layers may also be determined applying other accepted methods. In that case, the criteria of quality for incorporation shall be stated, along with the method and scope of testing, in agreement with the Engineer.

Acceptance of Incorporated Material

Every layer of embankment shall be subject to approval by the Engineer as specified under Quality Control of Incorporated Material, in compliance with specified criteria.

Replacement of Removed Soil of Insufficient Bearing Capacity

Replacement of removed soil of insufficient bearing capacity with a layer of non-cohesive soil. For the permanent stability of embankment, the material below the future embankment shall be replaced to the designed depth.

Materials

Material shall be in compliance with the intended use and meet the requirements set in SRPS EN ISO 17892-4, SRPS EN 1367-2 and other applicable standards.

Execution of Works

The excavation and transport of material shall be performed mechanically, and transported to a specifically designated landfill. Further works on the construction of embankment shall be executed using materials in accordance with Technical Specifications by Roads of Serbia.

This section of embankment shall be constructed in a layer of 0.50 m of length, free from the presence of water in excavations (if present, it shall be removed).

All design, materials and construction method statements should be submitted for the approval to the Engineer.

### Stripping of Topsoil

Where ordered by the Engineer topsoil shall be stripped from the whole or part of the Site to a depth of 250 mm or to such other depths as indicated in the Contract or such other depths and over such areas as the Engineer may direct, and set aside for re-use as a separate operation prior to any further excavation which may be required.

Topsoil shall include any surface material capable of supporting vegetation and suitable for use in soiling areas to be grassed or cultivated.

The Contractor shall not dispose of surplus topsoil without the written permission of the Engineer.

### Trial Holes

The Contractor shall excavate any trial holes he may require to determine the position of underground services, sub-soil drains or for any other reason.

The Contractor shall arrange for the refilling and reinstatement of trial holes to be carried out immediately the required information is obtained. The reinstatement of the surfaces of trial holes shall be carried out to the approval of the Engineer.

### Inspection by the Engineer

When the specified levels or limits of any excavation are reached, the Engineer will inspect the ground exposed and if he considers that any part of the ground is by its nature unsuitable he may direct the Contractor to excavate further. Such further excavation shall be refilled to the specified levels or limits with concrete, selected excavated material or selected imported material.

Should the material forming the bottom or sides of any excavation, while acceptable to the Engineer at the time of inspection, subsequently become unacceptable due to exposure to weather conditions or due to groundwater, flooding or have become puddled, soft or loose during the progress of the Works, the Contractor shall by approved methods remove such damaged, softened or loosened material and excavate further to a sound surface. Such further excavation shall be held to be Excess Excavation and material emanating therefrom shall be removed from the Site.

### Crossing Watercourses

Where the excavation crosses streams, ditches, culverts and other watercourses the Contractor shall be deemed to have allowed for all the additional measures necessary for the proper construction of the Works at these crossings including maintaining the full flow of water.

## Structures and Pipelines

### Dewatering

Unless otherwise specified, the Contractor shall keep the excavation clear of water during construction and, in the case structures being constructed in groundwater, for such further period as may be necessary to avoid the submergence of concrete.

It shall be considered whether the adopted dewatering scheme allows the sides of the excavation to remain stable at all times and that excessive heave or rupture of the base does not occur. Furthermore, care should be taken to prevent that the return of the groundwater results in collapse of soils having a sensitive structure, e.g. loose sand.

The method of keeping excavation clear of water, dewatering and disposal of water, shall be subject to the approval of the Engineer.

Where a structure is subject to uplift, the Contractor shall reduce the ground water pressures so that the structure is stable for the whole period of the construction.

The Contractor shall ensure that sufficient stand-by plant is available on Site at all times to avoid any interruption to continuous dewatering.

### Excavation

Excavation shall be carried out to such dimensions as will permit adequate dewatering, proper support of the sides of the excavation, the erection of shuttering, placing of concrete and fill including compaction and any other constructing operation.

Special care shall be taken not to disturb the formation level of any structural excavation.

The excavated material, classified by an accredited laboratory as satisfactory soil material for subsequent filling and backfilling, shall be stored in the designated place. Supplies should be placed, sorted, shaped to allow for proper water drainage, and stored in a manner to prevent contamination and segregation.

Note: During the earthwork’s execution, the Current Geotechnical Supervision and Current Quality Control of the performed works has to be carried out by the Accredited Soil-mechanical Laboratory, which the Contractor is obliged to provide with the aim of regular inspection of the excavation and implementation of adequate quality control of the excavated material. If, in the excavation during the works, material that does not correspond to the geotechnical profile of the terrain shown in the Geotechnical elaborate, is found, it is necessary to carry out immediate additional consultations with the Engineer.

### Tests on Groundwater

During the course of the work the Engineer will require samples of the groundwater to be taken for testing to ascertain the presence of harmful substances.

### Tests on Formation Level

On reaching the level for hand trimming as specified herein, the Engineer may order either in situ or other tests as specified to determine the nature and bearing capacity and deformation properties of the soil strata.

### Disposal of Surplus Excavated Material

The Contractor shall be responsible for negotiating and securing suitable areas for disposal of surplus excavated materials and shall pay any fees or other payments associated with such disposal. These shall be included in his rates and prices.

In connection with the disposal of excess spoils, the Contractor shall be responsible for the following during the Contract period:

- Upgrading the strength and the quality of the existing access road(s) and maintaining the same in good order and final reinstatement.

- Dewatering of the tipping area(s) by means of porous concrete pipes laid at the bottom of the valleys or as agreed with the Engineer.

- Unloading, spreading, levelling, and placing the soil into embankments etc. as necessary, in order to keep the top in good, safe and manageable order.

- Keeping third parties from using the tipping area(s). No claims will be entertained by the Engineer for any extra work associated with dealing with soil deposited by others or request for additional tipping area, should the existing become saturated due to the use by others.

- Keeping vehicles clean when leaving the tipping area(s) and to ensure they do not contaminate public roads.

### Over-Excavation

Any extra excavation beyond the limits specified or ordered shall be filled by the Contractor at his own expense with Concrete Class C8/10 or with approved fill material thoroughly compacted if the Engineer so directs.

### Excavation for Pipes

The formation of excavation for pipes shall be finally trimmed by hand, or such other method as may be approved or ordered by the Engineer, immediately prior to the laying of pipes.

The formation shall be excavated and backfilled as specified so that the barrel of each and every pipe shall be supported evenly throughout its length, except as necessary for proper joint holes which shall be excavated under every socket or collar to such depth that the socket or collar shall not touch the bottom of the hole.

Table 5: Minimum trench width in relation to the nominal pipe diameter DN

| DN (mm) | Minimum trench width (OD + X) in meters |  |  |
| --- | --- | --- | --- |
|  | Trench with shoring | Trench without shoring β ˃ 60° | Trench without shoring β ˂= 60° |
| ˂= 225 | OD + 0.40 | OD + 0.40 | OD + 0.40 |
| ˃ 225 to ˂= 350 | OD + 0.50 | OD + 0.50 | OD + 0.40 |
| ˃ 350 to ˂= 700 | OD + 0.70 | OD + 0.70 | OD + 0.40 |
| ˃ 700 to ˂= 1200 | OD + 0.85 | OD + 0.85 | OD + 0.40 |
| ˃ 1200 | OD + 1.00 | OD + 1.00 | OD + 0.40 |

With the details OD + x, x/2 corresponds to the minimum work space between pipe and trench wall respectively trench shoring;

OD – outside diameter of pipe, in m;

β – is angle of slope of the unsupported trench measured to the horizontal

Table 6: Minimum trench width dependent on trench depth

| Trench depth (m) | Minimum trench width (m) |
| --- | --- |
| ˂ 1.00 | No minimum trench width laid down |
| ≥ 1.00 to ≤ 1.75 | 0.80 |
| ˃ 1.75 to ≤ 4.00 | 0.90 |
| ˃ 4.00 | 1.00 |

### Hand Trimming at Formation Level

Where the formation level of any excavation is to receive concrete or compacted fill, the final 0.15 meters of the excavation shall be trimmed by hand, or by such other method as may be approved or ordered by the Engineer, after removal of any slurry and loose material and immediately before placing the concrete or fill.

The formation level shall be carefully levelled or shaped as required. The Contractor shall report to the Engineer when excavations are ready to receive pipes or concrete foundations and shall not proceed with pipe laying, concreting or other works until they have been passed and approved by the Engineer. Any pipe laying, concreting or other work carried out without prior approval of the Engineer shall be removed immediately at the Contractor's expense.

### Filling to not Endanger Structures

The Contractor shall arrange the timing and rate of placing of backfilling or of filling to structures in such a way that no part of the Works is over stressed, weakened, damaged or endangered. The layers of material shall be so placed as to maintain adequate drainage and to prevent accumulation of water. In particular, the placing of material around concrete structures shall commence only after they have been completed and have attained their full specified strength. The material shall be placed so as to exert a uniform pressure around the structures.

Regardless of the method of backfilling adopted, the Contractor shall ensure that backfilling to excavations is carried out to the satisfaction of the Engineer. The Contractor shall take all necessary precautions to ensure that no damage is caused to the Permanent Works or to adjacent structures.

### Selection and Compaction of Backfill

Where backfilling below ground level and adjacent to structures is required, the material to be used shall be carefully selected and compacted according to the Specification.

No backfilling work shall be carried out until it has been approved by the Engineer. Where backfilling is to be placed on two or more sides of the structure, it shall be placed simultaneously on the opposite sides so that the difference in level never exceeds 0.30 m, or as otherwise instructed. The difference in level of backfilling on either side of pipes shall not exceed a maximum of 0.20 m. Backfilling to structures shall generally be carried out as soon as practicable.

Excavation for pipelines on land shall receive a layer of approved pipe bedding material of depth in the pipe trench proportional to the pipe diameter in accordance with the following:

- 1/4 × outside diameter of the pipe, in good ground.

- 1/3 × outside diameter of the pipe, in poor ground.

- Minimum 200 mm beneath the barrel and socket.

Granular bed for pipes shall be formed by spreading and compacting material over the full width of the trench. Sufficient granular material shall be provided to allow the pipes to be worked into the granular material and firmly supported to true line and level. Sufficient space shall be left to enable the joints to be made, and inspected, and the Contractor shall ensure that at least three quarters of each pipe length is fully supported. After the pipeline has been approved by the Engineer the trench shall be carefully filled with granular material.

For rigid pipes (e.g. ductile iron, concrete), the filling shall be carried out as follows:

- Pipe bedding material well compacted up to the level of the horizontal diameter of the pipe;

- Selected granular fill well compacted up to the crown of the pipe;

- Selected fill lightly compacted by hand up to 300mm above the crown of the pipe.

Filling shall be carried out generally in layers not exceeding 150 mm thick, by a method approved by the Engineer.

For flexible pipes (e.g. steel, GRP, PVC, polyethylene, etc.) the filling with approved granular material shall be up to 300 mm above the crown of the pipe. This filling shall be carefully and well compacted in layers not exceeding 150 mm thick by a method approved by the Engineer to avoid disturbing either the pipes or the joints.

The remainder of the trench shall be backfilled with approved selected backfill material as per the Specification.

### Filling of Excavations beneath Roads

Excavations for pipelines laid under site roads and public roads shall be backfilled above the pipe fill surround with selected gravel or crushed stone road base material, as specified in Paragraph “Mechanically Stabilized Underlying Load-Bearing – Subbase Layer”

Filling shall be built up evenly over the full width and compacted in layers not exceeding 200 mm in depth at the optimum moisture content. The moisture content of backfill material may require adjustment to that required to attain maximum density. Backfill material, which contains insufficient moisture to obtain the desired compaction, will require the incorporation of additional water by the use of approved sprinklers and mixing before laying.

Layers more than 300 mm below road formation shall be compacted to 90% of the maximum dry density determined according to Proctor test, according with relevant standard. Layers less than 300 mm below road formation level shall be compacted to 95% of the maximum dry density determined according to the aforementioned standard methods.

The Contractor shall ensure that the backfill material lay immediately adjacent to a structure concrete wall or thrust block is well compacted. Hand operated vibrating plate compactors vibro-tampers or power rammers shall be used. In other cases, compaction shall be carried out by vibrating compactors, smooth wheel or pneumatic tyre rollers of types approved by the Engineer.

Excavations for pipelines laid otherwise or for other structures beneath the carriageways where mechanical compaction cannot be applied due to narrow space shall be backfilled with lean mix concrete. This concrete shall comprise proportions by weight of:

- 1 part of cement

- 3 parts of sand

- 6 parts of aggregate with a maximum size of 40 mm.

The concrete and its placing shall otherwise conform to the Specification, Paragraph “Concrete”.

### Reinstatement of Public Highways

Reinstatement of public highways shall be carried out as soon as is practical after completion of the Permanent Works and before the section of the road or pavement is re-opened for public use.

The types and thicknesses of the materials used in the road reinstatement shall be, as a minimum, as those of the existing construction or as otherwise instructed by the Engineer, to suit the requirements of the Authorities.

Reinstatement where not specifically required by the Authorities shall comprise an additional depth of sub-base material as instructed by the Engineer. Original surface materials may be placed by hand with the wearing course upper most. The method of placing and compacting of materials shall be similar to that for road base construction, to the same surface tolerance, and to suit levels of the surrounding undisturbed road or pavement.

Only materials approved by the Engineer shall be used for making good any defects.

### Levelling of Areas

Areas around or on top of structures shall be levelled to the required levels as indicated on the drawings or instructed by the Engineer. The Contractor shall the due precautions to prevent any damage to the structures during the levelling. The levelling of areas around structures shall be carried out by approved methods. Any damaged item shall be replaced or repaired at the Contractor's expense and to the satisfaction of the Engineer.

## Sheeting and Bracing

The Contractor shall be responsible for the design, installation, maintenance during construction, and where appropriate, removal of all support Works needed for trenches and other excavations. The Contractor shall submit to the Engineer for approval, details of his proposal for excavation support which details shall include such drawings, calculations or other explanatory matter as the Engineer may require, but such approval shall not relieve the Contractor of his responsibilities under the Contact. No excavation work may proceed until the Engineer's approval has been given to the Contractors proposals.

The Contractor shall not remove temporary Works supporting the excavations until in the opinion of the Engineer the Permanent Work is sufficiently advanced to permit such removal, which shall be executed under the personal supervision of a competent foreman.

Where the removal of excavation support Works is considered by the Engineer to endanger existing structures thus making them liable to subsidence damage, the Contractor shall leave such support Works in place, removing only the minimum necessary to allow the reinstatement of the surfaces.

## Additional Site Investigation

### General

The Contractor shall ascertain the subsoil conditions at the Site by undertaking a programme of Additional Site Investigation (Design Investigation). This programme shall comprise a suitable combination of routine investigation methods including in situ tests, borings, laboratory tests, and reporting. The methods shall involve generally available commercial tests performed according to generally accepted or standardised procedures.

In case investigations of a more specialised nature are required, these shall be undertaken where necessary, and test procedures and test interpretations shall be given.

Laboratory tests shall be carried out in a laboratory approved by the Engineer.

The geotechnical investigations shall provide all data concerning the ground and the ground water conditions at and around the construction site necessary for a proper description of the essential ground properties and a reliable assessment of the characteristic values of the ground parameter values to be used in design calculations.

The following items should be considered for inclusion in the design investigation of the relevant ground:

- Geological stratigraphy

- Strength properties of all relevant ground

- Deformation properties of all relevant ground

- Pore pressure distribution through the ground profile

- Permeability conditions

- Possible instability of subsoil

- Compaction properties of the ground

- Possible aggressiveness of the ground and the ground water

- Possibility of ground improvement

- Frost susceptibility

Should the Engineer consider that the investigations undertaken by the Contractor remain insufficient for detailed design of any part of the Works, the Contractor shall undertake further work, and/or employ a specialist Site Investigation firm as instructed by the Engineer.

Repetition of the tests due to unsatisfactory results shall be at the expense of the Contractor.

The fieldwork to be carried out by the Contractor may comprise but need not be limited to or exclude other field works:

- Vertical test borings

- Sampling and laboratory tests

- Penetration tests (SPT and/or CPT)

- Vertical plate load tests

- Permeability tests

- Groundwater table and ground water quality determination

The site investigation work shall be carried out using modern methods and equipment and by fully competent staff under the supervision of a qualified Engineer.

The equipment employed shall be such as to provide the necessary data.

### Soil Investigation Report

The Contractor shall submit to the Engineer a Soils Investigation Report incorporating a record of all the investigation work carried out by him. The Report shall include boring logs, records of field and laboratory tests, records of water level observations and recommendations as to the bearing capacity and deformation properties of the soil and water inflow. Laboratory tests shall be carried out in a laboratory approved by the Engineer.

### Design of Structures

The Contractor shall use the data in the documents and the results of the Additional Site Investigations to design in detail every aspect of the Works, permanent or temporary, that is affected by the subsoil.  Notwithstanding requirements outlined in this section the design shall be entirely the Contractors’ responsibility to the approval by the Engineer.

### Limit States

For spread foundations (1), retaining structures (2), embankments and slopes (3) a list of Limit States to be considered shall be compiled. The following limit states shall be considered:

- Loss of overall stability (1,2,3)

- Combined failure in ground and in structure/structural element (1,2)

- Bearing resistance failure (1)

- Excessive settlements (1)

- Excessive heave (1)

- Unacceptable vibrations (1)

- Failure by sliding (1)

- Structural failure due to foundation movement (1)

- Failure of a structural element such as a wall, anchor, wale or strut or failure of the connection between such elements (2)

- Movements of the retaining structure which may cause collapse or affect the appearance or efficient use of the structure, nearby structures or services which rely on it (2)

- Unacceptable leakage through or beneath the wall (2)

- Unacceptable transport of soil grains through or beneath the wall (2)

- Unacceptable change to the flow of groundwater (2)

- Failure due to internal erosion (3)

- Failure due to surface erosion or scour (3)

- Failure due to hydraulic uplift (3)

- Deformations (including those due to creep) of the embankment or slope and their foundations which cause structural damage, loss of serviceability or failure in adjacent structures, roads or services (3)

- Deformations of the embankment or slope, including those of creep, which cause loss of serviceability (3)

- Surface erosion (3)

Within the Serviceability Limit State (SLS) for shallow foundations, the progress of settlements through the various construction stages and throughout the specified lifetime of the structures shall be investigated. The Contractors design shall verify acceptable deformations at all stages and throughout the design lifetime of the project.

Retaining walls shall be designed to limit deformations at all stages of construction, and if permanent throughout the design lifetime of the project. Where retaining structures are in the immediate proximity of buildings, structures, roads, pipelines or utilities they shall be braced and dimensioned to sustain the different horizontal pressure resulting from vertical and possible horizontal loads.

### Durability

In geotechnical design the internal and external environmental conditions shall be estimated at the design stage to assess their significance in relation to durability and to enable provisions to be made for the protection or adequate resistance of the materials (see paragraph “Earthworks and Foundations”).

### Ground Treatment

Any ground treatment proposed by the Contractor to improve the bearing capacity and/or settlement characteristics of the soil must be supported by a full method statement and design calculations with a statement of the minimum performance to be achieved. Where directed by the Engineer the Contractor shall carry out a field trial of the proposed treatment to demonstrate that it meets the stated performance criteria.

### Geotechnical Design Report

The Contractor shall establish a set of geotechnical design parameters, which take into account the volume of soil involved in the particular analysis.

As a part of the Contractor’s design the assumptions, data, calculations and results of the verification of safety and serviceability shall be recorded in a Geotechnical Design Report.

The Geotechnical Design Report shall include a plan of supervision and monitoring, as appropriate. Items that require checking during construction shall be clearly identified in the report. When the required checks have been carried out during construction, they shall be recorded in an addendum to the report. An extract of the Geotechnical Design Report containing the supervision, monitoring and maintenance requirements for the completed structure shall be provided to the Employer.

# CONCRETE

## General Requirements

The Contractor shall carry out the works described in accordance with the appropriate standards and requirements of this Tender Dossier.

All the items of concrete and reinforced concrete works have to be executed professionally and have to be of top-quality, by qualified manpower, adequate machinery, tools and materials that completely comply with technical rules and regulations, norms and applicable standards relevant for this type of works.

## Standards

The Contractor shall carry out the works described in accordance with the appropriate standards or equivalent national or international standards and including “Rulebook for building structures with Annex 1 and Annex 2 (“Official Gazette of RS”, No. 89/2019, 52/2020, 122/2020)” and “Rulebook on Technical Standards for Concrete and Reinforced Concrete” (PBAB 87).

The main standards are as follows (but shall not be limited to):

- SRPS EN 1992 	Eurocode 2: Design of concrete structures

- SRPS EN 13670 	Execution of concrete structures

Other standards are listed in the following sections of General Technical Specifications.

### Production control

Concrete plant must have required production capacity, as well as the agreed size of the aggregate storage and silos, and in addition, it shall meet following standards, but shall not be limited to:

- SRPS EN 206	Concrete - Specification, performance, production and conformity

- SRPS.U.M1.206	Concrete - Specification, performance, production and conformity – Rules for the implementation of SRPS EN 206

The concrete plant must be equipped for the concrete production under special conditions, i.e. when air temperature is lower than +5°C, i.e. higher than +30°C.

Method Statements must specify the distance of the concrete plant from certain parts of the building, the number of mixer trucks available to the plant, as well as the duration of the transport, taking into account the traffic congestion on the road if it uses public roads. The concrete plant must have a report on the suitability of the concrete plant production and a report on the one-month test of the dosing device.

Production control according to the Method Statements shall be done by:

- Testing of concrete components - materials

- Testing of fresh concrete and

- Testing of hardened concrete.

Test methods and frequency are defined in standard SRPS EN 206 and should be detailed in Method Statements.

### Classes of Concrete Strength

The classes of concrete strength to be used in the works are the following:

All types of concrete must be designed in compliance with the relevant standards and Rulebook on Technical Standards for Concrete and Reinforced Concrete (PBAB 87). For concrete exposed to effect of aggressive environment, provisions of the Rulebook on Technical Standards for Concrete and Reinforced Concrete in Structures Exposed to Aggressive Effect of Environment shall be applied.

Concrete classes in compliance with PBAB 87, shall correspond to the following classes of hardness defined by SRPS EN 206-1:

- MB10 - C8/10

- MB15 - C12/15

- MB20 - C16/20

- MB25 - C20/25

- MB30 - C25/30

- MB35 - C30/37

- MB45 - C35/45

- MB55 - C45/55

### Properties of concrete in special environmental conditions

The prerequisite for the production of concrete with special properties is that such concrete must be mixed, prepared and installed correctly (well compacted and without segregation) and carefully cured. It must be made in accordance with the relevant conditions for concrete B.II

#### Watertight concrete

Testing of concrete for watertightness shall be conducted in accordance with SRPS U.M1.015 standard SRPS EN 12390-8 (Testing hardened concrete - Part 8: Depth of penetration of water under pressure). Concrete waterthightness grades shall be determined by the design documentation, i.e. structural design (V-I, V-II, V-III, and V-IV).  The appearance of drops on the upper surface must not be observed on five of the six tested bodies for the required grade, but with the fact that the first lower watertightness grade is satisfied by all six bodies.

#### Freeze-resistant concrete

For concrete that is exposed to frequent freezing and thawing in moisture-saturated conditions, frost-resistant aggregate and watertight concrete are required, all in accordance with the standard SRPS U.M1.206, Appendix R (Concrete — Specification, performance, production and conformity – Rules for the implementation of SRPS EN 206-1). The frost resistance test determines the frost resistance grades of M50, M100, M150 and M200, where the numbers indicate the highest number of cycles of alternating freezing and thawing.

Testing of concrete for freeze resistant shall be conducted in accordance with standard SRPS CEN/TS 12390-9- Testing hardened concrete - Part 9: Freeze-thaw resistance with de-icing salts - Scaling

The compressive strength of the body must be 75% of the strength, of unfrozen bodies of equivalent age.

The structural design shall define the freeze-resistant concrete.

#### Freeze-resistant and sulphate-resistant concrete

The structural design shall define, based on the exposure, which concretes have to be freeze- and sulphate-resistant. The concrete resistance shall be tested in accordance with the standard SRPS U.M1.206, Appendix O (Concrete — Specification, performance, production and conformity – Rules for the implementation of SRPS EN 206-1).

Testing the concrete surface resistance to frost and de-icing salt shall be determined by the degree of damage to the tested surface after 56 cycles of alternating freezing and thawing. The amount of exfoliated material in mg/mm2 is measured. Concrete exposed to frost or frost and salt must be protected by aeration.

#### Wear-resistant concrete

For concretes exposed to heavy-duty traffic or rapid water flow, based on the structural design, there will be certain requirements for their resistance to wear. The concrete wear test shall be carried out according to the standard SRPS B.B8.015 (Wear test - Grinding wheel method).

Тhe Concrete pavements (exposed to heavy-duty traffic ) shall be carried out according to the standard SRPS EN 13863-4:2013- Concrete pavements - Part 4: Test methods for the determination of wear resistance of concrete pavements to studded tyres.

#### Resistance of concrete to chloride migration

Testing for resistance of concrete to chloride migration shall be conducted in accordance with SRPS EN 12390-18- Testing hardened concrete - Part 18: Determination of the chloride migration coefficient.

Calcium chloride and chloride-based chemical admixtures shall not be added to concrete containing steel reinforcement, prestressing steel, or other embedded metal.

### Aggregates

The main standards are as follows (but shall not be limited to):

| - SRPS EN 1367 | Tests for thermal and weathering properties of aggregates |
| --- | --- |
| - SRPS EN 1744 | Tests for chemical properties of aggregates |
| - SRPS EN 932 | Tests for general properties of aggregates |
| - SRPS EN 933 | Tests for geometrical properties of aggregates |
| - SRPS EN 12620 | Aggregates for concrete |
| - SRPS EN 1097 | Tests for mechanical and physical properties of aggregates |

For concrete fabrication, the aggregate shall be used that meets the quality requirements according to the relevant standards.

Control of aggregate at the site shall be exercised in compliance with the relevant standard.

Granulometric composition of aggregate mixture for concrete shall be established on the basis of quality requirements, method of transportation and placing, as well as of other factors that may have impact on the quality of concrete. It is recommended to have the grading of aggregate mixture within the limits given in the standard.

The size of the largest grain of aggregate must not exceed 1/4 of the smallest dimension of the cross section of a concrete element (1/3 in case of slabs), nor bigger than 1.25 of the clear horizontal spacing of the reinforcement profile.

### Water for Concrete

The main standard are as follows (but shall not be limited to):

- SRPS EN 1008		Mixing water for concrete - Specification for sampling, testing and assessing the suitability of water, including water recovered from processes in the concrete industry, as mixing water for concrete

Drinking water may be used without evidence of its suitability.

### Cement

Cement quality and testing shall be according to the following standards (but shall not be limited to):

- Rulebook on cement quality (Official gazette of RS 34/13 I 44/14)

- SRPS EN 197-1		Cement - Part 1: Composition, specifications and conformity criteria for common cements

- SRPS EN 197-2		Cement - Part 2: Assessment and verification of constancy of performance

- SRPS EN 196-1		Methods of testing cement - Part 1: Determination of strength

- SRPS EN 196-2		Method of testing cement - Part 2: Chemical analysis of cement

- SRPS EN 196-3		Methods of testing cement - Part 3: Determination of setting times and soundness

- SRPS EN 14216		Cement - Composition, specifications and conformity criteria for very low heat special cements

- SRPS EN 413-1		Masonry cement - Part 1: Composition, specifications and conformity criteria

- SRPS EN 413-2 		Masonry cement - Part 2: Test methods

### Concrete

Concrete quality and testing shall be according to the following standards (but shall not be limited to):

| - SRPS EN 206 | Concrete - Specification, performance, production and conformity |
| --- | --- |
| - SRPS U.M1.206 | Concrete — Specification, performance, production and conformity – Rules for the implementation of SRPS EN 206-1 |
| - DIN 4235 | Compacting of Concrete by Vibrating |
| - SRPS EN 12350 | Testing fresh concrete (Part 1 till Part 9) Part 1: Sampling and common apparatus Part 2: Slump test Part 3: Vebe test Part 4: Degree of compactability Part 5: Flow table test Part 6: Density Part 7: Air content - Pressure methods Part 8: Self-compacting concrete - Slump-flow test Part 9: Self-compacting concrete - V-funnel test |
| - SRPS EN 12390 | Testing hardened concrete (Part 1 till Part 18) Part 1: Shape, dimensions and other requirements for specimens and moulds Part 2: Making and curing specimens for strength tests Part 3: Compressive strength of test specimens Part 4: Compressive strength - Specification for testing machines Part 5: Flexural strength of test specimens Part 6: Tensile splitting strength of test specimens Part 7: Density of hardened concrete Part 8: Depth of penetration of water under pressure Part 9: Freeze-thaw resistance with de-icing salts – Scaling Part 10: Determination of the carbonation resistance of concrete at atmospheric levels of carbon dioxide Part 11: Determination of the chloride resistance of concrete, unidirectional diffusion Part 12: Determination of the carbonation resistance of concrete - Accelerated carbonation method Part 13: Determination of secant modulus of elasticity in compression Part 14: Semi-adiabatic method for the determination of heat released by concrete during its hardening Part 15: Adiabatic method for the determination of heat released by concrete during its hardening process Part 16: Determination of the shrinkage of concrete Part 17: Determination of creep of concrete in compression Part 18: Determination of the chloride migration coefficient |
| - SRPS EN 12504 | Testing concrete in structures (Part 1 till Part 4) |
| - SRPS EN 15304 | Determination of the freeze-thaw resistance of autoclaved aerated concrete |
| - SRPS EN ISO 15148 | Hygrothermal perfomance of building materials and products - Determination of water absorption coefficient by partial immersion |
| - SRPS EN ISO 12571 | Hygrothermal perfomance of building materials and products - Determination of hygroscopic sorption properties |

The Contractor shall make all necessary arrangements for the sampling and testing of fresh and hardened concrete in the extent and numbers of samples required.

### Concrete prefabricated elements

Prefabricated elements shall be in accordance with following standards (but shall not be limited to):

| - SRPS EN 1917 | Concrete manholes and inspection chambers, unreinforced, steel fiber and reinforced |
| --- | --- |
| - SRPS EN 13225 | Precast concrete products - Linear structural elements |
| - SRPS EN 14844 | Precast concrete products - Box culverts |
| - SRPS EN 13693 | Precast concrete products - Special roof elements |
| - SRPS EN 13747 | Precast concrete products - Floor plates for floor systems |
| - SRPS EN 14843 | Precast concrete products - Stairs |
| - SRPS EN 14991 | Precast concrete products - Foundation elements |
| - SRPS EN 14992 | Precast concrete products - Wall elements |
| - SRPS EN 1168 | Precast concrete products - Hollow core slabs |
| - SRPS EN 12794 | Precast concrete products - Foundation piles |
| - SRPS EN 12839 | Precast concrete products - Elements for fences |
| - SRPS EN 12843 | Precast concrete products - Masts and poles |
| - SRPS EN 13224 | Precast concrete products - Ribbed floor elements |
| - SRPS EN 1338 | Concrete paving blocks - Requirements and test methods |
| - SRPS EN 1339 | Concrete paving flags - Requirements and test methods |

### Concrete Repair

Repair of concrete shall be in accordance with following standards (but shall not be limited to):

| - SRPS EN 12618:1-3 | Products and systems for the protection and repair of concrete structures - Test methods |
| --- | --- |
| - SRPS EN 12636 | Products and systems for the protection and repair of concrete structures - Test methods - Determination of adhesion concrete to concrete |
| - SRPS EN 12637-1 | Products and systems for the protection and repair of concrete structures - Test methods - Compatibility of injection products - Part 1: Compatibility with concrete |
| - SRPS EN 12637-3 | Products and systems for the protection and repair of concrete structures - Test methods - Compatibility of injection products - Part 3: Effect of injection products on elastomers |
| - SRPS EN 1504 | Products and systems for concrete repair |
| - SRPS EN 1542 | Products and systems for the protection and repair of concrete structures - Test methods - Measurement of bond strength by pull-off |
| - SRPS EN 1799 | Products and systems for the protection and repair of concrete structures - Test methods - Tests to measure the suitability of structural bonding agents for application to concrete surface |
| - SRPS EN 1877 | Products and systems for the protection and repair of concrete structures - Test methods - Reactive functions related to epoxy resins |
| - SRPS EN 12190 | Products and systems for the protection and repair of concrete structures - Test methods - Determination of compressive strength of repair mortar |

### Admixtures / Additives

Admixtures/additives shall be in accordance with following standards (but shall not be limited to):

| - SRPS EN 934 | Admixtures for concrete, mortar and grout |
| --- | --- |
| - SRPS EN 480 | Admixtures for concrete, mortar and grout - Test methods |
| - SRPS EN 12878 | Pigments for the coloring of building materials based on cement and/or lime - Specifications and methods of test (for reinforced concrete only B category pigments) |

Chemical concrete additives must meet the quality requirements prescribed in the relevant standard. Prior to concrete fabrication using additives, it must be verified whether an additive corresponds to the designed concrete mixture according to the relevant standard.

### Fibres

Fibers shall be in accordance with following standards (but shall not be limited to):

- SRPS EN 14889-1	Fibres for concrete - Part 1: Steel fibres - Definitions, specifications and conformity

- SRPS EN 14889-2	Fibres for concrete - Part 2: Polymer fibres - Definitions, specifications and conformity

## Design Concrete Requirements

### Classes of Concrete

The different classes of concrete shall be used as follows:

- MB10 - C8/10	for plain concrete only for fill in trenches, for blinding and for screed.

- MB15 - C12/15	for plain and reinforced concrete for screed and encasements.

- MB20 - C16/20 	for mass concrete structures and sub-base.

- MB25 - C20/25	for normal reinforced concrete structures, pipeline protection, benching in manholes and chambers, roads, pavements, etc.

- MB35 - C30/37 	for watertight reinforced concrete in contact with water, wastewater, sludge, leachate, digester gas, for precast concrete structures and where especially directed by the Engineer.

- MB45 - C35/45 	for precast concrete structures.

- MB55 - C45/55 	for pre-stressed precast concrete structures.

### Crack Control under Working Load

Concrete structures shall be designed, reinforced and poured and cured to limit crack width under working load:

- The maximum allowed crack width is 0.1 mm in the service ability limit state (structures filled with water to maximum design water level and with soil back-filled if any. The ground water level and the pressure from the surrounding soil should in this state be stipulated with low values).

- The partial safety factor, f, for water pressure shall be 1.0 and for earth pressure 1.4 in this state.

- Where the external restraint factor R is greater than zero, a minimum amount of reinforcement for reduction of crack widths shall be placed.

- For concrete water or sludge tanks, the minimum concrete pressure zone either inside or outside face of the wall shall be 5 cm, or, if aggregate is used with a grain size >32 mm: max. aggregate grain size +2 cm.

- In order to incorporate the effects from thermal action, shrinkage and creep the Contractor should make the construction joints in accordance with the approved drawings. No other joints will be allowed. The Contractor shall make his structural documentation in accordance with this layout.

### Testing of Tanks

- Upon completion, on every tank, 4 benchmarks each shall be installed for slump osculation and zero survey shall be carried out. Benchmarks shall be installed on angles in case of rectangular tanks and at an angle of 90° on circular tanks.

- Upon completion, the tank shall be tested to determine water tightness. The tank shall be filled with potable water to the level of the top of the tank. Maximum rate of a filling for a water tank that is being filled for the first time: uniform rate of not greater than 2 m in 24 h. It is necessary to allow the tank to stabilize for minimum of three (3) days while the water is absorbed into the concrete.

- The liquid volume loss for a period of 24 hours shall not exceed 0.1 percent of the water volume / of the tank capacity. If the liquid volume loss exceeds this amount, it shall be considered excessive, and the tank shall be repaired and retested.

- Damp spots on the exterior wall surface or measurable leakage of water at the wall base shall not be permitted. Damp spots are defined as spots where moisture can be picked up on a dry hand. All such areas shall be repaired as necessary.

- Damp spots or standing water on the footing may occur upon tank filling and are permissible within the allowable volume loss. Measurable flow in this area is not permissible and must be corrected.

- When first filled, the liquid level should be maintained by the addition of further liquid for a stabilizing period while absorption and autogenous healing take place. The stabilizing period may be 7 days for a maximum design crack width of 0.1 mm.

- In the period during 7 days of testing, after complete filling of tanks, it shall also be necessary to make measurement of vertical displacements using surveying instruments at four points per tank (osculation) for the purpose of monitoring and comparing slumping’s with respect to the values envisaged by the design.

### Minimum Elements Thickness

For water (including wastewaters) or sludge retaining structures, concrete members (bottom slabs, walls) must have a minimum thickness of 30 cm.

## Organization of Concrete Production at the Site

At the commencement of the Contract shall submit for the approval of the Engineer a Method Statement detailing with regard to the requirements of this Specification his proposals for organisation of concreting activities at the Site.

The Method Statement shall include the following items:

- Plant proposed.

- Location and layout of concrete production facility.

- Proposed method of organization of the concrete production facility.

- Quality control procedures for concrete and concrete materials.

- Transport and placing of concrete.

- Details of formwork including striking times and procedure for temporary support of beams and slabs.

- Protection and curing.

The Contractor shall give notice to the Engineer before each concrete pour so that an inspection can be made before the concrete is placed.

## Ready Mixed Concrete

Concrete obtained from a single supplier of ready-mixed concrete may be used in the Works subject to the approval of the Engineer. Such approval will not be given until the Engineer is satisfied that the organisation and control of the manufacture and delivery of all ready-mixed concrete is in accordance with the requirements of this Specification.

Ready Mixed Concrete shall comply with SRPS EN 206-1.

## Materials and Testing

### General

The Contractor shall ensure that all materials conform to the National and EN standards.

Control of material components shall be carried out in accordance with relevant standards.

Once the Contractor has been given the written consent for the source, quality, mixing plant and supplier of the materials for concreting purposes, these shall be adhered to throughout the works.

The Contractor shall supply the Engineer with certificates showing compliance with the relevant standards.

All materials which are unidentifiable or do not comply with this specification shall be removed from the Site immediately at the Contractor’s expense.

### Cement

#### Type of Cement

The type of cement used in each of the various works shall be that specified herein and shall be from a single approved source or as otherwise ordered by the Engineer.

Portland cement shall be CEM I or CEM II, class CE 32.5, 42.5 or 52.5 in accordance to SRPS EN 197.

Sulphate-resisting cement shall be used for infrastructure works and structures exposed to wastewater and sludge as specified in SRPS EN 197.

The cement shall either be delivered in sealed bags marked with the manufacturer's name or in bulk consignments in a manner approved by the Engineer.

#### Tests of Cement

Regarding the tested properties, the cement should meet the criteria of Rulebook on cement quality (Official gazette of RS 34/13 I 44/14).

Cement must be certified in Serbia. Only cements that are certified in compliance with “Rulebook on cement quality” may be used.

Control of each delivery of cement at the site shall be exercised in compliance with the relevant standard. Samples of cement from each delivery shall be kept for 6 months.

The Contractor shall submit to the Engineer test certificates relating to each consignment of cement. Each certificate shall show that a sample of the consignment has been tested by the manufacturer or by an approved laboratory.

#### Delivery and Storage of Cement

All cement shall be delivered to the Site in properly and permanently marked, sound and sealed paper bags or other approved containers, unless written approval from the Engineer is obtained for the handling of cement in bulk.

Cement shall be delivered in quantities sufficient to ensure the proper progress of the Works and the quantities held in stock on Site shall be to the approval of the Engineer. Such approval shall not in any way relieve the Contractor of his responsibilities for providing cement. Cement from abroad, shall be packed in sealed plastic bags and placed inside paper bags.

Cement when being conveyed to the Site in lorries or other vehicles, shall be adequately protected from the weather and from contamination by dust, sand or any organic materials. Any cement which shall prove to have been exposed to damage by water will be rejected upon delivery.

All cement shall be stored in a weatherproof, waterproof and reasonably airtight building provided solely to that purpose. The floors of the building shall be raised at least 300 mm above the ground level to prevent the absorption of moisture.

Storage of cement in the open may be permitted on small Works on the written authority of the Engineer, in which case the cement shall be placed on a raised platform and amply protected by waterproof coverings to the approval of the Engineer. It is not permitted to store bags to a greater height than 2 meters. In the case of delivery of cement in bulk, the cement shall be stored in a properly designed silo. The silo shall be waterproof and must be provided with walls properly insulated against sunlight.

Where silos are used for the storage of cement each silo or compartment thereof shall be completely separate and fitted with a filter or an approved alternative method of dust control. Each filter for dust control system shall be of sufficient size to allow delivery of cement to be maintained to prevent undue emission of dust and to prevent interference with weighing accuracy by build-up of pressure. The Engineer shall be furnished with the means of identifying the several consignments of cement delivered. Each consignment of cement shall be stored separately so as to provide easy access for inspection and testing.

After they have been approved by the Engineer, consignments shall be used in the order in which they were delivered. No cement shall be taken from the storage unless it is needed for immediate use.

#### Cement Measured by Weight

All cement used in the Works shall be measured by weight. Cement from partly filled or unsealed bags shall not be used, unless otherwise approved by the Engineer.

#### Rejection of Cement

Notwithstanding the receipt of the test certificate required by paragraph “Tests of Cement” and the approval of the Engineer, the Engineer may reject any cement as a result of further tests. The Engineer may also reject cement which has deteriorated owing to inadequate protection or other causes or in any other case where the cement is not to his satisfaction. The Contractor shall remove all rejected cement from the Site without delay and at the Contractor’s expense.

### Quality of Water

For concrete fabrication, water shall be used that meets the relevant standard. Drinking water may be used without evidence of its suitability.

### Aggregate

#### Fine and Coarse Aggregates

Fine and coarse aggregates for concrete shall be obtained from sources approved by the Engineer. For concrete fabrication, aggregate shall be used that meets quality requirements according to the relevant standards.

Fine aggregates shall consist of natural sand unless otherwise approved.

Aggregates for all types of concrete shall be in accordance with the requirements of relevant standards. Aggregate shall be hard, strong and durable and shall contain no harmful material of sufficient quantity to affect adversely the strength or durability of the concrete or, in the case of reinforced concrete, to attack the reinforcement.

Control of aggregate at the site shall be exercised in compliance with the relevant standard.

The Contractor shall notify the Engineer of his proposals for complying with this requirement at the time of commencement of the Works.

#### Granulometric Composition of Aggregate

Granulometric composition of aggregate mixture for concrete shall be established based on quality requirements, method of transportation, and placing, as well as of other factors that may have impact on the quality of concrete. It is recommended for the granulometric composition of aggregate mixture to be within the limits given in the relevant standard.

The size of the biggest grain of aggregate must not exceed 1/4 of the smallest dimension of the cross section of concrete element (1/3 in case of slabs), not bigger than 1.25 of clear horizontal spacing of reinforcement profile.

The maximum size of aggregates required will not normally exceed 32 mm.

#### Storage of Aggregates

Each size of fine and coarse aggregate shall be stored in separate bins or on areas covered with steel plate, concrete other hard and clean surface, which shall be self-draining and protected from contamination by earth or other deleterious matter.

Fine and coarse aggregates shall be stored in such a way so as to avoid the two materials from becoming intermixed.

#### Tests on Aggregates

The Contractor shall submit to the Engineer samples of the fine and coarse aggregates proposed for use in the Works. Samples shall be of a size sufficient to carry out all preliminary test which the Engineer may order in addition to the specified tests of concrete.

Only aggregate that is certified in compliance with the “Rulebook on technical requirements for Fractional aggregate for concrete and asphalt” may be used.

### Delivery of Samples

Samples of cement, water and fine and coarse aggregates called for in the foregoing Paragraphs shall be delivered to the Engineer for testing by the Contractor before concreting is due to start, so that the necessary tests on the materials and the preliminary concrete cube tests specified in Paragraph “Preliminary mix Tests” can be completed before work is due to start.

### Admixtures for Concrete

Only additives that are certified in compliance with the “Rulebook on technical requirements for chemical admixtures for concrete, sprayed concrete, masonry mortar and grout for prestressing tendons” (OG RS 39/2019) may be used.

Chemical concrete additives must meet quality requirements prescribed in the relevant standards. Prior to concrete fabrication using additives, it must be verified whether the additive corresponds to the designed concrete mixture according to the relevant standards.

### Fibres

The convenience of the fibres for concrete shall be established by relevant standards.

## Mixing and Testing

### Concrete Classes

The classes of concrete to be used in the Works together with the 28 day characteristic strength, minimum cement content by weight, maximum water cement ratio by weight, and application of each class shall be in accordance with relevant standards and with requrements of this TD.

Appraisal of achieved concrete class by lots shall be made according to Art. 46 PBAB 87, and three-monthly verification of the class according to the relevant standard.

### Proportions of Materials

The proportions of cement, fine and coarse aggregates and water proposed by the Contractor for the use in the Works for each Class of concrete shall be approved by the Engineer as a result of satisfactory preliminary tests made in accordance with the Specification.

### Concrete Mix Design

The various classes of concrete shall be designed by the Contractor with particular attention to durability, strength, workability and surface finish and to satisfy the Engineer on these qualities. The content of all concrete shall be rigidly controlled and kept to the minimum required to obtain a workable concrete suitable for the nature of the work to be executed. The addition of proprietary admixtures intended to change the flow characteristics, cohesion or rate of setting needs approval by of the Engineer. No admixture shall contain more than trace levels of chloride ion.

No concrete shall be placed in the Works until the relevant mix has been approved by the Engineer. Approval will not be given to any concrete mix until it has been successfully subjected to Preliminary Mix Tests.

The Contractor shall carry out Preliminary Mix Tests as specified hereinafter in order to determine for each class of concrete the minimum practicable water/cement ratio and the required mix proportions of the fine and coarse aggregate the necessary allowance being made for the moisture content of the aggregate. After the value of the water/cement ratio and the mix proportions have been approved by the Engineer, Trial Mixes shall be carried out by the Contractor as specified hereinafter. The water/cement ratio and mix proportions which have been approved as a result of the Preliminary Mix Tests shall be used throughout the course of the Works. The Contractor shall ensure that cube crushing strengths satisfies the compliance requirements specified hereinafter.

In concrete made with sulphate resisting cement the maximum total content of chlorides (as chloride ions) shall not exceed 0.2% by weight of cement and the total acid soluble sulphates (as sulphate ions) shall not exceed 4.0% by weight of cement.

Further tests shall be carried out if any feature of materials or mixes is changed during the course of the work.

### Preliminary Mix Tests

The proportions of cement aggregate and water determined by the Contractor in his mix designs shall be used in preliminary mixes of concrete made in the presence of the Engineer and tested for strength, workability and surface finish under laboratory conditions observing the appropriate requirements of these Technical Requirements and to satisfy the Engineer on these qualities. Preliminary mixes shall be repeated with adjusted proportions as necessary until concrete mixes meeting the relevant requirements.

### Trial Mixes of Concrete

Trial mixes of concrete shall be prepared and tested at the site by the Contractor in this presence of the Engineer after Preliminary Mix Tests have been completed and when the Engineer has approved the Contractor’s mix design for each class of concrete. Trial mixes of concrete shall be mixed for the same time and handled by means of the same type of plant as the Contractor proposes to use in the Works. Sampling and testing of trial mixes shall be in accordance with these Technical Requirements.

Three separate batches of concrete shall be made for each class of concrete. Each batch shall comprise not less than 0.5 m3 of concrete, unless otherwise approved by the Engineer. Three cubes shall be made from each batch of concrete. The average strength of the nine cubes made for each class of concrete and tested after 28 days shall exceed the specified characteristic strength by at least margins mentioned in these Technical Requirements.

Unless otherwise approved by the Engineer the Contractor shall carry out practical tests on the site with

Trial molds. Trial molds shall be made for reinforced and plain concrete with dimensions typical of the Works. The formwork face to the trial molds for each class of concrete shall be designed to display all the relevant surface finishes intended for use in the Works and specified in these Technical Requirements. In making, transporting, placing, compacting and curing the Trial Mix concrete in the trial molds the Contractor shall observe all the relevant requirements of these Technical Requirements. When curing has been completed the trial molds shall be stripped and the concrete thus revealed shall be submitted for the approval of the Engineer.

When a proposed mix has been approved, no variation shall be made in the mix proportions, or in the type, size, grading zone or source of any of the constituents without the consent of the Engineer, who may require further trial mixes to be made.

Where the Contractor intends to purchase factory-made pre-cast concrete units, trial mixes may be dispensed with, provided that evidence is given to satisfy the Engineer that the factory regularly produces concrete which complies with these Technical Requirements. The evidence shall include details of mix proportions, water/ cement ratio, workability and strength obtained at 28 days.

### Concrete Testing

The Contractor shall make all necessary arrangements for the sampling and testing of fresh and hardened concrete in the extent and numbers of samples required by relevant standards and rulebooks.

Slump tests shall be carried out at such times and places as the Engineer may direct and shall be used as a guide to the consistency of each class of mix. The degree of slump will be decided by the Engineer following Trial Mix Tests and the figure given shall be adhered to thereafter.

Crushing tests shall be carried out on concrete cubes.

Prior to the commencement of construction of the Works concrete test cubes shall be taken and tested in accordance with the requirements of these Technical Requirements.

All cubes shall be marked at the time of casting, with the date, class of concrete and other necessary markings to identify the part of the Works, from which they are taken.

### Compliance Requirements for Concrete

The number of samples for control of fabrication and control of compliance with the requirements of the design at the point of placement is prescribed in Art. 41 and Art. 48 PBAB 87 respectively.

A concrete lot shall be accepted if the previously selected criterion has been met in compliance with Art. 46 PBAB 87. If that criterion has not been met, subsequent evidence of the quality of concrete must be requested.

Special properties of concrete (water tightness, resistance to effect of frost, resistance to effect of frost and defrosting salt and wear) shall be tested if that is prescribed by the program of control.

If sufficient number of samples has not been taken according to the PBAB 87 or if the quality of concrete is lower compared to the required one, concrete quality shall be subsequently established in the structure according to the relevant standard.

### Mixes Not Approved

A mixture in which quantities of component materials deviate from the limits prescribed in the relevant standard may not be accepted.

In the event that approval of a mix for any class of concrete is withdrawn for any reason the Contractor shall carry out such further trials and tests in order to achieve a satisfactory mix for that particular class of concrete.

### Additional Testing of Concrete

If the results for the compressive strength of the concrete used in the Works do not fulfil these Technical Requirements or if defects of workmanship during construction give rise to doubt as to the strength, durability and/or safety of the structure or of part thereof, supplementary testing may be required to be performed.

Concrete of water (including wastewater) or sludge retaining structures shall be tested non-destructively with a rebound tester (“Schmidt hammer”) according to the relevant standard. The Contractor shall supply and maintain such a device.

Concrete of any other structure shall be tested destructively by tests of concrete cores.

Concrete cores shall, where ordered by the Engineer, be drilled or cut perpendicular to the face of the hardened concrete and tested in accordance with relevant standard.

If the compressive strength of the cores, adjusted for height/diameter ratio and age, fails to attain the specified characteristic strengthen 28 days, the suspected part of the concrete shall be cut out, removed and replaced with concrete to the satisfaction of the Engineer at no extra cost.

### Water Content

A check on the moisture content of the aggregate shall be made before concreting is commenced. For the propose of assessing the amount of free water to be added at the mixer, the Contractor shall provide himself with a chart, a copy of which shall be given to the Engineer for approval, relating moisture content in the aggregate to water to be added at the mixer for all Classes of concrete in use.

The amount of water introduced into the mix shall be strictly controlled and shall be the minimum amount consistent with complete compaction. The device for measuring water shall show accurately the quantity and be so designed that the water supply will be automatically cut off while water is being discharged into the mix.

Consistency of concrete shall be controlled on the occasion of taking samples for evidence of compliance (minimum once a day for each type of concrete). The consistency of the concrete shall be determined in accordance with the relevant standard.

### Weigh Batching and Mixing

Volume batching is under no circumstances allowed, expect under the conditions mentioned in this Section.

Concrete shall be mixed to the approval of the Engineer.

All plant and equipment used for batching and mixing concrete and concrete materials shall be and shall be according to the relevant standard.

Materials for all classes of concrete shall be proportioned by weight in an approved weigh batch and shall be thoroughly mixed so as to ensure a uniform distribution of the materials throughout the concrete. The type of the mixer shall be in accordance with the maximum nominal size of the aggregate. The materials shall be mixed for a period and at a drum speed specified by the manufacturer of the mixer. Mechanical means shall be provided for recording the number of revolutions for each batch and automatically preventing the discharge of the mixer until the materials have been mixed for the specified minimum time.

The accuracy of such equipment shall be maintained within the tolerance specified by the manufacturer of the mixer.

Weigh batching machines shall provide facilities for the accurate control and measurement of the aggregates either singly or cumulatively and shall be capable of immediate adjustment by semi-skilled operators in order to permit variations to be made to the mix. All weigh dials shall be easily visible from the place at which filling and emptying of the hoppers is controlled.

Cement used in the production of concrete may be measured by making the size of each batch of concrete such as to require an integral number of complete bags or drums of cement. The maximum size of the batch shall not exceed the maximum rated capacity of the mixer as stated by the manufacturer and as stamped on the mixer.

Weight batching equipment shall be kept clean and maintained in good order. If any mixer is out of operation for more than 20 minutes is shall be thoroughly cleaned, together with all the handling plant, before any further mixing of concrete shall commence. Under no circumstances shall a batch of concrete be mixed with more than one type of cement.

The weights of the fine and coarse aggregates shall be adjusted as appropriate to allow either for free water contained in the aggregates or for aggregate absorption. The quantity of water which has to be added to each concrete mix shall as appropriate be either reduced by the amounts of free-water contained in the fine and coarse aggregates or increased to allow for aggregate absorption. The values of either free water content or of absorption for the fine and coarse aggregates shall be determined by the Contractor by a method approved by the Engineer immediately before mixing begins and at such further intervals as the Engineer may require.

Every concrete mixing machine shall be fitted with a device to measure added water by weight or volume and shall be so constructed that the water inlet and outlet valves are interlocked so that neither one of them can be opened unless the other is fully closed. The device shall be provided with an overflow with a cross-sectional area at least 4 times that of the inlet pipe and with its discharge point clear of the mixing plant. The entire water system shall be maintained free of leaks at all times and the measuring device shall be fitted with a drain pipe which allows the full quantity of water being measured to be drained off for checking the measurement. The outlet arrangement of the measuring device shall be such that between 5% and 10% of the water enters the mixer before the other materials and a further 5% to 10% of the water enters the mixer after the other materials. The remainder of the water shall be added at a uniform rate with the other materials. The water measuring device shall be readily adjustable so that the quantity of the water added to the mixer can, if necessary, be varied for each batch.

Any admixtures which may be used shall be measured separately in calibrated dispensers. The accuracy of calibration of any weighing plant, water measuring device and admixture dispenser shall be checked before carrying out trial mixes, before the first mixing of concrete for inclusion in the Works, after each service or adjustment to the mixing plant, and in any case at least once per month.

Before the commencement of concreting operations for any particular section of the Works, the Contractor shall satisfy the Engineer that sufficient plant is in working order, including adequate stand-by equipment, in order to ensure the proper mixing of the concrete required during the period of placing. The first batch of concrete materials placed in the mixer shall contain sufficient amount of excess cement, sand and water to coat the inside of the drum without reducing the required mortar content of the mix. Upon cessation of mixing for a considerable period, the mixer shall be thoroughly cleaned. Mixing for each batch shall continue until there is uniform distribution of the materials and uniformity of color and consistency of the concrete. Admixtures for which approval in writing has been given by the Engineer shall be introduced into the concrete by means of automatic dosing equipment. Such equipment shall feed a fixed quantity of admixture into the mixing water before the latter is discharged into the mixer and shall be subject to the approval of the Engineer.

The Contractor shall take particular care to ensure that no residual materials remain in the mixer after depositing each batch of concrete and he shall wash and clean out the mixer drum immediately following the completion of each concreting operation or when changing to a mix using a different type of cement.  The Engineer may, at his discretion, forbid the mixing of any concrete if he considers the ambient temperature too high. The Contractor may also be required by the Engineer to carry out frequent cleaning of equipment to remove deposits of hardened or dried concrete which accretes rapidly at high air temperatures.

### Ready-Mix Concrete

Ready-mix concrete shall comply in any aspect to the Specifications and relevant standard (SRPS EN 206-1).

Concrete shall be handled from the place of mixing to the place of final deposit as rapidly as practicable by means, which will prevent the segregation or loss of any ingredient.

For the concrete transported by transit mixer or agitators, the time elapsing from the time water is added to the mix until the concrete is deposited in place shall not be greater than the time of concrete setting.  Driver of delivery trucks shall be provided with trip tickets, which shall be signed by a responsible representative of the Contractor, for submission to the Engineer. The ticket shall contain name and address of the concrete mixing plant, serial number of the ticket and date, truck number, class and/or strength of concrete, cement content of the mix, loading time, slump and any other type of relevant information. The Engineer may send his representative to the concrete mixing plant to check the batching and mixing verify loading time and take a copy of the trip ticket.

Wherever practicable the mixer shall transport the concrete to the place of final deposit and the concrete shall be emptied from the mixer directly into the concrete pump sump to avoid re-handling or flowing.

### Transporting Concrete

Concrete shall be handled from the place of mixing to the place of final deposit as rapidly as practicable by means which will prevent the segregation or loss of any ingredient.

Wherever practicable concrete shall be emptied from a mixer directly into a skip which shall then be transported to the place of final deposit and the concrete shall be discharged as close as possible to its final position to avoid re-handling or flowing.

Should the Contractor propose to use concrete pumps for the transporting and placing of concrete he shall submit full details of the equipment and operating techniques he proposes to use for the approval of the Engineer.

Where concrete is conveyed by chuting or pumping the plant used shall be designed to ensure continuous and unimpeded flow in the chute or pipe. The delivery end of the chute or pump shall be thoroughly flushed with water before and after each working period and shall be kept clean. Water used for this purpose shall be discharged away from any permanent Works.

### Sand-cement Mortar

Mortars/plasters shall satisfy the following standards:

- SRPS EN 998-2 	Specification for mortar for masonry - Part 2: Masonry mortar

- SRPS EN 998-1 	Specification for mortar for masonry - Part 1: Rendering and plastering mortar

## Placing and Compaction of Concrete

Placing and curing of concrete shall be carried out in compliance with relevant rulebooks.

Concrete shall be placed according to the concrete design.

The Engineer’s approval in writing shall always be obtained before any concrete is placed in the Works.

The methods of conveying and depositing concrete shall be such as to prevent segregation of the materials. The placing and compaction of concrete shall be carried out under the direct supervision of a competent member of the Contractor’s staff.

Concrete shall be thoroughly compacted during the operation of placing by means of approved internal mechanical vibrators and carefully worked around the reinforcement, embedded fixings and into all corners of the formwork   and moulds.

The Contractor shall ensure that all shuttering retains a sufficient amount of humidity and has not become shrunk or warped. All soaking or spraying of shuttering shall be done with potable water.

Concreting of any section or unit shall be carried out in one continuous operation up to the construction joints.

If concrete placing is interrupted due to unforeseen circumstances, measures must be undertaken for such interruption of concrete placing not to have negative impact on bearing capacity and other properties of the structure, or element.

Where deposition of concrete has to be interrupted, precautions shall be taken to ensure satisfactory adhesion of later batches of concrete to that previously placed.

Immediately after concreting, the concrete has to be protected from: drying out too quickly, quick heat exchange between concrete and air, precipitation and running water, high and low temperatures, vibrations which can change internal structure of concrete adhesiveness and reinforcement, as well as from other mechanical damages during the binding and hardening of the concrete.

If interruption of placing is not made in the manner envisaged in the design, the Contractor must clean the concrete surface and, at the point of interruption, as required, even to remove concrete in order to get the surface suitable for continuation of further concrete placing.

Initial temperature of fresh concrete in the phase of placement must not be below +5ºC.

The highest temperature of fresh concrete that is not placed by applying special procedures envisaged for tempered concretes must not exceed +30ºC.

If average daily air temperature is below +5ºC or above +30ºC, it shall be necessary to undertake special measures for normal hardening of concrete.

Concrete must be transported and placed in formwork in the manner and under the conditions that prevent its segregation, changes in its composition and properties.

Concrete of such consistency must be placed in the structure that it can be quality placed and compacted by envisaged mechanical devices for placement. Water must not be subsequently added to fresh concrete.

The height of free fall of concrete must not exceed 1.5 m if the necessary measures for prevention of concrete segregation are not undertaken.

Spreading of concrete using vibrator in formwork shall not be allowed.

The maximum distance from the place of placement to the place of final position in compacted condition must not exceed 1.5 m.

Concrete shall be poured in layers not higher than 70 cm.

The following layer must be placed within the time that shall ensure connecting of concrete with the previous layer.

Concrete placing in several layers shall be carried out by vibrating the upper layer, and re-vibrating the lower level.

Immediately after concreting, concrete must be protected from:

- Too quick drying

- Fast heat exchange between concrete and air

- Precipitation and running water

- High and low temperatures

- Vibrations that may change the internal structure, adhesion of concrete and reinforcement, as well as other mechanical damages at the time of setting and initial hardening.

### Depositing in Layers

Concrete shall be deposited in approved quantities and in horizontal layers of such depth as to permit thorough incorporation with the layers below by vibration, spading, ramming and working. If, for unforeseen reasons, it is necessary to stop concreting before completion of a lift, then construction joints as specified shall be formed.

### Concrete Placed in Water

Concrete shall not be placed under water without the written approval of the Engineer. The Contractor shall submit to and obtain the approval of the Engineer his detailed proposals of the plant and method for underwater concreting.

The quantity of cement in any concrete placed in water shall if necessary be increased so that the free water/cement ratio is not more than 0.47. The method of placing concrete in or under water shall be such as to keep as much as possible of the concrete being placed out of direct contact with the water so as to avoid any rapid movement or agitation of exposed surfaces. The work shall where possible be carried out in one operation. Where this is impracticable, laitance, washed out aggregate or foreign matter which may have accumulated on the previously placed concrete shall be completely removed prior to additional concrete being placed. This concrete shall then be placed directly on the cleaned surface. Tremie pipes shall be smooth bored, water-tight and fitted with quick release joints and have an adequate cross-section for the size of aggregate to be used. Bottom opening skips shall be straight sided, perfectly smooth, and fitted with externally operated bottom opening double doors and overlapping canvas flaps. Toggle bags shall be used only for small pours and for depositing small discrete quantities of concrete. Bagged concrete shall not be used for permanent work.

During and after concreting underwater, pumping or dewatering operations in the immediate vicinity shall be suspended until the Engineer permits them to be continued.

### Production and Placing of Concrete under Special Conditions

- Placing of concrete in molds or formwork at outdoor temperatures below +5ºC or above +30ºC shall be considered as concreting under special conditions and then special protection measures must be ensured.

- In plants in which production and placing of concrete is planned at outdoor temperatures below +5ºC, prior to the first frosts, equipment that shall be used for production and placement of concrete at low temperatures should be repaired and checked.

- Aggregate must be resistant to frost, particularly during multiple freezing and thawing.

- Aggregate must not contain organic additions that slow down cement hydration.

- Use of frozen aggregate shall not be allowed.

- When selecting cement, preference should be given to highly active cements with a lower standard consistency and faster emission of hydration heat.

- Cements with the addition of puzzolana shall not be used as a rule.

- Additives must not slow down the process of hydration at low temperatures, increase water permeability of concrete and corrosion of steel in the concrete.

- Effect of additives on concrete should be checked at temperatures of +5ºC and +20ºC with envisaged and double dosing quantity.

- Prior to the first freezing concrete must have minimum 50% of the required hardness.

- Concrete that will be exposed to frost in exploitation must have the required hardness prior to the first frost, and concrete that will at the same time be also exposed to the effect of defrosting salt must also have the required resistance to frost and defrosting salts.

- When on very cold days formwork or thermal protection is removed, sudden cooling of concrete must be avoided and, therefore, external surfaces of concrete must be protected.

- When concreting at high temperatures, the initial workability should be determined according to the previously established loss of workability during transportation and construction.

- If retarding agents and additives for increase of workability are used, their effect should be previously verified on samples with the selected cement and expected concrete temperature.

- Cement and other ingredients of concrete to be placed in massive elements must be such that the temperature of placed concrete in no case exceeds +65ºC.

- Otherwise, measures shall be undertaken to cool concrete components or to cool concrete in the actual element.

### Test Blocks

Before commencing any large pour (as defined in the preceding Section) for a particular mix of concrete, the Contractor shall construct three test blocks 2.0 m cube in size. The temperature of the concrete at the time of casting the blocks shall not exceed 15°C except under hot conditions, when the requirements of these Technical Requirements will apply. The materials used in making concrete for the test blocks, together with the reinforcement, formwork and materials used for protecting the top surfaces, shall be of the same type and from the same source as those intended for the large pour.

Two of the blocks shall be reinforced on two opposing sides and on the top face by 32 mm diameter high yield reinforcing bars 250 mm spacing in each direction. The cover to the outer bars shall be 60 mm. The Contractor shall ascertain the thermal characteristic of the cement and aggregates to be used, from which he shall calculate the likely maximum rise in temperature of the concrete. The data used shall be clearly indicated in the calculations which the Contractor shall give to the Engineer before casting the blocks.

Thermometers shall be installed in the concrete near to the surface at the centre of each face, with one placed centrally in the block. Temperatures shall be recorded at 6 hourly intervals for a period of at least 7 days for each of the blocks.

Six 150 mm test cubes shall be taken during placement of the concrete for each block, two for testing at 7 days and four for testing at 28 days.

The test blocks shall be considered satisfactory if all the following conditions are met for each of the blocks:

- The average strength of the four 28 day test cubes exceeds the specified 28 day characteristic strength by at least 7.5 MPa;

- The rise in temperature during hydration does not exceed 45°C and the difference in temperature between any face and center of the block does not at any stage exceed 20°C;

- The nature of any cracks appearing is such that, in the opinion of the Engineer, the cracks would not constitute a potential source of harm if they were to occur in the Permanent Works.

If condition 1. above is not fulfilled the Contractor shall redesign the concrete mix, construct further test blocks, and repeat the testing as specified.

If condition 2. is not fulfilled or if under 3. the Engineer is of the opinion that the cracks as noted are potentially harmful, the Contractor may proceed with the casting of a large pour only if he incorporates one or more of the following procedures in the concreting operation:

- replace the 19 mm plywood from work to formed faces with material having better insulating properties;

- Increase the surface protection to informed faces.

If the Engineer so requires, the Contractor shall construct further test blocks to demonstrate the efficacy of the measures which are being incorporated in the casting of the large pour.

### Compaction of Concrete

Compacting shall be done exclusively by mechanical procedures, except for concrete of consistency classes S4 and S5 that are suitable (those of 16 cm are not, and those of 22 cm are, in class S4, suitable for casting) for casting.

The Contractor shall regard the compacting of the concrete as work fundamental importance the object of which shall be to produce a watertight concrete of maximum density and strength.

Concrete shall be thoroughly compacted during the operation of placing and shall be thoroughly worked around the reinforcement and embedded fixtures and into corners of the formwork and moulds.

Mechanical vibrators shall be of the immersion type with a frequency of not less than 6,000 vibrations per minute and as approved by the Engineer. A sufficient number of vibrators shall be used to handle the maximum rate of concrete production with a 50% allowance for stand-by units during any period of concreting. All operators handling vibrators shall be trained in their operation.

Vibrators shall be inserted into the non-compacted concrete vertically and at regular intervals. Where the non-compacted concrete is in a layer above freshly compacted concrete the vibrator shall be allowed to penetrate vertically for about 10 cm into the previous layer. Vibrators shall be withdrawn slowly from the mass of concrete so as to leave no voids. Internal type vibrators shall not be placed in the concrete in a random or haphazard manner nor shall concrete be moved from one part of the work to another by means of the vibrators.

Vibration shall not be applied directly or through the reinforcement to sections or layers of concrete which have hardened to the degree that the concrete flow in the formwork over distances so great as to cause segregation. Vibration of concrete shall generally comply with the requirements as specified in relevant standard.

Every care shall be taken to see that reinforcement and fittings attached to the shuttering are not disturbed, and that no damage is caused to concrete that has already set or to the internal face of the shuttering by using immersion type vibrators. In areas of congested reinforcement, it may be necessary to use small diameter pokers and the Contractor shall supply suitable sizes of pokers for each part of the work. Vibration of concrete by hammering the shuttering with hand tools is not permitted.

When placing concrete against horizontal or inclined elements of water stops they shall be lifted and the concrete placed and compacted to a level slightly higher than the underside of the water stop before releasing the water stop to ensure complete compaction of the concrete around the water stop.

The duration of vibration shall be limited to that required to produce satisfactory compaction without causing segregation. Vibration shall not be continued after water or excess grout has appeared on the surface.

Concrete shall not be disturbed after compaction and placing in its final position. Concrete that has partially set before final placing shall not be used and shall be removed from the site.

### Bonding of Old and New Concrete

Continuation of concreting, prior to the undertaking of the procedure of bonding of the old-new concrete, shall call for preparation of surfaces of the previously concreted part over which contact with new concrete shall be established, regardless of whether interruption of concreting for technical or unforeseen reasons is in question.

### Protection and Curing of Concrete

Concrete shall be protected from damage by climatic conditions (direct sunlight, rain, snow or frost), running water or mechanical damage during curing. All methods to be used for curing and protection of freshly placed concrete shall be subject to the prior approval of the Engineer.

The maximum and minimum ambient temperatures and humidity shall be measured and recorded each day by the Contractor. The records shall be made available for the Engineer’s inspection.

Immediately after concreting, concrete must be protected from:

- Too quick drying

- Fast heat exchange between concrete and air

- Precipitation and running water

- High and low temperatures

- Vibrations that may change the internal structure, adhesion of concrete and reinforcement, as well as other mechanical damages at the time of setting and initial hardening.

All exposed surfaces shall as finishing proceeds be covered with a wet hessian sheet followed by a reflective polythene sheet. These shall be securely fastened around the edges and supported in order not to damage the finished concrete surface. As soon as practicable the hessian and polythene shall be lowered into close contact with the concrete and securely weighted or fastened down to prevent wind blowing underneath. The hessian sheet shall be maintained in a moist condition at all times and shall be inspected at intervals not exceeding 6 hours. Concrete shall be kept moist on exposed surfaces for a period of not less than 10 days, or as approved by the Engineer.

Alternative methods of protecting and curing concrete may be approved by the Engineer. In any case liquid curing membranes shall not be used on exposed surfaces or where laitance is to be removed and aggregate exposed to provide satisfactory bond for placing further concrete or mortar screeds. Liquid curing membranes shall not be used where mortar, resin mortar, or joint sealant is to be applied.

Sufficient methods to afford full protection to a concrete pour shall be available at the place of work prior to the commencement of concreting.

### Record of Concreting

The Contractor shall keep complete, accurate and up to date records of the works on site, showing for each day the sections of the works concreted:

- Date, time, weather conditions and air temperature;

- Results of all concrete tests including identification for which part of works the sampled material is representative;

- Number of batches produced, weight and kind of cement used, volume of concrete placed, number of batches wasted or rejected;

- Class of concrete, volume of concrete placed and number of batches used for each location.

The laboratory where concrete test has to be carried out shall be approved by the Engineer and the Employer and be accessible for the said parties at any time. The laboratory should preferably be placed at the site.

### Faulty Work

Any portion of the work which is honeycombed or otherwise inferior shall, on the written instruction of the Engineer, be immediately cut out and reconstructed in an approved manner without extra charge.

Plastering of defective work will not be permitted.

Any leaks or cracks shall be sealed by injection with a synthetic resin or other appropriate methods approved by the Engineer.

### Blinding Concrete (Sub-base)

A blinding layer of minimum 10 cm Concrete Class C16/20 shall be placed under foundations where is requested or ordered by the Engineer. The blinding layer shall be allowed to harden before the structural concrete for the foundation is placed.

### Loading of Concrete Structures

No external load of any kind shall be applied to any part of a concrete structure until the concrete has matured for at least 7 days and then only with the approval of the Engineer and after confirmation that 7- day cube strengths as agreed by the Engineer have been met.

The full design load shall not be applied until confirmation that the specified 28 day strength has been reached.

The Contractor shall not fill around any structure incorporating a ground or floor slab before confirmation that the slab and the wall have reached their specified 28 day strength.

## Joints

### Construction Joints

A construction joint is defined as a joint in the concrete introduced for convenience in construction at which special measures are taken to achieve subsequent continuity without provision for further relative movement.

The Contractor shall submit to the Engineer for his approval not less than 3 weeks before the commencement of concreting, drawings showing his proposals for placing concrete on which the position of all construction joints and lifts shall be shown. No concreting shall be started until the Engineer has approved the method of placing, the positions and form of the construction joints and the height of lifts. The construction joints shall be so located as not to impair the strength of the structure. Rebates, keys or notches shall be formed and water stops respectively joint plates inserted as specified or as the Engineer may require.

The position of construction joints and the size of formwork panels shall be so coordinated that where possible the line of any construction joints coincides with the line of a formwork joint and that in any case all construction joint lines and formwork joint lines appear as a regular and uniform series. For all exposed horizontal joints and purposely inclined joints, a uniform joint shall be formed with a batten of approved dimensions to give a straight and neat line.

Shuttering for construction joints shall incorporate continuous shear keys of substantial proportions to produce watertight joints. Stop-ends shall be freely fixed, made grout-tight and be closely fitted to the reinforcement or other fixtures.

Concrete placed to form the face of a construction joint shall have all laitance removed and the aggregate exposed prior to the placing of fresh concrete. The laitance shall wherever practicable be removed by spraying the concrete surface with water under pressure and brushing whilst the concrete is still green. Where the laitance cannot be removed whilst the concrete is still green, the whole of the concrete surface forming part of the joint shall be hacked to expose the aggregate. Where aggregate is damaged during hacking it shall be removed from the concrete face by further hacking. All loose matter shall be removed and the exposed surface thoroughly cleaned by wire brushing, air blasting or washing, and the surface to which fresh concrete is applied shall be clean and damp.

Where wall kickers are used, they shall be at least 15 cm high and shall be cast monolithically with the wall base.

Unless otherwise specified, the minimum time interval between lifts in slabs shall be 72 hours. At least 72 hours shall elapse between pouring adjacent bays of slabs less than 1 m thick and at least 10 days for thicker slabs.

### Expansions Joints

Expansion joints are defined as all joints intended to accommodate relative movement between adjoining parts of a structure, special provision being made where necessary for maintaining the water tightness of the joint. The Contractor shall comply with the instructions of manufacturers of proprietary jointing materials and shall, if required by the Engineer, demonstrate that the jointing materials can be applied satisfactorily.

Expansion and contraction joints are discontinuities in concrete designed to allow for thermal or other movements in the concrete.

Expansion joints are formed with a gap between the concrete faces to permit subsequent expansion of the concrete. Contraction joints are formed to permit initial contraction of the concrete and may include provision for subsequent filling.

The following general requirements shall apply to both expansion and contraction joints:

#### Filler Boards

Filler boards in expansion joints shall be a performed material securely fixed at right angles to the surface of the concrete within a tolerance of one degree. The boards shall extend without any gaps from the underside of the sealing groove to the base and between side forms or existing slabs. Dowel bars where specified shall be a close fit where they pass through boards. Joints in boards shall be taped to prevent discontinuities.

#### Dowel Bars

Dowel bars shall be round mild steel complying with the relevant standard and shall be sawn or flame cut to length. Flame cut bars shall be dressed by grinding to remove any snags or lips. Dowel bars shall be straight without any irregularities likely to interfere with longitudinal movement in the concrete.

Dowel bars in expansion joints shall be fitted at one end with sleeves which are a sliding fit on the bar and which contain compressible filling in the end remote from the bar, all to the dimensions and details shown on the Drawings.

#### Sealing Grooves and Sealant

Caulking grooves shall be provided where necessary and as specified. At all joints where a caulking groove is formed, the groove shall be wire brushed and loose material removed and blown out by compressed air immediately prior to caulking. After the groove has dried, it shall be primed and caulked with approved jointing compound applied in accordance with the manufacturer's instructions. At all caulked joints, the face of the caulking strip and 50 mm width of concrete on either side shall be painted with two coats of primer having the same base as the caulking compound.

Joints in the concrete shall be sealed with an approved sealant by an approved manufacturer which is suitable for the particular location and environment. Joints shall be sealed immediately after the expiry of the concrete curing period or as soon thereafter as weather conditions permit.

Before sealing is carried out, the sealing grooves shall comply with the following requirements:

- Grooves shall extend across the bays from edge to edge in the case of transverse joints and shall be continuous in the case of longitudinal joints.

- In expansion joints, the filler material shall be exposed for the full length of the joint.

- All grooves shall be dry and free of loose aggregate, paint, corrosion, oil, bitumen spillage, waterproofing agents, concrete curing agents, or release agents.

Bond breaking tape or other suitable material acceptable to the Engineer shall be placed in the bottom of the groove to leave the specified depth for the seal.

Primer shall be applied evenly to the sides of the grooves ensuring complete coverage. The interval between priming and sealing shall be within the limits specified by the sealant manufacturer. In dusty conditions, the primed joints shall be protected from contamination.

The sealant shall be prepared and applied in accordance with the manufacturer's instructions. Care shall be taken to avoid trapping air or forming bubbles and the finished surface of the sealant shall be smooth and free from blemishes to the specified level.

### Water-stops

Water-stops in compliance with relevant standards. No water-stop material shall be brought onto Site until the Contractor has submitted full details of the materials he proposes to use, including samples, and these have been approved by the Engineer. All samples shall be of adequate length for testing.

Water-stops shall be made of materials which are resistant to chlorides, sulphates, or other deleterious substance which may be present in the environment of the Works.

Rubber water-stops may be of natural or synthetic rubber and shall have an elongation at breaking stress of at least 500% at 23°C and shall be capable of accommodating a transverse movement of at least 50 mm. Polyvinyl chloride (PVC) water-stops shall be extruded from an unfilled plasticized PVC polymer or copolymer which does not contain any reclaimed or scrap PVC. PVC water-stops shall have an elongation at breaking stress of at least 240% at 23°C and shall be capable of accommodating a transverse movement of at least 10 mm.

Low modulus water-stops shall be of rubber or PVC as described above but shall have an elongation of at least 200% at 23°C under a tensile stress of 6 MPa and shall be capable of accommodating a transverse movement of at least 50 mm.

Water-stops shall be supplied in lengths as long as possible consistent with ease of handling and construction requirements.

In rubber or plastic materials, joints other than butt joints shall be supplied ready made by the manufacturer. Butt joints shall be made on Site in accordance with the manufacturer's instructions and with equipment supplied for the purpose by the manufacturer.

Water-stops material shall be stored carefully on Site to avoid damage and contamination with oil, or other pollutants. Rubber and plastic water-stops shall be stored in cool well-ventilated places away from direct sunlight.

Rubber and plastic water-stops which are embedded in one side of a joint more than one month before the scheduled date of placing concrete on the other side shall be protected from the sun.

The Contractor shall submit to the Engineer for his approval, not less 3 weeks before the commencement of concreting, details of his proposals for the installation of water-stops. These shall show where joints are to be located and details of the intersections and changes of direction to a scale that shows the position of any joint or shape of any molded section.

As far as possible, jointing on Site shall be confined to the making of butt joints in straight runs of water- stops. Where it is agreed with the Engineer that it is necessary to make on Site an intersection or change of direction or any joint, other than a butt joint in a straight run, a preliminary joint intersection or change of direction piece shall be made and submitted to such tests as the Engineer may require.

Flexible water-stops shall be fully supported in the formwork, free of nails and clear of reinforcement and other fixtures. Damaged water-stops shall be replaced and during concreting care shall be taken to place the concrete so that water-stops do not bend or distort.

Concrete shall be placed carefully round water-stops so as to avoid distortion or displacement and shall be fully compacted. Where water-stops lie in a horizontal or nearly horizontal plane, the Contractor shall ensure that no voids are left on the underside of the water-stops.

Formwork round water-stops shall be carefully removed to avoid damage. If water-stops suffer any damage which cannot be properly repaired in situ, the Engineer may require a section of concrete to be removed and the water-stops replaced.

### Metal Components Cast in Concrete

All metal components to be fixed in the concrete such as pipe sections, frames and covers, hooks, ladders etc., shall be tightly placed in their right position within the shuttering prior to casting of concrete. All faces of metal parts that will be embedded in the concrete shall be thoroughly cleaned to remove all dirt, oil, paint, scale etc., in order to secure thorough adhesion between concrete and metal. In case a free passage of the pipe is required through the concrete, the pipe shall be wrapped with bitumen-saturated felt or a similar elastic sealing material.

# SHUTTERING AND CONCRETE FINISHES

## General

Shuttering shall include all temporary molds for forming the concrete together with all temporary constructions required to support such molds.

## Drawings and Calculations

The Contractor shall submit drawings and calculations showing details of the shuttering he intends to use for the approval of the Engineer. The drawings shall show the materials proposed and indicate details of construction such as size of members, spacing and position of waling’s, struts, bolts and wedges. Shuttering shall not be constructed until the drawings and calculations, (if applicable) have been approved by the Engineer. But such approval shall not relieve the Contractor of his responsibility for the adequacy and performance of the shuttering. Any changes or modifications to the shuttering required by the Engineer shall be carried out at no extra cost to the Recipient.

Shuttering shall be of suitable design and adequate construction to carry the loads without excessive bulging, distortion or deflection. Shuttering shall be constructed so as to prevent loss of water or grout from the concrete. Special attention shall be paid to shuttering where poker or shutter vibrators are used for compacting the concrete.

## Materials for Shuttering

Shuttering shall be made from good quality timber, free from loose knots, shakes and warped surfaces. Timber for shuttering shall not be less than 30 mm in thickness, and the board faces in contact with concrete and the board edges shall be planed smooth and joints shall be tongued and grooved.

Alternatively, with the approval of the Engineer, shuttering may be made from either a) metal with accurately aligned and close fitting joints, or b) plywood or hardboard 5 mm in thickness supported by close boarded timber, 17.5 mm. in thickness, or c) plywood not less than 17.5 mm in thickness. The plywood or hardboard shall be resistant to deterioration by water, and shall be fixed and jointed in such a manner as to give a perfectly smooth and even finish to the concrete.

For textured concrete forms refer to Paragraph “Finish to Concrete Surfaces”.

## Fixing of Shuttering

Shuttering shall be fixed to perfect line and level and be truly plane with no crevices at joints, and shall be securely braced, supported and wedged so as to retain its position without displacement or deflection during the placing and compaction of the concrete. Joints in shuttering shall be made so that no leakage of grout from the concrete can occur.

All joints shall be either horizontal or vertical, unless the form of the finished concrete requires them to be otherwise.

## Back Shuttering

Back shuttering shall be used to form concrete surfaces which are designed to be concealed by earth backfill or further construction, and shall comply with the specified requirements of shuttering except in so far as the board faces are not required to be planed.

## Internal Ties

No internal wall ties shall be used in the construction of the Works except with the approval of the Engineer.

## Coating to Prevent Adhesion

All shuttering in contact with concrete shall be treated with an approved mold oil or solution before usage to prevent the adhesion of the concrete. Such oil or solution shall be carefully applied in such a manner that there is no contamination of the reinforcement or previously placed concrete by the oil or solution. Any material which will adhere to or discolor the concrete shall not be used.

## Access Holes

Adequate access holes shall be left for the purpose of cleaning the shutters and for placing and compacting the concrete.

## Cleaning and Re-use of Shuttering

Before any concrete is placed, the shutters shall be properly cleaned and washed out with water and air under pressure to remove sawdust, shavings and all other foreign matter. All water shall then be drained and mopped out from the shutter.

In no case shall concrete be placed in shuttering until the shuttering has been approved by the Engineer. If shutters or molds are to be re-used, all surfaces shall be cleaned and shall be completely free from remnants of concrete or mortar. If, in the opinion of the Engineer, shutters or molds are not acceptable for reuse, they shall be either properly repaired or substituted with new shutters or molds which shall comply with the requirements of Paragraph “Remedial Treatment of Concrete Surfaces”.

## Removal of Shutters

Shutters shall be removed only with the permission of the Engineer and under skilled supervision of a competent foreman and in such a manner as will not cause any damage to the concrete. Shutters shall not be removed before the concrete is sufficiently set and hardened. The minimum periods which shall elapse between the placing of the concrete and the removal of the shutters for the various parts of the structures cast in-situ are given in the table below, but compliance with these requirements shall not relieve the Contractor of his obligation to delay the removal of the forms if the concrete has not sufficiently set or reached the required strength. Should there be variations in Site temperature and depending on the curing conditions, the Engineer may, at his discretion, vary the period shown in the table below and the period shall be held to cover such a contingency.

Table 7: Period for removal of shuttering with an average temperature of 4°C or above

| Shutters to sides of beams, walls, slabs and columns | Shutters to soffit of slabs and beams |  |
| --- | --- | --- |
|  | Span smaller than or equal to 3 m | Span greater than 3 m |
| 3 days | 8 days | 20 days |

At all times the Contractor shall delay the removal of the shutter if in the opinion of the Engineer the concrete contained therein has not attained sufficient strength.

In cases of average temperatures being below 4°C, the period of removal shall be extended by the number of days the temperature has been lower than 4°C. The periods given in days are days of 24 hours duration. Alternatively, the removal of shutters shall be determined by the demanded compressive strength of the concrete at the time of removing. In this case, the demanded strength shall be in accordance with Paragraph “Concrete Mix Design”.

Any damage to the concrete, which may occur by removal of the shutters or by overloading, shall be made good at the Contractor’s expense and to the satisfaction of the Engineer.

## Finish to Concrete Surfaces

The following requirements for the finish to concrete surfaces shall apply as appropriate unless otherwise requested:

- Exposed surfaces (other than exposed upper surfaces), surfaces in contact with liquid including sewer inverts and outside vertical surfaces of in-situ caissons:

The surface texture required shall unless otherwise specified be that obtained from the use of a smooth impervious face of metal or the like.

- Concealed surfaces:

The surface texture required shall be that obtained from the use of sawn close-jointed timber or the like.

- Exposed upper surfaces:

Exposed upper surfaces of floor slabs and upper surfaces in contact with water shall be floated with a steel trowel to a dense smooth uniform finish free from trowel marks. Other exposed upper surfaces shall have a smooth finish obtained with a wood float.

- Concrete road and hard standing surfaces:

Concrete road and hard standing surfaces shall have the surface finish obtained by the conventional use of a hand tamper or vibrating beam.

- Rendered or surfaced areas:

Areas to be subsequently rendered or to receive a surfacing shall be adequately scored to provide an effective key.

- Exposed arises:

Exposed arises shall be formed with a chamfer 20 mm by 20 mm.

- Textured Concrete:

Surfaces to include a textured concrete finish shall be as detailed on the Drawings. The Contractor shall construct a sample of l m² for the Engineer’s approval prior to constructing textured concrete in the permanent Works.

- All surfaces:

All surfaces shall be free from cracks, sand runs, honeycombing, porosity and grout/matrix loss. For partly buried surfaces the exposed surface quality shall extend to 500 mm below final ground level.

## Dimensions and Surfaces of In-Situ Concrete

Workmanship in formwork and concreting shall be such that concrete shall normally require no making good, surfaces being perfectly compacted, smooth and with no irregularities. Concrete surfaces for the various finishes shall in any event never exceed the maximum permitted tolerances stated in the table below.

In the table “line and level” and “dimension” shall mean the lines, levels and cross-section dimensions shown on the drawings.

Surface irregularities shall be classified as ‘abrupt’ or ‘gradual’. Abrupt irregularities include, but shall not be limited to, offsets and fins caused by displaced or misplaced formwork, loose knots or other defects in formwork materials, and shall be tested by direct measurement. Gradual irregularities shall be tested by means of a straight template for plane surfaces or its suitable equivalent for curved surfaces, the template being 3.0 m long for unformed surfaces and 1.5 m long for formed surfaces.

| Finish | Maximum Tolerances [mm] for In-Situ Concrete |  |  |  |
| --- | --- | --- | --- | --- |
|  | Line and Level (except tunnel works) | Abrupt Irregularity | Gradual Irregularity | Dimension |
| Exposed or PVC/GRP lined formed surfaces and surfaces in contact with liquid | ± 3 | 0 | ± 3 | ± 6 |
| Rendered form surfaces | ± 6 | ± 3 | ± 6 | ± 6 |
| Other concealed surfaces | ± 12 | ± 6 | ± 6 | + 12 / – 6 |
| Exposed unformed surfaces | ± 6 | ± 3 | ± 3 | ± 6 |
| Concealed unformed surfaces | ± 12 | ± 6 | ± 6 | + 12 / – 6 |

## Remedial Treatment of Concrete Surfaces

Any remedial treatment to concrete surfaces shall be agreed with the Engineer following inspection immediately after the stripping of formwork and shall be carried out without delay.

Any concrete the surface of which is found to have been treated before inspection by the Engineer shall be rejected.

Any minor surface blemishes shall be repaired to the satisfaction of the Engineer immediately after completion of curing. Remedial measures may include, but shall not be limited to, the following:

- Holes left for formwork supports shall be thoroughly cleaned out to remove all loose material and the sides shall be roughened, if necessary, to ensure a satisfactory bond. They shall then be filled with dry-pack mortar.

- Fins, pinhole bubbles, surface discoloration and minor defects may be rubbed down with sacking and cement immediately the formwork is removed.

- Abrupt and gradual irregularities may be rubbed down with carborundum and water after the concrete has been fully cured.

- Small defects and minor honeycombing shall be chipped out perpendicular to the face of the concrete to a depth of at least 25 mm and filled with dry-pack mortar as specified in Paragraph “Dry-pack Mortar”.

All other defects will be regarded as too extensive to permit satisfactory repair and the concrete containing the defect shall be broken out and replaced.

## Dry-pack Mortar

Dry-pack mortar for filling holes and repairing surface blemishes shall be made from one part by weight of cement and three parts fine aggregate passing a 1 mm sieve and an expanding agent approved by the Engineer. Additives to improve workability may be added to the approval of the Engineer. The color of the mortar shall match that of the surrounding concrete. The mortar shall be mixed with only sufficient water to make the materials stick together when being molded in the hands.

The dry-pack material shall be placed and packed in layers having a thickness not greater than 15 mm. The companion shall be carried out by use of hardwood stick and hammer and shall extend over the full area of the layer, particular care being taken to compact the dry-pack against the sides of the hole. After companion the surface of each layer shall be scratched before further loose material is added. Holes shall not be over filled and the surface shall be finished by laying a hardwood block against the dry-pack fill and striking the block several times. Steel finishing tools shall not be used and water shall not be added to facilitate finishing.

## Concrete Injection

Before any injection application the cracks to be injected shall be examined carefully to find the best injection method and material. Remedial of any further damages on the concrete structure caused by wrong injection material or injection method shall be borne by the Contractor.

# STEEL REINFORCEMENT

## General

All reinforcement for structural concrete of the permanent works shall comply with the requirements of SRPS EN 10080 and be placed with laps in accordance with SRPS EN 1992-1-1.

Welding of reinforcing steel shall be carried out in accordance with SRPS EN ISO 17660.

The chemical and physical properties of reinforcing steel shall be tested and reported by valid Mill Test Certificates (MTC) (or MTR Reports) issued by the manufacturer in accordance with SRPS EN 10204 class 3.1. Quality control sampling and testing related to delivered consignments shall be conducted and reported as described in above-mentioned standard.

The Contractor shall submit the test certificates without undue delay for the Engineer’s review without objection.

### Reinforcement Supply and Testing

The Contractor shall submit details of the source and supplier of reinforcement to the Engineer for approval.

All manufacturers of reinforcement shall operate according to quality management system based upon ISO EN 9001 or higher and hold a valid certificate of approval for manufacture issued by a national authority. The certificate number shall be stated on all documentation.

If reinforcement is cut and bent by a distribution supplier and/or manufacturer, the distribution supplier or manufacturer shall operate a documented quality control system, which shall be approved as part of the Contractor's quality management system. The detailing shall be in accordance with the relevant EN design standard and comply with requirements of national technical regulations.

All reinforcement shall be delivered in clearly identified, tagged bundles, mats or prefabricated assemblies and shall be stored on site in a manner so as not to be contaminated or otherwise damaged. Fabric shall be stored flat in a horizontal position.

All dimensions shall be in accordance with reinforcement schedules and standard tolerances unless otherwise specified and with all reinforcement deliveries.

Reinforcement shall not be dropped from a height, mechanically damaged or shock loaded in any way.

Mechanical examination of concrete steel in accordance with SRPS EN ISO 15630-1, SRPS EN ISO 6892-1, SRPS EN ISO 7438 and examination of welded reinforcement grids SRPS EN ISO 15630-2, SRPS EN ISO 6892-1, SRPS EN ISO 7438.

## Types, Quality and Storage

Steel reinforcement for concrete shall consist of steel bars or steel wire fabric, except where otherwise shown.

The Contractor shall carry out the works described in accordance with the appropriate standards or equivalent local or international standards. The main standards are, but shall not be limited by the following:

| - SRPS EN 10020 | Definition and classification of grades of steel |
| --- | --- |
| - SRPS EN 10027 | Designation system for steels |
| - SRPS EN 10080 | Steel for the reinforcement of concrete - Weldable reinforcing steel - General |
| - SRPS EN ISO 15630 | Steel for the reinforcement and prestressing of concrete – Test methods |
| - SRPS EN ISO 6892 | Metallic materials - Tensile testing |
| - SRPS EN ISO 17660-1 | Welding - Welding of concrete steel - Part 1: Load-bearing welded joints |
| - SRPS EN ISO 17660-2 | Welding - Welding of concrete steel - Part 2: Non-load bearing welded joints |
| - SRPS EN ISO 7438 | Metallic materials - Bend test |
| - SRPS EN 1992-1-1 | Eurocode 2: Design of concrete structures - Part 1-1: General rules and rules for buildings |
| - SRPS EN 10204 | Metallic products - Types of inspection documents |

B 500B and MA reinforcement shall be installed in the structures.

Storage of reinforcement shall be on racks or supports clear of the ground. Different types and sizes of reinforcement shall be kept separate.

## Prestressing Steel

Quality of prestressing steel shall comply with the Rulebook on Technical Standards for Steel Wires, Rods, and Ropes for Prestressing of Structures.

All wire, strand or bars shall be assigned a lot number and tagged for identification purposes before shipment. Anchorage assemblies to be shipped shall be likewise identified. Reels of prestressing strands stored on the pre-stressed plant yard and intended for the use in the works shall be stored off the ground and protected from the weather by means of an approved cover.

The manufacturer shall supply typical curves obtained from mill tests of the material furnished for use in checking stresses by means of observed elongations. In addition, the manufacturer of the strand shall furnish affidavits certifying as to the required properties. Where the Engineer intends to require non-destructive testing of one or more parts of the structure, special specifications will specify the required details of the work.

All of the materials specified for testing shall be furnished without cost to the Contracting Authority and shall be delivered in time for tests to be made well in advance of anticipated time of use. All samples submitted shall be representative of the lot to be furnished and in the case of wire or strand, shall be taken from the same master roll.

The following described samples shall be selected from each lot of material by the Engineer:

- Pretensioning Method. For pretensioning strands, samples consisting of two pieces, one at least 1 m and one approximately 300 mm long, shall be furnished for each shipment, each strand size, and each heat number, per 5 reels or part thereof, of regular or high strength strand;

- Post tensioning Method. The following lengths shall be furnished:

  - For wires requiring heading - 1.5 m

  - For wires not requiring heading - Sufficient length to make up one parallel-lay cable 1.5 m long consisting of the same number of wires as the cable to be furnished

  - For strand to be furnished with fittings -1.5 m between near ends of fittings

  - For bars to be furnished with wedge anchors -1.5 m between faces of anchor plates

- Anchorage Assemblies. Two anchorage assemblies shall be furnished complete with distribution plates of each size or type to be used if anchorage assemblies are not attached to pre-stressed steel samples.

## Bending and Cutting Schedules

The Contractor shall prepare or his own use bar bending schedules and bar lists, cutting schedules and sheet lists for wire fabrics for each individual structure from the information given on the drawings and in the Specification, and shall be responsible for ensuring that correct information is given when ordering reinforcement. Copies of these schedules, list and orders shall be submitted to the Engineer for his approval. Steel bar supports shall be included in the bending schedules.

The approval of the bar bending and cutting schedules, lists, and orders shall not relieve the Contractor of his responsibility.

## Protection and Cleaning

Reinforcement shall be protected at all times from damage, and when placed in the structure shall be free from dirt, loose mill scale, rust scale, paint, oil, or other foreign substance. All reinforcing steel shall be carefully cleaned of all set or partially set concrete, shutter oil or paint which may have been deposited during the construction of adjacent Works.

## Bending of Bars

Steel reinforcement shall be cut from straight bars free from kinks and bends or other damage and shall be bent cold by experienced competent workmen. Bars of diameter greater than 12 mm shall be bent in a bending machine designed for the purpose and approved by the Engineer. Any reinforcing bar that has already been bent shall not be re-bent at the place of the previous bend.

## Cutting of Wire Fabrics

Wire fabric reinforcement shall be cut straight from the sheets. Cutting of sheets shall be done in such a way as to limit the loss of material. The use of off-cuts in the Permanent Works will not be permitted.

## Lapping of Bars and Wire Fabrics

Lapping bars and wire fabrics is permitted when necessary and approved by the Engineer. No welding of reinforcement shall be carried out unless authorized by the Engineer

Unless otherwise specified, lap length of bars shall be in compliance with the applied standard, and laps shall be positioned in a staggered pattern.

Laps on adjacent sections of wire fabrics shall generally be carried out as follows:

- End to End by lapping the two pieces one full mesh (measured from the ends of the longitudinal wires in the other piece) and securing the two pieces together with wire ties placed at intervals of about 450 mm.

- Side by Side by placing the two selvage wires (the longitudinal wires at the edges of the fabric) one alongside and lapping the other, and by securing the two pieces together with wire ties placed at intervals of about 900 mm.

## Fixing of Reinforcement

All reinforcing steel shall be accurately placed and fixed in position and retained in that position during the placing of the concrete.

Correct positioning will be achieved with the use of steel bar supports, blocks, ties, hangers or other approved supports. Spacer blocks for holding the reinforcement from contact with the forms, or adjacent reinforcement, shall be of dense precast concrete blocks of approved shapes and dimensions. The blocks shall be fitted with a semi-circular hollowing and double bent poured-in binding wires. The water tightness of these blocks must be at least similar to the concrete into which they are concreted. The use of pebbles, pieces of broken stone or brick or other materials will not be permitted. Steel shall be bound and tied in its correct position using steel wire. Apart from any other requirement, the reinforcing steel shall be fixed in such a manner that it will support its own weight and any loads which may be imposed upon it during construction without displacement, deflection, or movement of any kind.

In slabs provided with two more layers of reinforcement the parallel layers of steel bars shall be supported in position by the use of steel chairs. Spacer blocks shall be placed at each chair to support the layers of reinforcement from the blinding concrete or shuttering.

The concrete cover to the nearest reinforcement exclusive of plaster or other decorative finish and concrete blinding shall be in compliance with the respective standards.

The distance between any two parallel bars except at laps shall not be less than 5 mm greater than the nominal aggregate size.

All reinforcement projecting from construction joints or likely to be exposed to the weather for long periods before concreting is commenced, shall be covered with polythene, blinding tape, cement grout or other materials to the satisfaction of the Engineer in order to prevent excessive rusting or staining of the surrounding concrete. Should in spite of these precautions rust staining occur on any permanently visible surfaces, it shall be removed at once to the satisfaction of the Engineer.

## Approval before Concreting

All reinforcement, after having been fixed in position, shall be inspected and approved by the Engineer before any concrete is placed. Any concrete placed contrary to this requirement shall, if ordered by the Engineer, be removed together with the reinforcement and replaced by the Contractor at his own expense.

# PRESTRESSED CONCRETE

## Sustainability of Prestressed Concrete Structures

Sustainability of pre-stressed concrete structures shall be guaranteed by proper design and execution.

Class of prestressing steel, anchors and other prestressing equipment shall be defined by the design documentation prepared by the Contractor, which must be compliant with the applicable legislation, regulations, standards and technical recommendations of the Republic of Serbia.

In particular design and execution shall consider the following risks. The Contractor shall prove to the Engineer his measures to achieve sustainable structures by prevention of:

- Tendon corrosion and eventually tendon breakage;

- Uneven shim stack heights on the anchor-heads;

- Spalling and cracking of concrete beneath the anchor-head base plates;

- Free water in the bottom grease caps;

- Poorly drained top anchorage ledges;

- Absence of filler grease, and

- By minimizing tendon relaxation losses.

Prestressed concrete structures shall comply according to EC2.

## Tendons

### General

Quality and material of prestressing steel is described in these Technical Requirements. In generally, for tendons the following requirements shall apply:

- Type homologation is required;

- Requirements on strength, deformation and fatigue resistance have to be fulfilled by:

  - Proper choice of system (pre- or post-tensioning, bond or unbound)

  - Design of concrete strength, profiles and dimensions fit for the purpose of the structure in dependence of chosen system

  - Limitation of ultimate strain - Proper anchorage system and location

  - Force transmission has to be guaranteed.

### Tendon Fabrication and Supply

- No tendon containing splices shall be used;

- No welding shall be permitted on or near tendons, nor shall any heat be applied to tendons. Any tendons which have been affected by welding, weld spatter and/or heat, or otherwise damaged shall be rejected and shall be replaced by the Contractor at its expense;

- A durable metal label, on which shall be stamped the length of the tendon and the coil number of the wire or strand used, shall be tied to each tendon;

- The tendons shall be supplied in coils of a sufficiently large diameter so that they are straight as they unwind from the coils. Kinked or damaged tendons will not be permitted.

### Storage and Cleaning

- Coils of tendons shall be protected from the weather, chlorides, dirt, mortar, loose rust, tar, paint, oil or any other deleterious matter and other aggressive substances, and shall not be placed in direct contact with the ground;

- Components shall be handled and stored so that mechanical damage and detrimental corrosion are prevented. They shall be kept free from chlorides, urea;

- All lubricant used in the drawing of the tendon shall be thoroughly removed by a suitable degreasing agent. No rust shall be permitted on the tendons.

### Testing Requirements for Tendons

#### Manufacturer's Test Data

Testing of wire or strand will be carried out in accordance with the requirements of the relevant standard (Tensile testing)

Testing of wire or strand will be carried out in accordance with the requirements of SRPS EN ISO 6892-1 (Metallic materials - Tensile testing - Part 1: Method of test at room temperature).

Each delivery of materials shall be accompanied by documentation showing the lot numbers from which each coil is taken, together with the relevant test certificates, which shall include the data on chemical composition. All coils of tendons shall be capable of being identified with the test certificates.

The information provided by the manufacturer or supplier shall demonstrate that each coil complies with the Specification and with the stated properties submitted.

For each coil used in the Works the Contractor shall also provide the following information obtained from the manufacturer:

- Breaking force;

- Yield strength and elongation (based on lots representing not more than five manufactured lengths);

- Load-strain relationship (based on lots representing not more than five manufactured lengths), stating the measured cross-sectional area and the elongation per 10 m at 70% and 80% of nominal minimum breaking force;

- 1,000 hour relaxation loss at 70% and 80% of nominal minimum breaking force;

- Plot of the load-strain relationship which is representative of the tendon material proposed for use in the works.

#### Field Tests to Confirm Stressing Calculations

- The Contractor shall confirm the validity of his predicted elongation’s by carrying out field tests on lengths of strand not less than 10 m in length. This would normally be the stressing of an undeflected strand in a structure;

- One length of strand from each coil proposed for use in the Works shall be stressed to confirm the load-elongation results provided by the manufacturer. The sampling and stressing of this strand shall be carried out in the presence of the Superintendent;

- During stressing of the test strands, measurements of elongation shall be taken at incremental jacking forces up to 80% of the minimum breaking force to establish the full load-strain relationship for the test strand which shall then be compared with that provided by the manufacturer;

- If the measured elongation (including extrapolated component for the pull-up force) agrees with the value obtained from the manufacturer's data sheet to within ±2% then the manufacture's test data may be used for predicting elongations for all strand taken from that coil;

- If the measured elongation is not within ±2% of the value predicted from the manufacturer's test data, the Contractor may revise his calculations on the basis of the field tests, provided he can demonstrate that the total prestress forces will be within the limits.

### Corrosion Protection of Unbounded Tendons

Tendons shall be lubricated and protected against corrosion by a properly applied coating of grease or other approved material. Minimum weight of coating material on the prestressing strand shall be not less than 3 g of coating material per m and per 1 mm diameter of the strand. The amount of coating material used shall be sufficient to ensure essentially complete filling of the annular space between the strand and the sheathing. The coating shall extend over the entire tendon length. Coatings shall remain ductile and free from cracks at the lowest anticipated temperature and shall not flow out from the sheath at the maximum anticipated temperature. Coatings shall be chemically stable and non-reactive to the tendon, the concrete and the sheath.

### Anchorage

Stress able anchorage, fixed anchorage and couplings shall develop almost 100% of the actual ultimate strength of prestressing steel without exceeding anticipated set. Dynamic tests shall be performed on the whole system of anchorage and prestressing steel as specified below.

Anchorage castings shall be nonporous and free of sand, blow-holes, voids and other defects. Damaged or used anchorage components shall not be permitted.

#### Types of Anchorage

For a wedge type anchorage, the wedge grippers shall be designed to preclude premature failure of the prestressing steel due to notch or pinching effects under static test load conditions to determine yield strength, ultimate strength and elongation of the tendon.

An anchorage of any other type than described below may be used provided the basic requirements noted herein are demonstrated by an acceptable test program.

#### Anchorage for Bar Tendons

Stressable anchorage for bar tendons shall consist of an anchor-plate casting with a wedge seat. A reusable pocket former shall provide a recess for the stressing jack. Special care shall be given to the corrosion protection between the anchor-plate and the duct.

Fixed anchorage for bar tendons shall be similar to stress able anchors (preseated and secured anchoring wedges).

#### Anchorage for Multiple Strand Tendons

Stress able anchorage for multiple strand tendons shall consist of a steel anchor head with different types of bearing plate and trumpet assemblies. Strands shall anchored individually by wedges which, by means of the stressing unit, are hydraulically seated in the anchor head for equal gripping. The wedges shall be self-centering on the anchorage body.

Fixed anchorage for multiple strand tendons shall be either similar to the stress able anchorage or alternatively, depending on the number of strands either with button heads on strands or of the loop-type or whereby each strand is provided with a short loop outside the duct. The loops shall be formed on the construction site by means of a special light tool.

Coupling anchorage for multiple strand tendons shall be used when structural components are concreted in sections and tendons have to be connected to already stressed ones, anchored at a construction joint. The anchor head shall accommodate an equal number of strands from both sides and for safe gripping, wedges and springs shall be preassembled. The second stage strands shall be coupled by inserting the chamfered strands into the anchor holes with special spring fixed wedges. On each strand the insertion length shall be marked in order to have a visual control that it is properly positioned.

For cylindrical structures (water tanks, digester tanks, large pipes or dome shells) that require circumferential post-tensioning non-fixed coupler may be applied. The tendon anchorage shall consist of an anchorage block with wedge holes on both sides to accept bars or greased and sheathed strands. The strands shall overlap in the block (belt-buckle principle).

#### Anchorage for Multiple Wire Tendons

Stress able anchorage for multiple wire tendons shall consist of a button head by which each wire shall be fixed in a compact anchor head. The button head shall be cold-upset by special machines. After prestressing the anchor head shall be blocked either by a screwed-on lock nut or by shims inserted between anchor-head and bearing plate.

Fixed anchorage for multiple wire tendons shall be either similar to the stress able anchorage or alternatively of the fan-type. The fan-anchor partially transmits the forces by bond and partially by an anchor plate.

Coupling anchorage for multiple wire tendons connecting two tendons shall consist essentially of two stress able anchorage coupled by a rod or a coupling sleeve.

#### Requirements

Anchorage shall meet the following requirements:

- An anchorage for bonded tendons tested in an unbounded state shall develop 95% of the actual ultimate strength of the prestressing steel, without exceeding anticipated set at time of anchorage. An anchorage which develops less than 100% of the minimum specified ultimate strength shall be used only where the bond length provided is equal to or greater than the bond length required to develop 100% of the minimum specified ultimate strength of the tendon. The required bond length between the anchorage and the zone where the full prestressing force is required under service and ultimate loads shall be sufficient to develop the specified ultimate strength of the prestressing steel. The bond length shall be determined by testing a full-sized tendon. If in the unbounded state the anchorage develops 100% of the minimum specified strength it need not be tested in the bonded state.

- An anchorage for unbounded tendons shall develop 95% of the minimum specified ultimate strength of the prestressing steel with an amount of permanent deformation that will not decrease the expected ultimate strength of the assembly.

- The minimum elongation of a strand under load in an anchorage assembly tested in the unbounded state shall be not less than 2% when measured in a gauge length of 3 m.

#### Anchorage Reinforcement

Spiral and other reinforcement specified by the manufacturer as being required as part of the anchorage devices shall be incorporated in the works in accordance with the sizes and dimensions recommended by the manufacturer for the prestressing system to be used.

### Sheathing

In generally, for sheathing the following requirements shall apply:

- Type homologation is required;

- The sheathing and all splices shall be mortar tight;

- Sheathing shall be stored off the ground and protected from the weather at all times;

- Profile of sheathing has to guarantee sound force transmission;

- The Manufacturer's test values for the friction coefficients of the proposed sheathing shall be confirmed by the Contractor;

- Sheathing shall have sufficient strength and durability to resist damage and deterioration during fabrication, transport, storage, installation, concreting and tensioning.

#### Specific Requirements

Sheathing for Bonded Post-Tensioned Tendons

- Sheathing shall be strong enough to retain its shape, resist unrepairable damage during production, and prevent the entrance of cement paste or water from the concrete;

- Sheathing shall be securely fixed throughout its length, by methods that will hold it in position and resist movement due to flotation, concrete placement or vibration and do not damage or deform it;

- Sheathing material left in place shall not cause harmful electrolytic action or deteriorate;

- The inside diameter shall be at least 6 mm larger than the nominal diameter of single wire, bar or strand tendons; or in the case of multiple wire, bar or strand tendons, the inside cross-sectional area of the sheath shall be at least twice the net area of the prestressing steel;

- Sheaths shall be capable of transmitting forces from the grout to the surrounding concrete;

- Sheaths shall have grout holes or vents at each end and at all high points except where the degree of tendon curvature is small and the tendon is relatively level.

Sheathing for Unbounded Tendons (Post-Tensioning System)

- Sheathing shall be of material which is not reactive with concrete, coating or steel. The material shall be waterproof;

- The sheath shall have a coefficient of friction with the strand of less than 0.05;

- Tendon covering shall be continuous over the unbounded length of the tendon and shall prevent the intrusion of water or cement paste and the loss of the coating material during concrete placement;

- The sheaths shall not become brittle or soften over the anticipated exposure temperature and service life of the structure;

- The minimum wall thickness of sheaths for non-corrosive conditions shall be 1 mm;

- The sheathing shall have an inside diameter at least 0.8 mm greater than the maximum diameter of the strand;

- Joints between the sheathing and any other part of the prestressing system shall be effectively sealed to prevent entry of mortar, dust, water or other deleterious matter.

## Installation of Pre-Tensioning Systems

### Pre-Tensioning Anchorages Installation

Strand chucks for pre-tensioning shall be capable of anchoring the strand without slippage after seating. Length of grips and configuration of serrations shall be such as to ensure against strand failure within the vise jaws at stresses less than 95% of strand ultimate strength. Steel casings for strand vises shall be verified by the manufacturer as capable of holding at least 100% of the ultimate strength of the strand. Devices used to deflect the strand to the required position shall be designed to minimize friction to the level consistent with the tolerances for strand tensioning. Strand shall be able to move freely over, under, or through the device.

Harped strands must be held in position by devices capable of supporting the load imparted from the tensioned strand without excessive deformation. Excessive friction in such devices can cause the strand tension to vary over the length of the bed. If a strand becomes pinched or otherwise caught in the device, strand breakage can occur.

Strand restraining devices should be designed for an appropriate factor of safety.

Each anchorage device shall be set square to the line of action of the prestressing tendon and shall be positioned securely to prevent movement during concreting.

The anchorage devices shall be cleaned prior to the placing of concrete.

### Pre-Tensioning Tendon Installation

- Tendons containing nicks, kinks, or former chuck grip marks shall not be used;

- Steel showing evidence of scale formation or which has become pitted shall not be used;

- Tendons shall be located as shown on the drawings within a tolerance of ±5 mm. Suitable devices shall be provided so as to maintain the correct positioning of the tendons during placing of concrete;

- Care shall be used during placement of prestressing steel to avoid physical damage and contamination. Damaged strands shall be rejected;

- Particular care shall be taken that the tendons shall not come into contact with the oiled surface of the forms or be otherwise soiled. Any oil etc. found on the tendons shall be removed. Then the cleaned strand shall be restored to its original condition prior to concrete placement;

- The prestressing steel shall be inspected for broken wires and other damage after placement into the bed;

- Any damaged prestressing steel in the bed shall be removed and replaced before the stressing operation begins;

- Prestressing steel that has been stressed in a draped position shall not be reused.

## Installation of Post-Tensioning Systems

### Grout Holes Installation

Grout holes shall be provided at both ends of the ducts and shall be at least 10 mm diameter. The ends of the grouting holes shall be equipped with a plug, valve or similar device capable of withstanding a grout pressure of 1 MPa without loss of water or air. Additional vents with plug valves shall be provided at high and / or low points of the duct to bleed air or water and to ensure the duct is completely filled after grouting.

### Tendon Installation

Special uncoilers or hydraulic winches shall be used to properly install the tendons in the structure. Tendons shall be handled with care, and be installed through the sheathing in such a manner as to avoid damage or contamination to either the tendon or sheathing.

Strands may be pushed into the sheathing either before or after casting the concrete. The mechanical pushing equipment shall provide relatively high push speed and shall be equipped with a length measurement meter with automatic shut-off and an electric push-button switch at discharge end for locking into place and length correction.

Strands may be as well pulled into the duct onsite. In normal cases, the whole tendon i.e. all strands shall be pulled through simultaneous hydraulically winching the bundle with the winch cable. The winch cable shall be placed by threading steel or glass fibre wires through the sheathing. Winches shall offer control of speed and pulling force.

## Stressing Equipment

All stressing equipment shall conform to the requirements of (a), (b), or (e) below. In addition, all stressing equipment shall be calibrated in accordance with (c) below in order to give a correlation between the force applied to the tendon and the reading indicated by the pressure gauge.

- The stressing equipment shall be a hydraulic jacking system which can be adjusted to automatically apply and sustain a predetermined load together with a pressure transducer built into the hydraulic system. Such transducer shall be connected to a digital readout and printer which shall provide an instantaneous readout and record of the applied load in pounds. The readout record shall provide a numerical value of the applied load. The jacking system used shall have the capacity to induce the required load. The jacking equipment shall contain pressure bypass valves that will permit pulling to a predetermined load which can be held while elongation checks are made. Use of this system shall be based on demonstrated accuracy and repeatability verified through comparison with loads indicated by either an independent load cell or proving ring;

Continued use of the equipment shall be contingent upon the satisfactory performance of the equipment in service as determined under the requirements of (d) below;

- The stressing equipment shall be a hydraulic jacking system as described in (a) above with a load cell built directly into the hydraulic jack and connected to the digital readout and printer instead of the pressure transducer. Continued use of the equipment shall be contingent upon the satisfactory performance of the equipment in service as determined under the requirements of (d) below;

- Prior to their use, all jacking systems shall be calibrated. Calibration shall be repeated at intervals not exceeding 12 months. Recalibration during the intervals may be required by the Engineer as described hereinafter. Calibrations and recalibrations shall done by a qualified calibration agency;

Gauges, jacks and pumps shall be calibrated as a system in the same manner they are used in tensioning operations with the cylinder extension in the approximate position that it will be in actual use at final jacking force. Calibrations should cover the load ranges that will be used during production. A certified calibration curve shall accompany each tensioning system. Load readings can be used directly if the calibration determines a reading is within 1.5% tolerance of actual load. Calibration of load cells or proving rings used to calibrate jacking systems shall be on compression testing equipment that has been checked by an independent agency accredited for this kind of testing within the preceding 24-month period;

If, while work is in progress, any jack or gauge appears to be giving erratic results, or if the jack force and elongation do not compare within specified limits and differences cannot be justified, recalibration shall be required. Recalibration shall also be required after internal jacking system repairs or when gauge and jacking units are switched;

- Any calibration or recalibration shall be done in accordance with SRPS EN ISO 6892-1 (Metallic materials - Tensile testing - Part 1: Method of test at room temperature). After calibration or recalibration has been completed, a certificate shall be prepared and signed by the person in responsible charge of the verifications as outlined;

- The accuracy of the jacking and recording system shall be verified by the Contractor a minimum of once each week during stressing operations by either an independently calibrated load cell or a proving ring. The load reading from the recording system shall agree within 1.5% of the load indicated by the load cell or proving ring.

Pressure gauges shall comply with the requirements for industrial gauges. Test certificates showing such compliance shall be kept in the site office of the Contractor.

Jacks for multi-strand tendons shall be equipped with:

- Internal strand guide tubes with automatic strand gripping and releasing devices; - A check valve which shall hold the pressure in the event of hydraulic failure; - Special devices for power seating all wedges simultaneously.

- Jacks also shall allow for;

- Bleed-back to achieve full utilization of the maximum allowable stresses along the tendon length; - Detention of already pre-stressed tendons.

## Stressing Records

The Contractor shall keep records of the stressing operation as follows:

- Identification number of dynamometers, gauge, pump and jack;

- Identification particulars of tendons;

- Initial forces (or pressures) when tendons are marked for measurement of elongation;

- Final forces (or pressures) and elongation obtained on completion of tensioning;

- Elongation remaining after anchoring;

- Elongation obtained at intervals during tensioning, together with corresponding forces (or pressures);

- Concrete stress shall be controlled at the time just after transferring of prestress and at service load after all losses

## Pre-Tensioning Stressing

### Pre-Stressing

The stressing operations shall consist of the application of the final load required by the plans and adjusted for abutment rotation, bed shortening, anchorage header movement, anchor set, slippage, live end seating and any other element as applicable for the type of bed and anchorage being used.

Also, the final load required by the Drawings shall be adjusted when the temperature differential between the ambient temperature at time of stressing and the expected concrete temperature at time of placement is greater than 24°C The load shall be increased 0.5% for each 3°C increment between the ambient temperature at time of stressing and the expected concrete temperature at time of placing. When the expected concrete temperature at time of placing is below the ambient temperature at time of stressing, no adjustment to the final load shall be made.

The stress in the prestressing steel shall not exceed the stress allowed.

Compensation for temperature differential and abutment rotation is not required for self-stressing beds. However, the final load shall be adjusted for the effects of bed shortening due to the load from all the strands.

If the placement of concrete is delayed for more than 7 days after the completion of the stressing operation, the Contractor shall check and adjust the final strand load as necessary prior to the placement of concrete.

The stressing methods, in general, consist of stressing to the loads indicated by the jacking system, or stressing to the required load while monitoring the elongation of the prestressing steel.

Stressing shall be accomplished by either single strand stressing or multiple strand stressing, and shall be symmetrical about the vertical axis of the structure.

### Single Straight Strand Stressing

When single straight strand stressing is used, the prestressing steel shall be tensioned until the required final load is attained. The loads indicated by the jacking system shall control the tensioning process. Two stage stressing, consisting of an initial load and final load, may be used. The initial load, if used, shall be between 5% and 25% of the final load.

### Multiple Straight Strand Stressing

Each strand to be stressed in a group shall be individually brought to an initial uniform tension prior to being given their full tensioning. The amount of the initial load will be influenced by the length of the casting bed and the size of strands in the group to be tensioned. The minimum initial tensioning load shall be 5% of the required final load. The magnitude of this load may be increased if deemed necessary but shall not exceed 25% of the required final load. The strands shall then be stressed by multiple strand stressing to final load by pulling to elongation and checking against the jack load. The required elongation shall control the tensioning. The actual jack load shall agree within 5% of the computed elongation converted to load.

For uniform application of load to strands, the face of anchorage at final load must be in a plane parallel to its position under initial load. This shall be verified by measurement of movement on opposite sides of the anchorage and a check of its plumb position before and after application of the final load. During stressing, the anchorage shall be free to move without restraint.

### Draped Strand Stressing

Draped strands shall be tensioned by either of the following methods:

- Partial Stressing and Subsequent Strains:

This method applies when the strands are tensioned through a combination of applied jack loads and strand uplift. To verify the final force, a load cell shall be placed between the stressing anchorage and anchor chucks at the dead end on at least two draped strands. Other methods as approved by the Engineer may be used to verify the final force in the dead end. The partially draped strand shall be brought to an initial tension using a force in the range of 5 to 25% of the required final stressing force. After application of the initial force, reference marks for measuring elongation shall be established.

A precalculated jacking force shall then be applied and elongations measured on a minimum of four strands. The average measured elongation shall agree within 5% of the theoretical elongation for the strand force measured by jack load, or the factors contributing to the difference shall be identified and corrected prior to proceeding. The load indicated by the jacking system shall control the tensioning for the precalculated load.

The required final force shall be obtained by raising the strand simultaneously at all pickup points or in an approved sequence as shown on the shop drawings. On each different bed set-up, after deflecting the strands to their final position, the final force shall be checked on two strands at the dead end of the bed. If the load is below the required stressing force by more than 5%, it shall be adjusted to the final load.

- Final Stressing in Draped Position:

When the final stressing is performed in the draped position, the tensioning load shall be applied in two increments with the tendons being held in their draped positions. To verify the final force, a load cell shall be placed between the stressing anchorage and anchor chucks at the dead end on at least two draped strands. Other methods as approved by the Engineer may be used to verify the final force at the dead end. Each strand shall be brought to an initial tension of 5 to 25% of the final load prior to the application of the required final load.

After application of the initial load, reference marks for measuring elongation shall be established. The strands shall then be stressed to final load and the elongation measured. The load indicated by the jacking system shall control the tensioning for the initial and final loads.

The measured elongation shall agree within 5% of the theoretical elongation for the strand force measured by jack load, or the factors contributing to the difference shall be identified and corrected prior to proceeding.

When the jacking is performed at one end of the bed, the applied load shall be checked on two strands at the other end of the bed. If the load on the end opposite the jacking end is below the required value by more than 5%, the load shall be adjusted to the required final load.

### Wire Breakage

Wire breakage shall be limited to 2% of the total area of the strands in any structure and verification that breakage is not indicative of a more extensive distress condition, otherwise all stranding shall be rejected.

Individual strands with more than one wire failure shall be replaced.

### Strand Chucks and Splice Chucks

Chucks shall be used as complete units and shall be cleaned, inspected and lubricated between each use. Care should be taken to avoid improper fit and seating of wedges on the strands. The wedges and housing shall be compatible and made for the specific type and size of steel being used.

Wedges that become worn, cracked, deformed, or that allow slippage in excess of 1 cm shall not be used and shall be discarded. Only components from the same manufacturer shall be used to make up chucks and to provide proper wedge fit.

One patented splice per strand will be permitted subject to the following:

- Splices shall be located outside the concrete structures

- Strands which are being spliced shall have the "lay" or "twist" in the same direction.

### Cleanliness of Prestressing Steel

After stressing operations are complete, the prestressing steel shall be inspected for any evidence of contamination. Steel shall be free of deleterious materials such as grease, oil, wax, dirt, paint (except that used for marking identification) or other similar contaminants. Any contaminants detected shall be removed from the steel before proceeding with fabrication activities.

## Detensioning

Transfer of prestress shall not be carried out until the concrete has attained the specified transfer strength as proved by standard test cylinders, manufactured and cured for this purpose, however not less than 30 MPa.

The Contractor shall verify the release strength by compressive strength cylinder tests or other approved means no later than 24 hours after casting, and every 24 hours thereafter until release strength is obtained. For structures cured using accelerated curing, the prestressing force shall be released immediately after terminating curing. For structures cured using methods other than accelerated curing, the prestressing force shall be released within 24 hours of verifying release strength by compressive strength cylinder breaks, or other approved strength gain monitoring system, unless the required time for release occurs on a weekend or holiday.

Structures cured using methods other than accelerated curing, but which induce heat into the concrete shall be detensioned before a concrete temperature drop occurs of more than 30°C, from the concrete temperature at the time release strength was verified. The Contractor shall provide means and methods of insuring compliance with the above requirements of monitoring concrete temperature.

### Method of Stress Transfer

In all detensioning operations, the prestressing forces must be kept nearly symmetrical and must be applied in a manner that will minimise sudden shock or loading. Forms, ties, inserts, or other devices that would restrict longitudinal movement of the structures along the bed shall be removed or loosened. Hold downs of draped strand profiles shall be removed at the appropriate time for the specific structure.

Hold-downs for structures with draped strands shall be released prior to releasing the stresses at the anchorages, unless the hold downs are free to move longitudinally. If the latter is the case, the hold-downs may be released subsequent to release of the anchorage stress.

Dormant strands shall be cut prior to releasing any fully tensioned strands. Fully bonded strands shall be released next, followed progressively by strands having the minimum length of tubular sheathing through to those strands having the maximum length of tubular sheathing. The Contractor may propose alternative detensioning patterns to suit his particular operation. The method of the stress transfer to be used by the Contractor shall be specified either in construction submittals or shop drawings to be submitted to the Engineer for approval.

Prestressing forces shall be transferred to the concrete by multiple strand release, as follows:

All the strands shall be detensioned simultaneously by hydraulic dejacking or by other approved mechanical means. Flame releasing shall not be allowed. The total force is taken from the header by the jack, and then released gradually. The overstress required to loosen the anchoring devices at the header shall not exceed the force in the strand by 5%. Shock releases shall NOT be permitted; if tendons should fail suddenly, the Engineer may order load testing of any structures so affected. Special care shall be taken to ensure that the force in any tendon never exceeds 85% of the specified ultimate tensile strength of the tendon.

### Trimming Strands

After the transfer of prestress, severed tendons shall be trimmed flush with the end of the structure using abrasive disc grinders without damaging the concrete. Electric arc welders or oxygen flame trimming shall not be used.

After trimming and within 12 hours of detensioning, the ends of the tendons and the area immediately adjacent to the tendons shall be painted with an epoxy compound to provide a film thickness at least 0.3 mm dry or 0.6 mm wet. A minimum of two coats shall be applied.

## Post-Tensioning Stressing

Before any stressing operation the Contractor shall ensure that sheathings are clear of obstructions and allow free movement of the tendons. The Contractor shall prevent damage to the sheaths caused by any water freezing in the sheaths prior to grouting.

At least 1 week prior to stressing the Contractor shall provide detailed calculations of extensions corresponding to the required tension force at the anchorage, as shown on the drawings, to the Engineer. These calculations shall be based on the secant modulus determined from the test certificates or test samples and the expected jack and anchorage friction.

Furthermore, the Contractor shall submit to the Engineer a stressing procedure plan for approval, stating all relevant stressing steps and stressing control measures like:

- Sequence of stressing;

- Bar protrusion at the anchorage before and after stressing to evaluate the effective elongation; - Counter control for elongation during stressing operation; - Gauge control for hydraulic pressure.

Particular attention shall be given to minimisation of seating losses.

Stressing shall not be carried out without 24 hours prior notice being given to the Engineer. The stressing operation shall be performed under the supervision of a competent person provided by the Contractor.

### Stressing Procedure

- The stressing operation shall be performed in accordance with best practice applicable to the particular system approved;

- The sequence of stressing shall be as shown in the stressing procedure plan and in the drawings;

- No tendons shall be stressed if they are at a temperature of 0oC or below. In addition, the air temperature must be 5oC or above;

- The tensioning force applied to any tendon shall be determined by direct measurement of the jack gauge reading and shall be checked by measurement of the elongation of the tendon;

- Under no circumstances shall the maximum jacking force exceed the rated capacity of the jacking equipment used or 85% of the specified minimum ultimate tensile strength of the tendon, whichever is the lesser;

- True extension of the tendon shall be considered to be the sum of the measured extension and the zero corrected value of the extension obtained by application of the initial tension minus the amount of pull-in at anchorages and anchorage movements (if any);

- Whenever the actual extension and the calculated extension differ by more than 5% the Engineer shall be notified;

- No structural structure shall be left partly stressed unless the drawings require the structure to be stressed in stages.

- After taking up the slack, the tendon shall be accurately marked at both ends and elongations or drawing measured from these markings;

- Where tendons consist of a number of individual components each component shall be marked so that any slip may be observed;

- Where one or more components or tendons of a group stressed together slips during stressing operations, a compensating increase in the elongation of the remaining tendons of the group will be permitted provided that the jacking force does not exceed 85% of the minimum ultimate tensile strength of the remaining tendons;

- In the case of a tendon breaking or slipping after tensioning, so that the allowable tolerance specified above is exceeded, the tendon shall be released, replaced and re-stressed.

### Tensioning with one Jack

Unless otherwise stated on the Drawings, the tendons may be tensioned by means of one jack only. Tendons shall be marked for measurement of elongation at both the jacking end and the anchored end, and allowance shall be made for any draw-in of the tendon at the anchored end.

## Grouting

The durability of post-tensioned construction depends to a great degree on the success of the grouting operation considering that the hardened cement grout provides bond between concrete and tensile element as well as primary long-term corrosion protection (alkaline medium) for the prestressing steel. Advanced methods such as pressure grouting, post-grouting and vacuum grouting shall be applied preferably.

Tendons shall be grouted as soon as practicable, but not more than 48 hours after fully stressing the tendons.

### Preparation of the Duct before Grouting

- Anchorages shall be sealed to prevent loss of grout;

- The grouting duct shall be water tested for blockages and shall be capable of sustaining a pressure of at least 1 MPa without leakage. Any leaks shall be plugged;

- All surplus water shall be removed from the grouting ducts prior to grouting.

### Grout Materials and Properties

Grout for bonded tendons shall consist of a mixture of Portland cement and water unless the gross inside cross-sectional area of the sheath exceeds 4 times the tendon cross-sectional area, in which case a fine aggregate may be added to the mixture.

- Fly ash and pozzolanic mineral admixtures may be added at a ratio not to exceed 0.3 by weight of cement;

- Mineral admixtures shall conform to relevant standards;

- Approved shrinkage-compensating material, which is well dispersed through the other admixture, may be used to obtain 5 to 10% unrestrained expansion of the grout;

- Admixtures containing more than trace amounts of chlorides, fluorides, zinc or nitrates shall not be used;

- Fine aggregate, if used, shall conform to relevant standard;

- Grout shall achieve a minimum compressive strength of 17 MPa at 7 days and 34 MPa at 28 days.

- 2 cubes shall be taken from each day's grout material. Test cubes shall be made and cured;

- Grout shall have a consistency that will facilitate placement; - Water content shall be the minimum necessary for proper placement; - Water-cement ratio shall not exceed 0.45 by weight.

The bleeding of the grout shall not exceed 2% of the volume 3 hours after mixing and shall not exceed 4% of the volume at any time. All separated water shall be absorbed within 24 hours. Bleeding shall be measured in a metal or glass cylinder with an internal diameter of approximately 100 mm and with a height of grout of approximately 100 mm. During the test the container shall be covered to prevent evaporation. At least one bleeding test shall be carried out for each day's grouting.

### Mixing and Pumping Equipment

Grout shall be mixed until a uniform colloidal consistency is produced. Mixing by hand, or by a tumbling action, will not be permitted.

Grout shall be mixed and pumped into place not more than 1 hour after the addition of cement to the mix. Pumps shall be capable of continuous operation with little pressure variation, and shall have a system for recirculating the grout whilst actual grouting is not in progress. Pumps shall be fitted with a pressure gauge and shall be capable of delivery at pressures up to 1 MPa. The use of compressed air will not be permitted.

All equipment, especially piping, shall be maintained in a clean condition.

### Grouting

Grouting shall not be carried out while the air temperature is below 5°C, or while the shade temperature exceeds 32°C. A continuous, steady flow of grout shall be maintained until the duct is completely filled and pure grout issues from all vents and all entrapped air has been expelled.

The vents shall be progressively closed as required to ensure the complete filling of the duct. The grout pressure shall then be held at 0.7 MPa for 10 minutes. During this period bleed water shall be bled from the crest vents at 5 minutes and just prior to the end of the period. After this 10-minute period the inlet vent shall be closed in such a way as to hold the pressure in the duct at 0.7 MPa. If any leaks occur such that the pressure over the length of the duct cannot be maintained at 0.7 MPa, the grouting shall be stopped, the duct flushed clean with water and the leakage plugged before continuing with grouting. The quantity of materials shall be such as to enable the completion of grouting of whole duct(s) (allowing 10% wastage) without interruption.

All vents and ends shall be kept closed until final setting of the grout has taken place.

All duct openings shall be inspected two or 3 days after grouting and topped up if necessary.

In the event of difficulties occurring due to a blockage which prevents a duct from being completely filled with grout the grouting shall be stopped, the duct flushed clean with water and the blockage removed before continuing with grouting.

### Trimming

After the grout has hardened sufficiently any vents or grouting tubes which extend to the surface of the concrete shall be cut off 25 mm below the concrete surface and the recess plugged with an approved concrete repair mortar.

Tendons shall not be cut until 5 days after grouting. The tendons shall be cut back to give a minimum of 25 mm cover on post tensioned structures.

Before concreting, the recesses shall be roughened lightly by abrasive blasting and a "wet to dry" epoxy shall be applied to the whole of the end faces in accordance with the manufacturer's instructions.

# PRECAST CONCRETE UNITS

## General

Precast concrete units both reinforced and not reinforced shall comply with the requirements of the Specification where applicable.

Precast concrete units shall be manufactured either on the Site or in a concrete factory approved by the Engineer.

All precast concrete units shall have the date of casting and identification number engraved on them before the concrete is fully hardened. Any undated units will be liable to be rejected by the Engineer. The Contractor shall take all measures concerning the curing and protection of the units after fabrication. Transportation of the units to the Site shall be permitted only on one of the following conditions:

- 28 days after fabrication, or

- After the required compressive strength has been reached.

Where the installation of precast concrete units in any particular structure is such that the faces of the units are to be left exposed either internally or externally, the exposed surfaces of the units as finished shall be uniform in color and in texture. All cement, aggregates and other materials used in the manufacture of the units shall be obtained from the same approved sources throughout the period of manufacture.

Concrete for precast units shall be placed and compacted by methods approved by the Engineer.

## Concrete Quality and Tests on Concrete

The concrete used in the manufacture of precast concrete units shall comply in every respect with the following standards (but shall not be limited to)::

| - SRPS EN 1916 | Concrete pipes and fittings, unreinforced, steel fibre and reinforced |
| --- | --- |
| - SRPS EN 1916:2007/AC:2011 | Concrete pipes and fittings, unreinforced, steel fibre and reinforced |
| - SRPS EN 12629 | Machines for the manufacture of constructional products from concrete and calcium-silicate – Safety |
| - SRPS EN 1168 | Precast concrete products - Hollow core slabs |
| - SRPS EN 12794 | Precast concrete products - Foundation piles |
| - SRPS EN 12839 | Precast concrete products - Elements for fences |
| - SRPS EN 12843 | Precast concrete products - Masts and poles |
| - SRPS EN 13224 | Precast concrete products - Ribbed floor elements |
| - SRPS EN 13225 | Precast concrete products - Linear structural elements |
| - SRPS EN 13693 | Precast concrete products - Special roof elements |
| - SRPS EN 13747 | Precast concrete products - Floor plates for floor systems |
| - SRPS EN 14844 | Precast concrete products - Box culverts |
| - SRPS EN 14843 | Precast concrete products - Stairs |
| - SRPS EN 14991 | Precast concrete products - Foundation elements |
| - SRPS EN 14992 | Precast concrete products - Wall elements |
| - SRPS EN 1917 | Concrete manholes and inspection chambers, unreinforced, steel fiber and reinforced |
| - SRPS EN 1338 | Concrete paving blocks - Requirements and test methods |
| - SRPS EN 1339 | Concrete paving flags - Requirements and test methods |

The design, mixing, testing, curing and quality control of the concrete used in precast units shall be in accordance with Paragraph “Concrete”.

Shuttering and concrete finishes shall comply with Paragraph “Shuttering and Concrete Finishes”.

## Cast-in Parts

The cast-in parts, such as lifting lugs, fasteners, jointing materials supporting structures, etc. shall be fixed in the positions as shown on the working drawings. Cast-in parts shall be free from rust, dirt or grease and shall be properly stored before using.

## Transport, Storage and Erection

At all stages and until completion of the Works, precast units shall be adequately protected to preserve all permanently exposed surfaces and arises. The protection shall not mark or otherwise disfigure the concrete.

Transportation, storage and erection of the precast concrete units shall be done carefully and in such way as to avoid any damage and to keep the surfaces of the units free from dirt or other unwanted marks. Loading and unloading, storage and erection of the precast concrete units at the Site shall be carried out by skilled labour and under supervision of a competent supervisor.

Any precast concrete unit which is found to be cracked, damaged or otherwise inferior in quality either before or after erection shall be rejected and shall be replaced by the Contractor.

## Installation of Precast Concrete

All precast concrete units shall be laid, bedded, jointed and fixed in accordance with the lines, levels and other details shown on the approved working drawings.

Dry-pack mortar where necessary shall be used for jointing or packing as specified in Paragraph “Dry Pack Mortar”. The mortar shall be placed and packed in stages where possible from both sides of the space being filled using a hardwood stick hammered until the mortar is thoroughly compacted.

## Manufacturing in a Factory

Precast concrete units may be manufactured in a factory approved by the Engineer and which is off the Site. If the units are to be made in a concrete factory, then the Contractor shall give the Engineer full information, in advance concerning the name and address of the factory, details of the probable date of commencement of manufacture. The Contractor shall make the necessary arrangements for the Engineer to inspect the factory during working hours.

## Work Programme and Method Statement

The Contractor shall submit to the Engineer for his approval, the Work Programme and Method Statement giving full details of his proposed method of carrying out all operations connected with the manufacture and erection of precast concrete units, which shall include the following:

- Period required to produce the drawings and detailed calculations;  Dates of commencement of manufacturing of the concrete units.

- Dates of delivery to Site with the Specification for erection;

- Sequence of erection and the period required for Site erection works;

- A description of the types of casting bed, mould and shuttering for the various types of members;

- Procedure for reinforcing, concrete casting and method of curing the concrete;

- Procedure for transporting, handling, hoisting and placing of each type of precast concrete unit;

- The necessary strength of in situ cast concrete before starting site erection works;

- The design, manufacturing and mounting details to adapt the in-situ cast concrete to the assembly; and

- Particulars of temporary supports as deemed necessary to ensure adequate stability during erection and to sustain the effects of construction loads, wind loads or other transient loads.

No commencement of works shall be permitted until the programme and method statement have been approved by the Engineer.

# CONNECTIONS TO CONCRETE STRUCTURES, TEMPORARY HOLES AND OPENINGS

## General

All connections to concrete structures, temporary holes and openings in structures shall be made in accordance with the drawings and/or to the directions of the Engineer.

All steel constructions and other items to be cast in, such as anchor bolts, steel frames, sockets, pipes, strips, water-stops of rubber, etc. shall be fixed and cast in by the Contractor in accordance with the approved working drawings.

The Contractor shall also provide templates and other supplementary means for the correct positioning of the constructions and items as mentioned above.

The Contractor is to ensure that all of the constructions and items as mentioned above are on Site in time in order to avoid interruptions during the execution of concrete works. If recesses are provided, these shall be sufficiently larger in size than the dimensions of the construction or items to be cast in.

## Building-in Pipes and other Items

Pipes and other items passing through concrete structures shall wherever practicable be built into the structure as work proceeds, having been installed and connected to the remainder of the system to ensure proper fit prior to the start of any concreting.

Before placing concrete all bolts, pipes or conduits or any other fixtures which are to be built in shall be fixed in their correct positions, and cores and other devices for forming the holes shall be held fast by fixing to the formwork or otherwise. Holes shall not be cut in any concrete without prior approval of the Engineer in writing.

When that procedure cannot be adopted, holes or openings of suitable dimensions shall be formed for such items to allow them to be built in later along with or after installation of the remainder of the system. Such holes or opening shall be of size and shape sufficient to permit proper placing and companion of concrete or grout. The surfaces of the holes or openings shall be treated as construction joints.

All items to be built-in shall be securely supported in their correct position to prevent movement or damage during building in. In particular, any pipe with flanged joints shall not be concreted in until its accurate fit with other pipework has been checked and it has been secured in position.

Concrete used for building-in shall be of the same Class as the surrounding concrete, except that the mix shall also incorporate an approved expanding additive used with due regard to the manufacturer’s instructions.

Cement sand mortar or cement grout used for this purpose shall also incorporate an expanding additive. Concrete, mortar and grout shall be placed and compacted by methods which will avoid moving or damaging built-in items.

## Cutting or Displacement of Reinforcement

Reinforcement shall not be cut bent or displaced to facilitate building in without the Engineer’s approval. Where reinforcement is cut or displaced to facilitate the formation of holes or openings, the Contractor shall provide and fix additional reinforcement steel as required and approved by the Engineer to transfer the stresses from one side of the hole, opening or recess to the other.

Cutting or displacement of reinforcement shall only be permitted after the approval and inspection by the Engineer.

## Cleaning

Before filling or grouting, the holes and openings shall be roughed and cleaned to remove dust or other impurities. The openings and holes shall be moistened with clean water before filling or grouting. The threads of anchor bolts and other items shall be cleaned and greased immediately after filling or grouting.

## Grouting in Narrow Spaces

In the event of the space between the fixture or unit to be cast in and the adjacent concrete being less than or equal to 25 mm, the grouting shall compose of one part cement and two parts of sand with an approved expanding additive.

## Joint between Old and New Concrete

Where new concrete is joined with old or existing concrete, the Contractor shall cut the old concrete to form a straight surface. The joint shall be considered as a construction joint and treated with a material approved by the Engineer, prior to placing the new concrete.

## Grouting under Hand-railings

The grouting under hand-railings shall be executed with a synthetic resin mortar based on epoxy and to be approved by the Engineer.

# COATINGS ON CONCRETE SURFACES

## General

Bituminous coatings shall be applied to concrete structures for outside surfaces in order to protect tile concrete against aggressive effects of saline groundwater or other unwanted matters. Generally, protective coatings shall be applied to surfaces of concrete structures which are underground and/or in contact with groundwater.

The Contractor shall supply, deliver and apply all paints and protective coatings necessary. The type of coating to be used shall be bituminous, or other appropriate type chosen with the approval of the Engineer.

All priming-coats and undercoats shall be obtained from the same manufacturer and shall be the type of primer and undercoat recommended by the manufacturer for that particular paint or bitumen.

All paints and bituminous coatings shall be applied strictly according to the instructions of the manufacturer. All the paints shall be delivered to the Site(s) in sealed containers with the manufacturer’s name clearly shown. All coatings shall be applied by skilled labour under supervision of a competent foreman and to the satisfaction of the Engineer. No bituminous coatings shall be applied until the concrete has been cured in accordance with the period described in Paragraph A10 and prior approval of the Engineer has been obtained.

## Preparation of Surface

Before the application of any coating or primer, the surface of the concrete shall be thoroughly cleaned of all dirt, curing compound, dust and loose material and, where necessary, the surface shall be made good so that it is smooth and free from air or water holes. The surfaces of the concrete shall be dry before application of the first priming coat. No bituminous coating shall be applied until the Engineer has approved the preparatory work. The Contractor shall ensure that the required quantity of paints and coatings are on Site prior to commencing work so as to avoid interruptions during the execution of the work.

## Application

No paint, bituminous coating or primer shall be applied until the surface to be treated has been approved by the Engineer. After the application of a particular coat, the surface shall be approved by the Engineer before the next coat is applied.

### Priming Coat

The priming coat shall be applied and well brushed into the concrete and allowed to dry.

### First Coat

A heavy brush coat shall be applied in one direction and allowed to dry.

### Second and Subsequent Coats

A heavy brush coat shall be applied at right angle to the previous coat and allowed to dry.

### Number of coats

A minimum of two coats of bitumen excluding the priming coat shall be applied to concrete and other surfaces unless otherwise ordered by the Engineer.

### Holidays or Skips

The applying of any layer or coating shall be done in such a manner that no holidays or skips shall occur on any treated surface.

### Quantity and Curing

The application rate for the primer shall be 0.05 kg/m² and subsequent coats shall be not less than 0.5 kg/m² of surface. Each coat shall be thoroughly dry before applying a subsequent coat and shall be considered as dry when no staining occurs on a wet finger which is rubbed vigorously over the coating. No coating shall be immersed in water for at least seven days after it has been applied on the surface.

### Coating underside of Structures

The underside of concrete structures in water logged ground shall be protected by the application of bituminous coating to a layer of cement sand mortar of minimum thickness 25 millimeters.

The cement sand mortar shall be constructed on top of the blinding concrete and when it has been properly cured and hardened, the bituminous coating shall be applied as per Paragraph “Materials and Testing” prior to laying the structural concrete.

# STRUCTURAL STEELWORK

## Standards

All structures of steelwork shall be made in accordance with followings standards (but shall not be limited to):

- SRPS EN 1090-2- Execution of steel structures and aluminium structures - Part 2: Technical requirements for steel structures

- SRPS EN 1090-4- Execution of steel structures and aluminium structures - Part 4: Technical requirements for cold-formed structural steel elements and cold-formed structures for roof, ceiling, floor and wall applications

- SRPS EN 10365-Hot rolled steel channels, I and H sections - Dimensions and masses

- SRPS EN 287- 6- Qualification test of welders - Fusion welding - Part 6: Cast irons

- SRPS EN ISO 4063- Welding and allied processes - Nomenclature of processes and reference numbers

- SRPS EN ISO 2553 	Welding and allied processes – Symbolic representation on drawings – Welded joints

- SRPS EN ISO 5817-Welding - Fusion-welded joints in steel, nickel, titanium and their alloys (beam welding excluded) - Quality levels for imperfections

- SRPS EN ISO 9692-1-Welding and allied processes - Types of joint preparation - Part 1: Manual metal arc welding, gas-shielded metal arc welding, gas welding, TIG welding and beam welding of steels

- SRPS EN ISO 14373- Resistance welding - Procedure for spot welding of uncoated and coated low carbon steels

- SRPS EN ISO 16432-Resistance welding - Procedure for projection welding of uncoated and coated low carbon steels using embossed projection(s)

- SRPS EN ISO 16433-Resistance welding - Procedure for seam welding of uncoated and coated low carbon steels

- SRPS CEN ISO/TR  3834-6- Quality requirements for fusion welding of metallic materials - Part 6: Guidelines on implementing ISO 3834

- SRPS EN ISO 9712- Non-destructive testing - Qualification and certification of NDT personnel

- SRPS EN ISO 3452-1-Non-destructive testing - Penetrant testing - Part 1: General principles

- SRPS EN ISO 23279-Non-destructive testing of welds - Ultrasonic testing - Characterization of discontinuities in welds

- SRPS EN ISO 17636-Non-destructive testing of welds - Radiographic testing - Part 2: X- and gamma-ray techniques with digital detectors

- SRPS EN ISO 11666-Non-destructive testing of welds - Ultrasonic testing - Acceptance levels

- SRPS EN ISO 6507-1-Metallic materials - Vickers hardness test - Part 1: Test method

- SRPS EN ISO 6507-2-Metallic materials - Vickers hardness test - Part 2: Verification and calibration of testing machines

- SRPS EN ISO 6507-3-Metallic materials - Vickers hardness test - Part 3: Calibration of reference blocks

- SRPS EN ISO 6507-4-Metallic materials - Vickers hardness test - Part 4: Tables of hardness values

- SRPS EN ISO 9018-Destructive tests on welds in metallic materials - Tensile test on cruciform and lapped joints

- SRPS EN ISO 10447-Resistance welding - Testing of welds - Peel and chisel testing of resistance spot and projection welds

- SRPS EN ISO 12944	Part 1 ‘til Part 8 Paints and varnishes - Corrosion protection of steel structures by protective paint systems

- SRPS EN ISO 1461 	Hot dip galvanized coatings on fabricated iron and steel articles - Specifications and test methods

- SRPS EN ISO 2063 	Thermal spraying - Zinc, aluminum and their alloys

- SRPS EN 13144		Metallic and other inorganic coatings - Method for quantitative measurement of adhesion by tensile test

- SRPS ISO 12679-Thermal spraying - Recommendations for thermal spraying

- SRPS EN ISO 2063-1-Thermal spraying - Zinc, aluminium and their alloys - Part 1: Design considerations and quality requirements for corrosion protection system

- SRPS EN ISO 2063-2-Thermal spraying - Zinc, aluminium and their alloys - Part 2: Execution of corrosion protection systems

- SRPS EN ISO 14916	Thermal spraying - Determination of tensile adhesive strength

- SRPS EN ISO 8503-1-Preparation of steel substrates before application of paints and related products - Surface roughness characteristics of blast-cleaned steel substrates - Part 1: Specifications and definitions for ISO surface profile comparators for the assessment of abrasive blast-cleaned surfaces

- SRPS EN ISO 8503-2-Preparation of steel substrates before application of paints and related products - Surface roughness characteristics of blast-cleaned steel substrates - Part 2: Method for the grading of surface profile of abrasive blast-cleaned steel - Comparator procedure

- SRPS EN ISO 13920-Welding - General tolerances for welded constructions - Dimensions for lengths and angles - Shape and position

- SRPS EN ISO 10025-1-Hot rolled products of structural steels - Part 1: General technical delivery conditions

- SRPS EN ISO 10025-2-Hot rolled products of structural steels - Part 2: Technical delivery conditions for non-alloy structural steels

- SRPS EN  10210-1-Hot finished structural hollow sections of non-alloy and fine grain steels - Part 1: Technical delivery conditions

- SRPS EN  10210-2-Hot finished steel structural hollow sections - Part 2: Tolerances, dimensions and sectional properties

- SRPS EN  10219-1-Cold formed welded structural hollow sections of non-alloy and fine grain steels - Part 1: Technical delivery conditions

- SRPS EN  10219-2-Cold formed welded steel structural hollow sections - Part 2: Tolerances, dimensions and sectional properties

- SRPS EN  10204-Metallic products - Types of inspection documents

- SRPS EN  10027-1-Designation systems for steels - Part 1: Steel names

- SRPS EN  10027-2-Designation systems for steels - Part 2: Numerical system

- SRPS EN ISO 3269-Fasteners - Acceptance inspection

- SRPS EN 1337		Structural bearings

- SRPS EN ISO 683 	Heat-treatable steels, alloy steels and free-cutting steels

- SRPS EN 10034		Structural steel I and H sections - Tolerances on shape and dimensions

- SRPS EN 10149		Hot-rolled flat products made of high yield strength steels for cold forming

- SRPS EN 10051		Continuously hot-rolled strip and plate/sheet cut from wide strip of non-alloy and alloy steels - Tolerances on dimensions and shape

- SRPS EN 10055		Hot rolled steel equal flange tees with radiused root and toes - Dimensions and tolerances on shape and dimensions

- SRPS EN 10058		Hot rolled flat steel bars for general purposes - Dimensions and tolerances on shape and dimensions

- SRPS EN 10163		Delivery requirements for surface condition of hot-rolled steel plates, wide flats and sections

- SRPS EN 10067		Hot rolled bulb flats - Dimensions and tolerances on shape, dimensions and mass

- SRPS EN 10029	 	Hot rolled steel plates 3 mm thick or above - Tolerances on dimensions, shape and mass

Additional Materials for Welding

- SRPS EN ISO 14175	Welding consumables – Gases and gas mixtures for fusion welding and allied processes

- SRPS EN ISO 2560 	Welding consumables - Covered electrodes for manual metal arc welding of non-alloy and fine grain steels - Classification

- SRPS EN ISO 14341 	Welding consumables - Wire electrodes and weld deposits for gas shielded metal arc welding of non-alloy and fine grain steels - Classification

- SRPS EN ISO 14171 	Welding consumables

- SRPS EN ISO 18275 	Welding consumables - Covered electrodes for manual metal arc welding of high-strength steels

- SRPS EN ISO 17632 	Welding consumables - Tubular cored electrodes for gas shielded and non-gas shielded metal arc welding of non-alloy and fine grain steels

- SRPS EN ISO 544 	Welding consumables - Technical delivery conditions for filler materials and fluxes - Type of product, dimensions, tolerances and markings

- SRPS EN ISO 14174 	Welding consumables - Fluxes for submerged arc welding and electroslag welding

- SRPS EN ISO 636 	Welding consumables - Rods, wires and deposits for tungsten inert gas welding of non-alloy and fine-grain steels

- SRPS EN 12074 	 	Welding consumables - Quality requirements for manufacture, supply and distribution of consumables for welding and allied processes

- SRPS EN ISO 20378	Welding consumables - Rods for gas welding of non-alloy and creep resisting steels – Classification

- SRPS EN ISO 14343 	 Welding consumables - Wire electrodes, strip electrodes, wires and rods for arc welding of stainless and heat resisting steels – Classification

- SRPS EN 25184	 	 Straight resistance spot welding electrodes

- SRPS EN ISO 887	 Plain washers for metric bolts, screws and nuts for general purposes - General plan

- DIN 7989 	 	Washers for steel structures

- DIN 7990 	 	Hexagon bolts and nuts for steel structure

- SRPS EN ISO 4032 	 Hexagon regular nuts (style 1) - Product grades A and B

- SRPS ISO 8673 		Hexagon regular nuts (style 1) with metric fine pitch thread - Product grades A and B

- SRPS EN ISO 4034 	 Hexagon regular nuts (style 1) - Product grade C

- SRPS EN ISO 898 	 Mechanical properties of fasteners made of carbon steel and alloy steel

- SRPS EN ISO 3506-1 	Mechanical properties of corrosion-resistant stainless steel fasteners - Part 1: Bolts, screws and studs with specified grades and property classes

- SRPS EN ISO 3506-2	 Mechanical properties of corrosion-resistant stainless steel fasteners - Part 2: Nuts with specified grades and property classes

Additional Materials - Screws

- SRPS EN ISO 4034 	Hexagon regular nuts (style 1) - Product grade C

Quality Control of Welding Work

- SRPS EN ISO 5579 	Non-destructive testing – Radiographic testing of metallic materials using film and X- or gamma rays - Basic rules

- SRPS EN ISO 4136 	Destructive tests on welds in metallic materials - Transverse tensile test

- SRPS EN ISO 5173 	Destructive tests on welds in metallic materials - Bend tests

- SRPS EN ISO 17637 	Non-destructive testing of welds - Visual testing of fusion-welded joints

- SRPS EN ISO 23277 	Non-destructive testing of welds - Penetrant testing of welds - Acceptance levels

- SRPS EN ISO 17638 	Non-destructive testing of welds - Magnetic particle testing

- SRPS EN ISO 23278 	Non-destructive testing of welds - Magnetic particle testing of welds - Acceptance levels

- SRPS EN ISO 17636 	Non-destructive examination of welds - Radiographic examination of welded joints

- SRPS EN ISO 17643	Non-destructive examination of welds - Eddy current examination of welds by complex plane analysis

- SRPS EN ISO 11666 	Non-destructive testing of welds - Ultrasonic testing - Acceptance levels

- SRPS EN ISO 23279 	Non-destructive testing of welds - Ultrasonic testing - Characterization of indications in welds

- SRPS EN ISO 17640 	Non-destructive testing of welds - Ultrasonic testing - Techniques, testing levels, and assessment

- SRPS EN ISO 10893 	Non-destructive testing of steel tubes

- SRPS EN ISO 17635 	Non-destructive testing of welds - General rules for metallic materials

- DIN EN ISO 10675 	Non-destructive testing of welds - Acceptance levels for radiographic testing

Protection of Steel Structures against Corrosion

- SRPS EN ISO 12944	Part 1 ‘til Part 8 Paints and varnishes - Corrosion protection of steel structures by protective paint systems

- SRPS EN ISO 14916	Thermal spraying - Determination of tensile adhesive strength

- SRPS EN ISO 1461 	Hot dip galvanized coatings on fabricated iron and steel articles - Specifications and test methods

- SRPS EN ISO 2063 	Thermal spraying - Zinc, aluminum and their alloys

- SRPS EN 13144		Metallic and other inorganic coatings - Method for quantitative measurement of adhesion by tensile test

## Basic Steel Materials for Structure

An integral part of technical documentation must be a detailed specification of materials.

The Contractor shall comply with the latest version of the standards SRPS EN 10025-1 to -6, SRPS EN 10210 and SRPS EN 10219. Only hot-finished hollow sections profiles according to the standard SRPS EN 10210 shall be used as hollow parts for the supporting elements of the structure. Only steel with strength classes S235, S355 and S460 can be used.

Steel belonging to the JR and JO quality groups must not be used for fabrication of supporting structural elements.

For structural steel with a sheet thickness of up to 80 mm, the nominal values for the elastic limit and tensile strength according to table 3.1 of the SRPS EN 1993-1-1 standard shall be used. Values for larger sheet thicknesses can be found in the corresponding product standard.

The Contractor shall submit a certificate on the performed control 3.2 in accordance with SRPS EN 10204 for elements of the main building structure. For secondary structural elements, certificates of performed inspection 3.1 will be sufficient.

Testing costs must be included in the Contractor's offer. The tests schedule shall be submitted to the Engineer before appointing them, and the certificates before beginning of production.

Test certificates in accordance with SRPS EN 1090-2 are also required for secondary structural elements of the roof and other building structures.

Certificates on the performed control must be submitted to the Engineer before the beginning of production.

Certificates on performed control 3.1 and 3.2 of structural elements must include the following information:

- Name / Title (Certificate of control performed 3.2 in accordance with SRPS EN 10204),

- The body issuing a certificate,

- Employer,

- Manufacturer with information about the steel mill,

- Finished product,

- Material (type of steel),

- Standard with date of issue,

- Heat number,

- Sample number,

- Condition upon delivery,

- Dimensions of the metallurgical product,

- Dimensions check and visual inspection of external quality,

- Chemical composition – melting analysis (14 elements; C, Si, Mn, P, S, Al, N, Cr, Cu, Mo, Ni, Nb, Ti, V),

- CEV carbon equivalent,

- Tensile strength test results (tensile yield point, tensile strength, bursting pressure)

- Impact test results,

- Sulphur print, if necessity,

- Ultrasound test if necessary,

- If necessary, bending test of welded joints in accordance with SEP 1390 for nominal thicknesses over 30 mm,,

- Declaration of conformity using the CE mark by the manufacturer

- Manufacturer's statement regarding compliance with the requirements stipulated in the contract.

It may be necessary for the certificate of inspection 3.2 to contain other data, such as improved characteristics in terms of thickness (Z quality), suitability for the hot-dip galvanizing process, cold deformability, tensile strength and lateral impact energy

### Special Requirements

Mechanical and chemical properties of materials given in the relevant standard must be met for all the thicknesses from the ordering specification. The basic material must be weldable, resistant to brittle breaking. Such properties shall be verified by impact tenacity tests whereby values given in relevant standard should be met. Installation of double-skin sheet metals shall be forbidden. Double skin of sheet metals is registered by ultrasound testing.

Certificates for the basic steel materials must contain the following data: Number of the batch to which the assortment is related, standards and qualities mandatory according to the design documentation and prescribed actual values of chemical and mechanical characteristics of materials. Certificates in the form of statements that a material corresponds to the demanded quality shall not be allowed and must not be taken as evidence of the quality of the material.

### Takeover of Material

All the materials shall be qualitatively and quantitatively taken over in the rolling mill by the Contractor, including inspection of all surfaces and dimensions. Individual parts of the basic material can also be subsequently rejected, despite the fact that the material has previously been accepted in the rolling mill if, during the fabrication of the structure in the workshop, the Contractor establishes that the delivered parts of materials have flaws or inadequate dimensions. The supplier of the materials shall be obliged to deliver replacement for the rejected materials within the shortest possible time, without the right to remuneration. All the materials in the rolling mill must be marked by a color with regard to dimensions and must have stamped batch number and item number from the ordering specification.

## Construction procedure

Auxiliary elements for assembly and transport, e.g. assembly openings, partitions and assembly elements shall be subject to Engineer’s approval. They must be indicated on the construction drawings and checked through structural analysis for deformation, weakening of the cross-section and other effects. They may be retained in the structure only with the Engineer’s consent of the Engineer.

In the event of water penetration, it must be removed before the openings are finally closed.

## Welding

The Contractor shall, within the bid, provide valid certificates in accordance with SRPS EN 1090 (welding certificate and EC certificate), for works execution on the steel structure in the factory and on the site, provide all the necessary evidence that its skilled labor and equipment to be engaged in construction have valid certificates issued by one of authorized Institutes. The entire equipment that is to be used in works on fabrication, assembly and quality control of steel structure must be in good operating condition and the same shall be subject to inspection by the Engineer.

Technologies for carrying out of welding work, used materials, and control procedures must be in compliance with the previously specified standards.

For welded structures under dynamic load, in principle, electrodes with a thick jacket of basic character and low content of hydrogen are recommended. Statically loaded welded structures may also be worked on using electrodes lined with medium and thick jacket of acid character. For semi-automatic welding of elements of a structure, wire EPP2 (or Sinkord) shall be applied protected by imported powder UM 50 or a domestic one of adequate quality.

If rolled profiles are butt welded along the height of the entire profile, bearing capacity of thus welded girder exposed to bending shall be reduced by 50% of the nominal bearing capacity. It is recommended to the Contractor to cover such butt welded profiles by splice plates of adequate bearing capacity and to weld them to the main profile by fillet welds. In such a case, bearing capacity of a girder extended with splice plates can be taken as 100%.

### Quality Control of Welded Joints

Quality control of welded joints shall be exercised by the Contractor in cooperation with engineers of one of authorized Institutes.

The contractor shall perform welding in accordance with the standard SRPS EN ISO 15613 or SRPS EN ISO 15614-1.

In the workshop and at the site, a special archive of documents related to the control of quality of welded joints must be formed. The archive must be furnished with a table for review of films and a catalogue IIW with film check samples. The final assessment of the quality of every joint shall be provided by the Engineer.

Fillet welds must be executed in dimensions in accordance with the design documentation. The Contractor shall be obliged to control all fillet welds for dimensions and quality. Qualitative control can be exercised visually using magnifying glasses or "Difuterm" procedure by penetrating paints. Control of dimensions shall be exercised using special stencils. Results of control must be stated in writing.

Butt seams shall be executed according to the valid technical regulations in three qualities: special, quality I and quality II. As a rule, quality control of butt seams is exercised by radiographic procedure. Allowable evaluations of seams range between 1 and 3. Seams graded with mark 4 must be repaired, seams marked 5 are rejected as unsuitable. Results of control must be included in a separate study.

## Screws

Minimum 21 days prior to commencement of relevant work, the Contractor shall provide all the necessary evidence that its equipment has valid certificate issued by one of authorized Institutes. The entire equipment to be used in work on fabrication, assembly and quality control of a steel structure, must be in good operating condition and the same shall be subject to inspection by the Engineer. The technology for work on joints with VV screws and screws of a lower class of hardness, used materials and quality control must be in compliance with the previously specified standards.

## Fabrication of structure in the workshop

Fabrication of a steel structure may be entrusted only to a qualified Contractor of such work in accordance with SRPS EN 1090 (welding certificate and EC certificate). Contractor within the Bid, must prove its eligibility by a list of successfully completed similar works, a list of available tools and machines, and a list of skilled staff.

The Contractor shall carry out all the works in compliance with the approved design documentation, with comprehensive and daily control by the Engineer. The Contractor shall elaborate the design documentation according to its technology, and fully in accordance with prescribed requirements - Detailed Drawings. In such elaboration, amendments of the designed concept and stipulated details of structure must not be made.

### Storage of Materials

Materials for certain items, which have not been taken over in the rolling mill by the Contractor, must be marked by a color and must have a stamped batch number. It shall only be possible to establish a connection between the ordered materials and certificates through such marks.

The Contractor shall carefully unload and place in a storage area the arrived steel materials. When handling them, materials must not be thrown or held at edges without the previous protection of the same. All possible damages shall be judged by the Engineer: as to whether they can be tolerated or a piece damaged by the Contractor should be replaced at the cost of the Contractor. Stacked materials in storage must be sufficiently lifted off the ground. Marks on materials must remain visible.

### Actions Preceding Fabrication of Structure

Prior to commencement of fabrication of a steel structure, in parallel with the preparation of the workshop documentation, the Contractor shall prepare and submit to the Engineer for approval the following documents/studies:

- Dynamic plan of production, control, and delivery

- Welding technology

- Technology of execution of locksmith’s work

- Technology of test assembly (if envisaged in the design)

- Control plan with special reference to inter-phase and phase control of welded assemblies, or topographical control at test assembly

- Technology of carrying out of the work on anti-corrosion protection.

- Plan of packing and method of transportation.

The planned welding technology for complicated assemblies with increased scope of welding must be proven on test pieces. Thereby the tendency of materials to change the structure under the impact of welding temperature should be checked as well as the magnitude of deformations due to welding. Based on such tests, certain pre-heating temperatures shall be empirically verified for various thicknesses and qualities of materials as well as the regime of cooling of welded joints and the magnitude of predeformations.

The space in the workshop where test assembly shall take place (if required by the technical documentation of the design) must be specially arranged – all the supports of individual elements of a structure in test assembly must have such foundation that excludes settlement. When preparing the above study, full cooperation must be established as well as adherence to the design of assembly.

### Workshop Fabrication

The Contractor must not install in the structure any materials without having an adequate certificate. When cutting certain items from the procured larger dimension of metal sheets, concerning all the items that are to form main load-bearing parts of the structure, the stamped batch number and the number of ordering item must actually be transferred to the individual items. It must be evident in the workshop diary of the Contractor what items have been cut from one ordering item.

All the records of the materials, starting from procurement to installation, must be duly kept and submitted as document when delivering the structure. The structure must not be accepted without such a document.

When making the structure in the workshop, the Contractor must meet the requirements of the law, regulations, and standards and other technical norms specified within these requirements, which apply to the type of structure that is being fabricated.

In addition to the Contractor's internal quality control, the Engineer shall perform the additional quality control of steel structures and corrosion protection in the factory and on the site.

The Engineer has to be, in a timely manner, informed on the production deadlines, so that inspection of current production and final inspection of steel components can be carried out before loading them.

Before delivering parts of the structure to the site, the Contractor shall submit a manufacturer's declaration of performance. The submitted declaration shall confirm compliance with main technical regulations and compliance with construction documentation. It shall be confirmed that:

- there is compliance with the applicable regulation,

- the production has been carried out in accordance with the approved construction plans,

- there are test certificates for all materials,

- the weld tests have been performed in accordance with the weld test schedule and the results have been recorded in accordance with the requirements,

- the corrosion protection has been performed in a professional manner and in accordance with relevant standards, and recorded as part of internal quality control

The Declaration of Performance shall be a prerequisite for putting into operation by the Engineer.

Structures shall be made per exact dimensions. Tolerances of various structural elements, tools and construction auxiliary elements must be harmonized so that quality and functionality requirements are guaranteed during construction and after the completion of the works. Geometric deviations must not exceed the limit values indicated in SRPS EN 1090-2 for "geometric" or "additional" tolerances. "Special" tolerances can also be defined with the Engineer's consent, which shall be taken into account during construction and mathematical verification. Compliance with the permissible values shall be recorded by on-site measurement. The scope, nature and date of measurements shall be subject to agreement with the Engineer. The results shall be presented and compared with the permissible values. Main deviations must be clearly indicated. Records of measurements and estimates shall be submitted to the Engineer in accordance with the given schedule. If it is determined that the permissible tolerances have been exceeded (non-conformity), then the deviation shall be rectified by taking appropriate measures or structural analysis shall prove that they are not harmful. If none of the above is possible, then the load-bearing capacity of the reinforcing structure shall be proven by adequate measures, for which it is necessary to obtain the Engineer’s permission.

In production, care must be taken to ensure the precision of the adjacent structural elements’ fitting in, through installation and/or geometric measurements of the same.

Elements That Are Particularly Stressed:

- Cut edges of lamina must be finished by grinding and edges chamfered.

- Welded elements must, after welding, have the designed shape and flat surfaces.

- Holes for screws must be exclusively drilled.

- Screw threads must not penetrate in the package of structural elements. Length of screws shall be ordered for every joint individually subject to the thickness of the package. The Contractor shall obligatorily produce the specification of the connecting materials. In case of screws that function exclusively by their tightening, only their length must be taken care of.

Assemblies assembled in the workshop must be executed within the tolerances that apply to the type of the structure being fabricated. The structure must be fabricated in such a way as to allow assembly without forced pulling.

### Acceptance of Structure in the Workshop

The Engineer shall withhold the right to inspect finished elements ready for acceptance and delivery only after the inspection is previously conducted by the control service of the Contractor and the report is made by it thereon. In the minutes of acceptance of a finished element, all the deviations from the designed dimensions shall be recorded and the list of the entire Contractor’s documentation shall be provided (certificates of materials, welders’ certificates, minutes and sketches of cutting of individual items from ordered sheet metals, findings of the Control of the Contractor, findings of the inspection by the Engineer, copies of the workshop diary).

Delivery of a finished structure from the workshop to the site may be made only after the Engineer ascertains that the structure has been fully fabricated in accordance with the approved documentation and valid regulations and standards and provided with supporting documentation. The Engineer shall give the permit for delivery of the structure in writing. The engineer of the Contractor in charge of assembly of the structure shall obligatorily be present at the acceptance of the structure in the workshop.

### Delivery of the Structure

The Contractor must mark steel structures with big marks: all the assemblies, extensions, and joints prior to the delivery of the structure. Such marks must correspond to the marks from the design documentation and shall serve for subsequent proper erection at the site.

## Erection of the structure

Erection of steel structures may be carried out only by a specialized organization, which must prove, within the Bid, its eligibility by a list of successfully completed similar jobs, a list of available tools and machines, and a list of skilled staff.

The Contractor shall carry out all the works according to the design documentation and the approved documentation prepared by themselves in line with prescribed requirements given in the point – Temporary Structures and in the point - Detailed Drawings, with the comprehensive and daily control by the Engineer. Based on the design documentation, the Contractor shall elaborate the plan of erection taking care thereby not to change the concept formulated in the design of the facility and stipulated phases of erection, to adhere to the workshop documentation, and to ensure stability of the structure in all its phases complying with all the valid rulebooks and standards.

Prior to the commencement of fabrication of steel structure in the workshop, the Contractor shall prepare the Final Design of Erection and submit it to the Engineer for approval.

Prior to the commencement of erection of the steel structure, the Contractor shall prepare and submit to the Engineer for approval the following documents:

- Dynamic plan of erection and anti-corrosion protection

- The Detailed Design of Erection

- Technology of welding in erection

- The design of geodetic staking out and monitoring of the facility in the course of erection 5. Control plan

6. Technology of carrying out of the work on anti-corrosion protection of the steel structure.

The structure delivered to the site must be placed on a dumpsite prepared in advance. When handling the steel structure, care must be taken not to damage it – tools especially adapted to the structure must be used to grip it. If the structure has a protective coating applied in the workshop or it is hot galvanized, special "canvas" strips must be used in handling it.

The erection plot must be equipped in such a way as to enable proper execution of all the planned joints with the full topographic control, as well as to enable unobstructed control by the Engineer.

During assembly of the structure, control must be exercised by measurements on several occasions as to whether the shape and position of the structure correspond to the drawings. Thereby deviations should be within the limits prescribed by Technical Regulations for Tolerance of Measures and Shapes in Loadbearing Steel Structures.

The erection technology must be selected in such a way as to hold an element of the structure in the course of carrying out of the welding work.

## Temporary scaffolding and construction aids

The Contractor shall design and construct scaffolding in accordance with the SRPS EN 12811 standard. Scaffolding must be at least in the load class 2 according to the SRPS EN 12811-1 standard.

## Protection against corrosion

The Contractor must:

- Ensure that protective measures are taken to avoid any corrosion or any deleterious effects caused by manufacturing, finishing, transportation, storage and installation of materials.

- Ensure full resistance to any corrosion for components that are secured or bolted to each other, paying particular attention to the surface damage caused by such bolting or securing.

- Ensure full resistance in repair of corrosion protection to cope with the Site cutting of components, especially at boundary and external conditions.

- Allow for protection against all corrosion arising from exposure to non-saline water, soil, high humidity, low or high temperatures, chemical acids and alkalis, abrasion and impact, fungi and bacteria.

- Particular care shall be taken with delivery and storage on Site, particularly if storage is prolonged. On no account shall materials or components be stored or used beyond the manufacturer's expiry date.

The Contractor must define the systems of anti-corrosion protection to be applied to certain surfaces of the steel structure and submit with them corresponding certificates issued by one of accredited Institutes.

The offered systems must be in line with the provisions of the detailed requirements for corrosion protection systems according to SRPS EN 1090-2.

The order, type, and technology of applying and method of control of coats of the systems of anticorrosion protection planned in the Bid must be contained in the corresponding studies. As a rule, preparation of the surface shall be made by a jet of abrasive. The degree of achieved cleanness of a surface shall be determined according to SIS 053900. After cleaning and dust collection, surfaces of steel elements must be protected either by a previous protection or immediately by the first prime coat, not later than within 8 hours. The degree of cleaning of areas within the meaning of Article 24 of the above Rulebook must meet the criterion 2 1/2 of SIS. Preparation, depending on the equipment in the workshop, can be made just before entry of materials in the workshop and upon completion of fabrication of the workshop assembly. After cleaning and dust collection, surfaces of steel elements must be protected either by previous protection or immediately by the first prime coat, not later than within 8 hours. When assembling/erecting the steel structure, care must be taken that the surfaces to be covered by splice plates previously also get the second prime coat, so that all the parts of assembled structure have the same degree of protection.

At the construction site, the Contractor must ensure optimal conditions for storage and application of selected coatings fully in compliance with the approved studies, submitted instructions of the Contractor and/or certificates of Institutes, for the offered anti-corrosion coatings. At the construction site, the Contractor must provide all the needed equipment and check samples for control.

The principal code colors shall be as follows:

| - Water | Blue |  |
| --- | --- | --- |
| - Wastewater and sludge | Green |  |
| - (Fuel) oil | Brown |  |
| - Gas | Yellow |  |

## Galvanising

If requested that part of steel construction should be hot-dip galvanized. The galvanising shall be carried out after all fabrication has been completed and approved by the Engineer. Metal components to be hot dip galvanised shall not be shot blasted.

The complete hot-dip galvanizing process shall comply with the EN ISO 1461 standard.

The elements, i.e. structures, must be prepared in accordance with the EN ISO 14713 standard.

The articles shall be thoroughly cleaned and pickled in dilute sulphuric acid or hydrochloric acid followed by rinsing in water and pickling in phosphoric acid. They shall be thoroughly washed, stoved and dipped in molten zinc and brushed so that the whole of the metal shall be evenly covered. The edges shall be clean and surfaces smooth and bright. The layer thickness shall be 80 m minimum. Generally, hot-dip galvanising shall comply with the requirements as specified in relevant standard.

Galvanised surfaces that are abraded or damaged shall be repaired by thoroughly wire brushing the damaged area and removing all loose and cracked coating, after which the cleaned area shall be given 2 coats of inorganic zinc rich epoxy paint.

# STEELWORK COATING SYSTEMS

## General

The coating systems for steelwork shall be as listed below and as detailed in the following sections.

The Contractor shall submit his painting programme together with the manufacturer's documentation for the Engineers approval.

The paint manufacturers’ instructions shall be followed closely, particularly regarding coat thicknesses, drying time, pre-treatment, etc.

The base coat shall be applied in the shop within four hours of sandblasting. The surfaces which shall not be affected by the welding operations shall be painted with an intermediary coat.

For painting on site, the following shall apply:

Welding zones and zones which have been damaged shall be carefully cleaned and made smooth as described above. After cleaning and smoothening, a base coat and an intermediary coat shall be applied. All surfaces shall receive two coats of finishing paint. The total thickness of paint shall be not less than 280 microns.

| System No | Application |
| --- | --- |
| 1 | Ferrous surfaces, including items of structural steelwork subject to atmospheric exposure and operating at up to 100 °C. |
| 2 | Not used. |
| 3 | Ferrous surfaces in contact with soil or water not specified to be zinc metal sprayed, galvanized, or mortar coated. |
| 4 | Ferrous surfaces within 100 mm of a site weld line, all ferrous surfaces encased in concrete, and for temporary protection to ferrous surfaces. |
| 5 | Ferrous surfaces subject to atmospheric exposure, not insulated, and subject to operating temperatures between 100 °C and 500 °C |
| 6 | Proprietary coating systems. |
| 7 | Internal surface of ferrous storage tanks, pipe ends receiving flange adaptors and flexible couplings and inside surfaces of socket joints. |
| 8 | Galvanising |

Coating thicknesses for liquid coatings are referred to throughout as minimum dry film thickness (m.d.f.t.).

## Coating System 1

Ferrous surfaces, including items of structural steelwork subject atmospheric exposure and operating at up to 100 °C

| 1 | Prior to blast cleaning, surface irregularities and surface contaminants shall be removed. |
| --- | --- |
| 2 | Blast clean surfaces to visual standard of Sa 2½ in accordance with SIS 05 5900 |
| 3 | Surface amplitude of between 50 and 75 microns shall be obtained. |
| 4 | Method of coating application, drying/curing conditions and over coating sequence shall be in accordance with coating manufacturer’s recommendations. |
| 5 | Ensure surface to be coated is free from dust, grit or foreign matter immediately prior to coating application. |
| 6 | Immediately prior to coating application ensure surfaces still have Sa 2 l/2 surface quality. |
| 7 | Coating thickness. |

| Primer | Undercoat | Intermediate | Finish Coat | Total Dry Film Thickness |
| --- | --- | --- | --- | --- |
| Zinc-rich 2-pack epoxy 50 microns m.d.f.t. | High-build 2-pack epoxy 100 microns m.d.f.t. | High-build 2-pack epoxy 100 microns m.d.f.t. | Polyurethane acrylic 40 microns m.d.f.t. | 290 microns m.d.f.t. |

## Coating System 3

Ferrous surfaces, except inside surfaces of water storage tanks, in contact with soil or water, not specified to be zinc metal sprayed, galvanized, or mortar coated.

| 1 | Prior to blast cleaning, surface irregularities and surface contaminants shall be removed. |
| --- | --- |
| 2 | Blast clean surfaces to visual standard of Sa 2½ in accordance with SIS 05 5900. |
| 3 | Surface amplitude of between 50 and 75 microns shall be obtained. |
| 4 | Method of coating application, dry/curing conditions and over coating sequence shall be in accordance with coating manufacturer’s recommendation. |
| 5 | Ensure surface to be coasted is free from dust, grit or foreign matter immediately prior to coating application. |
| 6 | Immediately prior to coating application ensure surfaces still have Sa 2½ surface quality. |
| 7 | Coating thickness. |
| 8 | Additional inspection requirements. |

| Finish Coat | Total Dry Film Thickness |
| --- | --- |
| Pure solvent-free polyurethane 1.5 mm m.d.f.t. | 1.5 mm m.d.f.t. |

The coating shall be compatible with the application of cathodic protection and cathodic disbandment test data shall be submitted by Contractor for Engineer’s approval. The use of a primer to improve cathodic disbandment characteristics may be acceptable subject to Engineer’s approval.

## Coating System 4

Ferrous surfaces within 100 mm of a site weld line, temporary protection for surfaces and all ferrous surfaces encased in concrete.

| 1 | Prior to blast cleaning, surface irregularities and surface contaminants shall be removed. |
| --- | --- |
| 2 | Blast clean surfaces to visual standard of Sa 2½ in accordance with SIS 05 5900. |
| 3 | Surface amplitude of between 25 and 50 microns shall be obtained. |
| 4 | Method of coating application, dry/curing conditions and over coating sequence shall be in accordance with coating manufacturer’s recommendation. |
| 5 | Ensure surface to be coated is free from dust, grit or foreign matter immediately prior to coating application. |
| 6 | Immediately prior to coating application, ensure surfaces still have Sa 2 ½ surface quality. |
| 7 | Coating thickness. |

| Coating | Total Dry Film Thickness |
| --- | --- |
| 2 – pack epoxy zinc phosphate primer | 25 to 50 microns m.d.f.t. |

## Coating System 5

Ferrous surfaces subject to atmospheric exposure, not insulated and subject to operating temperatures between 100 °C, and 500 °C.

| 1 | Prior to blast cleaning, surface irregularities and surface contaminants shall be removed. |
| --- | --- |
| 2 | Blast clean surfaces to visual standards of Sa 3 in accordance with SIS 05 5900. |
| 3 | Surface amplitude of between 75 and 115 microns shall be obtained. |
| 4 | Method of coating application by gas flame or electric arc process using aluminum wire. |
| 5 | Ensure surface to be coated is free from dust, grit or foreign matter immediately prior to coating application. |
| 6 | Immediately prior to coating application, ensure surfaces still have Sa 3 surface quality. |
| 7 | Coating thickness. |
| 8 | Apply sealing coat. |

| Coating | Sealer Coat |
| --- | --- |
| Aluminum metal spray 150 to 250 microns thick | Aluminum silicone, minimum thickness to achieve complete sealing and coverage |

## Coating System 6

Items of equipment which due to their use and/or complexity are not suitable for coating with any of the coating systems defined elsewhere in this Specification may, on the Engineer’s approval, be coated with Contractor’s standard heavy-duty coating system(s). In such circumstances, the Contractor shall submit full details of the proposed coating system(s) for review and approval by the Engineer prior to ordering. The Contractor’s submittal to the Engineer shall include but not necessarily be limited to the following:

- Proven suitability of the coating system for an aggressive salt laden environment.

- Contractor’s procedures and specification for substrate surface preparation, coating application and quality control.

- Coating manufacturer’s data sheets and recommendation for surface preparation and coating application.

- The m.d.f.t.’s for each coating application and for the total coating system.

## Coating System 7

Internal surfaces of ferrous storage tanks.

| 1 | Prior to blast cleaning, surface irregularities and surface contaminants shall be removed. |
| --- | --- |
| 2 | Blast clean surfaces to visual of Sa 2 ½ in accordance with SIS 05 5900 – 1967. |
| 3 | Surface amplitude of between 50 and 75 microns shall be obtained. |
| 4 | Method of coating application, drying/curing conditions and over coating sequence shall be in accordance with coating manufacturer’s recommendations. |
| 5 | Ensure surface to be coated is free from dust, grit or foreign matter immediately prior to coating application. |
| 6 | Immediately prior to coating application ensure surface still has Sa 2 ½ surface quality. |
| 7 | Coating thickness. |
| 8 | Additional inspection requirements. |

| Primer | Undercoat and Intermediate Coats | Finish Coat | Total Dry Film Thickness |
| --- | --- | --- | --- |
| 2-pack epoxy zinc phosphate 25 microns m.d.f.t. | High-build 2-pack epoxy 100 microns each m.d.t.f. | High-build e-pack epoxy 100 microns m.d.f.t. | 325 microns m.d.f.t. |

The Contractor shall submit to the Engineer test certificates from the proposed coating manufacturer to demonstrate compatibility of the coating system with the substances to be stored in the tank. Additionally, coating to be used in water storage tanks shall be compatible with the application of cathodic protection and cathodic disbandment test data shall be submitted by Contractor for Engineer’s approval.

## Coating System 8

Applicable standards are:

- SRPS EN ISO 2081 Metallic and other inorganic coatings -- Electroplated coatings of zinc with supplementary treatments on iron or steel

- SRPS EN ISO 2082 Metallic and other inorganic coatings -- Electroplated coatings of cadmium with supplementary treatments on iron or steel

Surfaces required to be hot dip galvanized are ladder, racks, cable trays, stair-treads, gratings, grilles, hand railing, bolts, nuts, washers and other miscellaneous carbon steel or low alloy steel items unless otherwise specified.

Other surfaces requiring galvanizing shall be as shown on drawings and in the Specifications.

Galvanising shall be carried out only after completion of all welding, drilling, grinding and other fabrication activities associated with the items to be galvanized. Steels to be galvanized shall not be susceptible to embrittling by the galvanising process.

Galvanising shall be in accordance with the relevant standard. The minimum zinc coating weight shall not be less than 610 gm/m² of surface area or, for threaded fasteners only, 305 gm/m² of surface area. The galvanized surfaces shall possess a uniform bright metallic sheen free from defects.

In special cases, and at the Engineer’s sole discretion, threaded fasteners may be zinc electro-plated and passivated in accordance with the relevant standards, class ‘A’. Steels possessing a minimum specified ultimate tensile strength of 100 kgs/mm² or greater shall be heat treated in accordance with the relevant standards prior to passivation.

Where galvanised ferrous metals are specified to be painted, the following shall be applied:

Preparations: 	Degrease

Abrade or pre-treatment etching primer

Primer:  	1 coat zinc chromate primer, 25–50 microns m.d.f.t.

Finishing: 	2 coats alkyd gloss finish, 50 microns m.d.f.t.

# MASONRY WORKS

## General

The Contractor shall carry out the works in accordance with the appropriate National end EN standards.

Before the material delivery, it is necessary to submit reports, quality proofs, certificates, and all required test results per regulations, to the Engineer for approval.

The tests shall be conducted in an independent accredited laboratory approved by the Engineer.

Additional tests shall be conducted if the material source changes

## Standards

Execution of masonry works and materials for execution shall be in accordance with, but not limited to, the following rulebooks and standards:

- Rulebook on technical standards for masonry walls, ("Official Gazette of the SFRY", no. 87/91)

- Rulebook on technical and other requirements for brick products made of clay and calcium-silicate bricks and blocks ("Official Gazette of SMNG" No. 53/05)

- Rulebook on technical requirements for clay masonry elements, calcium-silicate masonry elements and clay blocks for semi-prefabricated fine-ribbed ceilings ("Official Gazette of the RS", no. 90/19)

- SRPS EN 771- 1 Specification for masonry units - Part 1: Clay masonry units

- SRPS EN 10080-Steel for the reinforcement of concrete - Weldable reinforcing steel - General

- Rulebook on cement quality ("Official Gazette of RS", no. 34/13 and 44/14)

- SRPS B.C1.012-Cement - Delivery, packing and storage

- SRPS EN 459-1- Building lime - Part 1: Definitions, specifications and conformity criteria

- SRPS EN 13139- Aggregates for mortar

- SRPS EN 934-3- Admixtures for concrete, mortar and grout - Part 3: Admixtures for masonry mortar - Definitions, requirements, conformity and marking and labelling

- SRPS EN 1015-11- Methods of test for mortar for masonry - Part 11: Determination of flexural and compressive strength of hardened mortar

- SRPS EN 1015-12- Methods of test for mortar for masonry - Part 12: Determination of adhesive strength of hardened rendering and plastering mortars on substrates

- SRPS EN 1015-19-Methods of test for mortar for masonry - Part 19: Determination of water vapour permeability of hardened rendering and plastering mortars

- SRPS EN 998-1- Specification for mortar for masonry - Part 1: Rendering and plastering mortar

- SRPS EN 998-2- Specification for mortar for masonry - Part 2: Masonry mortar

## Masonry units

Masonry unit shall be made of clay or calcium silicate.

The quality of Masonry unit shall correspond to the above-listed relevant standards. Masonry unit shall be hard, sound, square and clean with sharp, well defined arises.

Strength test certificates performed on the basis of appropriate standards shall also be submitted on request of the Engineer.

## Mortar

### Sand

Sand shall be clean and sharp course grit, fresh water river or pit sand and shall be re-washed on site if the silt, loam or clay content exceeds the limits prescribed in the relevant standards. The sand shall be obtained from a source approved by the Engineer.

### Cement

Cement shall be Portland cement as specified in Paragraph “Concrete” and in accordance with the specified standards for masonry works. The source of cement is subject to the approval of the Engineer and shall not be changed without his prior approval.

### Hydrated lime

Hydrated lime, shall be according the relevant standards.

### Water

For the mixing of mortar and plaster the Contractor shall provide tap water, if not otherwise directed or approved by the Engineer.

### Mortar Mix

Masonry mortar for setting bricks shall be mixed in a specified ratio: cement: lime: sand. Cement shall be added to the mix in an amount compatible with workability. Mortar constituents shall be measured by volume using clean gauge boxes.

Mortar shall be mixed in a mechanically operated mortar mixer.

Mortar shall be used within 2 hours after discharge from the mixer at normal temperatures. No mortar shall be used after the initial set has taken place. Reconstitution of mortar will not be permitted.

## Workmanship

Workmanship has to be professional, with qualified workforce and in all respects according to valid technical regulations and average norms in construction industry. Masonry works should be carried out exactly in accordance with the plans, with regular bonds in completely horizontal rows.

Before beginning of masonry works, the masonry units should be well watered so that they do not weaken the strength of the joint between the masonry unit and the mortar by absorbing water from the mortar, and thus the strength of the wall itself.

Vertical and horizontal joints must be completely filled with mortar, without voids. The mortar in the joints must not be thicker than 10 - 12 mm. Leave the external joints empty to a depth of 15-20 mm for better bonding of the mortar when plastering the walls. Remove the excess mortar from the joints.

Carry out anchoring of facade bricks and hollow-clay block walls to the load-bearing wall with stainless steel anchors, 5 pieces per 1m2.

At the height above the door, for walls with a thickness of d=7 cm and d=12 cm, carry out reinforced concrete bond beams, along all the walls, anchored in the lateral structural walls.

The connection of brick walls with reinforced concrete walls and columns should be carried out with rebars  in every second row with a corresponding projected connection from the concrete elements.

For erection of facade walls with facade bricks that are not plastered, use only suitable bricks with sharp, straight and parallel edges, uniform in colour.

During the walls erection, pay attention that:

- the bricks bond determined by the designer is consistently and correctly followed over the entire surface of the wall,

- the bricks is machine cut,

- the joints are completely horizontal, i.e. vertical and with a continuous width of the joint.

Connection of external and internal load-bearing walls:

The connection of external and internal bearing walls should be rigid in order to enable the transmission of forces through a solid connection. This rigid connection is achieved as follows: make a recess in the load-bearing wall, in order to ensure the connection of the bearing walls of two perpendicular walls, the recess is filled with mortar, into which the wall element of the wall from the perpendicular direction is laid. The size of the recess depends on the wall material. If the wall is made of bricks, the recess should be at least 5 cm.

Bond beams and bond columns must be connected and anchored to the elements of the main load bearing system. Concreting of the bond beams and columns should be carried out after masonry works in order to achieve a better adhesion between the bond beams and columns and the wall. The minimum dimensions of the bond beams and columns are 15x15 cm. Bond columns should be performed at each wall butt joint. The horizontal distance of bond columns must not exceed 4 m.

## Wall ties

Wall ties shall be galvanized. Unless otherwise specified or approved by the Engineer they shall be of the vertical-twist strip type.

Special anchor ties for connecting brickwork blockwork or masonry to dovetail slots case in concrete shall be of similar specification and approved by the Engineer.

## Miscellaneous

The Contractor shall build in or provide all miscellaneous items to be set in masonry including lintels, frames, reinforcing steel, electrical boxes, fixtures, sleeves, grilles, anchors and other miscellaneous items. All anchorage, attachments and bonding devices shall be completely covered with mortar.

## Plastering

### Mortar

Mortar for plastering shall be as specified in previously.

### Decorative mortar

Decorative mortar shall be applied as specified on drawings, in tone and quality according to instructions by the Engineer. It shall be a ready-mixed decorative mosaic based on acrylite and marble grain with 2mm granulation. It shall adhere well to substrate, have good vapour permeability and resistant to atmospheric agents and UV radiation.

### Workmanship

Plain finish plastering shall be carried out in two coats. Walls which are to be plastered should be solid, clean, without loosely connected parts, greasy stains, etc.

Make sure that all the MEP works that precedes the plastering have been carried out.

Protect the built-in doors and windows.

If plaster is to be applied to smooth surfaces, a dash coat shall be applied as a bonding surface. Where dissimilar wall backgrounds meet to form a continuous surface a 150 mm wide strip of galvanised steel mesh wire shall be fixed over the joint between the dissimilar surfaces before the first undercoat is applied. Mesh wire edge profiles shall be installed to protect edges, and vertical trims – guides shall be installed on the walls, from the floor to the ceiling.

The mortar shall be prepared mechanically, by mixing the dry mixture with water according to the manufacturer's instructions.

Store the material in a dry place on pallets. The plastering machine should be cleaned from previous plastering. The optimal temperature in the room where the works shall be carried out is between +5ºC and +25ºC.

It is not allowed to dry the mortar with heaters.

## Floor Screed

### Standards

Standards for materials used for floor screed are covered in the previous sub-clauses.

The relevant standards on the basis of which the cement screed is made, but not be limited to, are the following:

- SRPS EN 13318- Screed material and floor screeds - Definitions

- SRPS EN 13813- Screed material and floor screeds - Screed material - Properties and requirements

- SRPS EN 13892-1- Methods of test for screed materials - Part 1: Sampling, making and curing specimens for test

- SRPS EN 13892-2- Methods of test for screed materials - Part 2: Determination of flexural and compressive strength

- SRPS EN 13892-3- Methods of test for screed materials - Part 3: Determination of wear resistance-Böhme

- SRPS EN 13892-4- Methods of test for screed materials - Part 4: Determination of wear resistance-BCA

- SRPS EN 13892-5- Methods of test for screed materials - Part 5: Determination of wear resistance to rolling wheel of screed material for wearing layer

- SRPS EN 13892-6- Methods of test for screed materials - Part 6: Determination of surface hardness

- SRPS EN 13892-7- Methods of test for screed materials - Part 7: Determination of wear resistance to rolling wheel of screed material with floor coverings

- SRPS EN 13892-8- Methods of test for screed materials - Part 8: Determination of bond strength

- SRPS EN 13892-9- Methods of test for screed materials - Part 9: Dimensional stability

### Workmanship

The screed thickness shall be determined by the design documentation. Screed in buildings on the insulating layer ("floating screed") shall be applied to a thickness of at least 3.5 cm, maximum 80 mm and surface shall be plane level. Larger and smaller thicknesses, have to be approved by the Engineer.

Before screed is applied onto concrete slabs all laitance shall be removed and the concrete slab shall be cleaned from all loose material, dust and dirt by thorough washing with water.

The screed mix shall be prepared from appropriate cement, water and aggregates and shall be thoroughly and efficiently be mixed dry by mechanical means until a uniform distribution is obtained prior to adding the water.

The Contractor should submit a Method Statement for the production of Floor Screed, to the Engineer for approval.

According to the design requirements, the floor screed can be reinforced with fibres, reinforced mesh or lightweight steel mesh “schulz”.

# INSULATION WORKS

## Moisture protection

### Description of work

The Contractor shall provide all materials, equipment labour and perform all operations required to furnish and install moisture protection as shown and noted on the designed documentation, as specified herein and as is evidently necessary to provide waterproof and moisture proof structure and to complete the works.

### General requirements

All materials shall be sound and free from defects that might impair the strength, quality and durability of the work.

Prior to delivery of any materials to the Site the Contractor shall furnish the Employer with certificates issued by the manufacturers stating that the materials that will be delivered shall comply with the requirements of the Specification.

All materials shall be products of firms normally engaged in the manufacture of such items, having a proven record of successful installations and acceptable to the Employer.

The materials shall be obtained from approved manufacturers and shall be delivered in the original sealed containers of the manufacturers and shall be stored in cool, dry places not exposed to the sun or dampness. Frequent tests shall be carried out to check the consistency of these materials. Membranes shall be delivered in the original sealed rolls of the manufacturers. In order to check the weight of membranes delivered, at least five out of every 100 rolls delivered shall be selected at random and checked for weight. If the Employer finds that these rolls are under their normal weight he may reject the whole delivery.

### Materials

#### Standards

The damp proof membrane, shall be applied in accordance with the design requirements.

Its application, installation and properties shall be complaint with, but not limited to, the following standards:

- SRPS EN 13707:2016  Flexible sheets for waterproofing - Reinforced bitumen sheets for roof waterproofing - Definitions and characteristics,

- SRPS EN 13859-1:2016, Flexible sheets for waterproofing - Definitions and characteristics of underlays - Part 1: Underlays for discontinuous roofing

- SRPS EN 13859-2:2016, Flexible sheets for waterproofing - Definitions and characteristics of underlays - Part 2: Underlays for walls

- SRPS EN 13956:2014, Flexible sheets for waterproofing - Plastic and rubber sheets for roof waterproofing - Definitions and characteristics

- SRPS EN 13967:2014, Flexible sheets for waterproofing - Plastic and rubber damp proof sheets including plastic and rubber basement tanking sheet - Definitions and characteristics

- SRPS EN 13984:2014, Flexible sheets for waterproofing - Plastic and rubber vapour control layers - Definitions and characteristics,

- SRPS EN 13969:2011, Flexible sheets for waterproofing - Bitumen damp proof sheets including bitumen basement tanking sheets - Definitions and characteristics

- SRPS EN 13970:2011, Flexible sheets for waterproofing - Bitumen water vapour control layers - Definitions and characteristics,

- EN 14891:2017, Liquid applied water impermeable products for use beneath ceramic tiling bonded with adhesives - Requirements, test methods, assessment and verification of constancy of performance, classification and marking,

- SRPS EN 14909:2014, Flexible sheets for waterproofing - Plastic and rubber damp proof courses - Definitions and characteristics,

- SRPS EN 14967:2011, Flexible sheets for waterproofing - Bitumen damp proof courses - Definitions and characteristics,

- SRPS EN 15814:2015, Polymer modified bituminous thick coatings for waterproofing - Definitions and requirements.

#### Damp proof Course

Damp proof course shall be lapped 100 mm at all joints, ends and intersections.

#### Polythene Membrane

The Polythene membrane shall be black low-density polythene sheet of single thickness not less than 0.20 mm thick manufactured from Polymer and mineral filler, in accordance with relevant National and EN standard. The membrane shall be lapped 100 mm at all joints, ends and intersections and spot bedded and sealed at joints in bitumen solution as specified herein.

#### Bitumen and Bitumen Solution

The hot bitumen shall be a blown bitumen type R.85/25 having a flash point of 200˚C, a melting point of 80˚ to 90˚C and a 20-30 penetration.

#### Building Paper

The Building paper shall be Class A Grade A2 paper conforming to relevant EN standard.

The Building paper shall be laid with a minimum of 150 mm laps at all joints and intersections and spot bedded and sealed in bitumen solution as specified herein.

#### Waterproofing Felts

All waterproofing felts and sheets shall be obtained from an approved manufacturer. The samples of materials shall be submitted to the Employer, and the approved samples shall be retained on the site as a standard against which the work will be judged.

The bitumen glass fibre felt shall be 4 mm thick overall.

The bitumen aluminium felt shall be overall 1.5 mm thick comprising aluminium foil 0.10 mm thick coated with bitumen solution of both sides and covered with surfacing material to prevent the felt from sticking during manufacture and when in the roll.

The aluminium foil shall be 0.10 mm thick, lapped at all joints 100 mm.

The plastic felt shall be polyizobuthilene felt of 1.5 mm thickness. All joints shall be welded.

The bitumen polyester felt shall be overall 4 mm thick comprising polyester net with improved bitumen containing plasticizers on both sides and covered with surfacing material to prevent the felt from sticking during manufacture and when in the roll.

The mineral surfaced bitumen polyester felt shall be overall 4 m thick as described above and finished with mineral chippings on the upper surfaces. The colour of the chippings shall be approved by the Employer.

### Workmanship

#### Generally

All waterproofing shall be performed in strict accordance with the requirements stated on the drawings and in this Specification by a firm that is normally engaged in such kind of work. All materials shall be stored, handled and laid according to the manufacturer's instructions.

Whenever waterproofing materials are to be applied on underground structures excavation shall be carried to such widths that enough clearance will be provided to perform the waterproofing work. All extra expenses connected with increasing the excavation and carrying it to limits greater than those required for the structures shall be borne by the Contractor.

While waterproofing is in progress the foundations of structures should be kept dry.

The Contractor shall exercise every care to ensure that the waterproofing is not at any time or in any way damaged and he is required to guarantee the watertightness of the structures. Care shall be taken not to injure the waterproofing either during application of after completion. During backfilling and/or filling the Contractor shall exercise great care to ensure that the back-filled and/or filling materials contain no objects likely to damage the waterproofing. Special care shall be taken when applying waterproofing on wall angles and footings and places where the water-proofing may be subjected to abnormal strain.

No water-proofing shall be applied nor shall it be covered before the approval of  the Employer.

No water-proofing work shall be carried during rainy days and/or when the air temperature falls below 5˚C.

#### Preparation of Surfaces

All Surfaces, whether horizontal or vertical, on which water-proofing is to be applied shall be firm smooth dry and free from loose materials, wood shavings, metal, concrete or block projections, nails and the like that may cause injury to the water-proofing.

Furthermore, all surfaces, shall be made smooth and free from air holes and cavities. Unevenness shall not exceed ±5 mm when tested with a 3 m long rod. The Contractor shall fill any cavities, holes, cracks joints and the like with (1:3) cement mortar and then float the surfaces with a thin layer of (1:3) cement mortar to give a smooth finish.

When the surfaces are ready and dry the cold bitumen as a primer coat shall be applied at a rate of no less than one (1) kg per square metre of treated surface with thorough brushing and then the surfaces shall be left exposed to air and allowed to dry; it is essential that this coating shall be free from voltalies before the waterproofing coat is applied. No waterproofing shall be applied or laid unless the surface that will receive it is treated with a primer coat.

#### Laying the Felts

The hot bitumen solution shall be applied at a rate of no less than 1.5 kg per square metre of treated surface. Each felt layer shall be laid with lapped and staggered joints with a minimum laps of 150 mm at ends and sides and shall be welded at joints where described.

The Felt may be laid either by pouring and rolling or by mopping. The first length of the felt shall be laid in position and firmly rolled back half way, the bonding compound shall be poured on the structure and the felt rolled out. Pressure shall be applied to allow a coat of hot compound to soften and adhere to the coating material of the felt. Only sufficient bonding compound shall be poured in front of the roll to allow a thin strip of the compound to be squeezed out at the edge. The other half of the length of the felt shall then be rolled up and the process repeated making sure that the coat or the hot bonding compound is continuous. The felt shall be thoroughly rubbed into the hot bonding compound and the entire surface shall be immediately rubbed to ensure through adhesion of the felt to the bonding compound. The felts shall be laid without wrinkles or buckles and the finished membrane shall be free from pockets and blisters. In mopping the procedure shall be similar to pouring and rolling except for the use of mops to spread hot bitumen bonding compound.

### Steel Sheet Flashing

The steel sheet flashing shall be provided to cover the joints, such as expansion joints, joints of dissimilar material etc. when indicated on the final drawings.

The Steel sheets shall be in accordance with relevant National and EN standard, low carbon steel sheet, and hot dipped zinc of appropriate type.

The flashings shall be bent and shaped as shown on the drawings, and shall provide adequate lapping over under-flashing or with roofing felts. Flashing shall be fixed with galvanised nails, or clips. The flashings shall be turned into grooves or collars of roof outlets and shall be finished with neat pointing in cement mortar if specified or other approved sealing material.

## Thermal Protection

### Description of Work

The Contractor shall provide all materials, equipment, labour and perform all operations required to furnish and install thermal protection as shown and noted on the design documentation, as specified herein and as is evidently necessary to provide thermally insulated structure in accordance with the calculations and provisions made in the final design and to complete the work.

### General Requirements

All materials shall be sound and free from defects that might impair the strength, quality and durability of the work.

Prior to delivery of any material to the Site the Contractor shall furnish the Employer with certificates issued by the manufacturers stating that the materials that will be delivered shall comply with the requirements of the Specifications and the calculations and provisions made in the design documentation.

The materials shall be obtained from a manufacturer that is normally engaged in such kind of production, and that has a proven record of at least two years of such production.

### Materials

#### Standards

Application of materials for thermal protection of buildings, their installation and properties shall be compliant with, but not limited to, the following standards:

- SRPS EN 13162- Thermal insulation products for buildings - Factory made mineral wool (MW) products - Specification

- SRPS EN 13163-Thermal insulation products for buildings - Factory made expanded polystyrene (EPS) products - Specification

- SRPS EN 13164-Thermal insulation products for buildings - Factory made extruded polystyrene foam (XPS) products - Specification

- SRPS EN 13165- Thermal insulation products for buildings - Factory made rigid polyurethane foam (PUR) products - Specification

- SRPS EN 13169- Thermal insulation products for buildings - Factory made expanded perlite board (EPB) products - Specification

- SRPS EN 14063-1- Thermal insulation products for buildings - In-situ formed expanded clay lightweight aggregate products - Part 1: Specification for the loose-fill products before installation

- SRPS EN 14303-Thermal insulation products for building equipment and industrial installations - Factory made mineral wool (MW) products - Specification

- SRPS EN 14307-Thermal insulation products for building equipment and industrial installations - Factory made extruded polystyrene foam (XPS) products - Specification

- SRPS EN 14308-Thermal insulation products for building equipment and industrial installations - Factory made rigid polyurethane foam (PUR) and polyisocyanurate foam (PIR) products - Specification

- SRPS EN 14309-Thermal insulation products for building equipment and industrial installations - Factory made products of expanded polystyrene (EPS) - Specification

- SRPS EN 14315-1-Thermal insulating products for buildings - In-situ formed sprayed rigid polyurethane (PUR) and polyisocyanurate (PIR) foam products - Part 1: Specification for the rigid foam spray system before installation

- SRPS EN 14318-1-Thermal insulating products for buildings - In-situ formed dispensed rigid polyurethane (PUR) and polyisocyanurate (PIR) foam products - Part 1: Specification for the rigid foam dispensed system before installation

- SRPS EN 14319-2-Thermal insulating products for building equipment and industrial installations - In-situ formed dispensed rigid polyurethane (PUR) and polyisocyanurate foam (PIR) products - Part 2: Specification for the installed insulation products

- SRPS EN 14320-1Thermal insulating products for building equipment and industrial installations - In-situ formed sprayed rigid polyurethane (PUR) and polyisocyanurate foam (PIR) products - Part 1: Specification for the rigid foam spray system before installation

- SRPS EN 15501- Thermal insulation products for building equipment and industrial installations - Factory made expanded perlite (EP) and exfoliated vermiculite (EV) products - Specification

- SRPS EN 16069-Thermal insulation products for buildings - Factory made products of polyethylene foam (PEF) - Specification

### Workmanship

#### General

All thermal insulation shall be performed in strict accordance with the requirements stated on the design documentation and in this specification and in accordance with the manufacturer's instructions and recommendations.

#### Preparation of Surfaces

All surfaces to which thermal insulation is to be applied shall be firm, dry and free from loose materials, wood shoring, metal, concrete or block projections, nails and the like that may cause injury to the insulation and vapour barrier.

#### Fixing the Boards

The board shall be fixed to the base with approved, proprietary type of adhesive as recommended by the board manufacturer resistant to high temperatures and moisture.

# DRY WALL PARTITIONS AND SUSPENDED CEILINGS

## Drywall Partitions

Use plasterboard with a nominal thickness of 12.5 mm. Longitudinal edges should be conical (designation KK according to SRPS EN 520), semi-rounded or conical semi-rounded. The dimensions and type of board, as well as the edge treatment, should be marked on the back of each board, on the accompanying label or on the packaging.

In rooms with increased humidity (bathrooms, showers, kitchens, etc.), use moisture-resistant plasterboard (impregnated) - mark H (1, 2 or 3). For shower cabins etc. use boards of moisture absorption class H1, while in bathrooms, kitchens, laboratories, etc. Use boards of minimum H2 moisture absorption class.

According to the design documentation for fire protection, it is necessary to provide dray wall partition systems with the required degree of fire resistance.

The substructure of the drywall system shall be manufactured from profiles made of cold-rolled low-carbon steel strips, coated with zinc, aluminum-zinc or zinc-aluminum, with a minimum thickness sheet of 0.6 mm. Profiles must be straight and must not be twisted.

The dimensions and layout of the substructure profile depend on the height, thickness and load on the wall. The profile is installed according to the manufacturer's instructions. The minimum distance between the vertical profiles of the substructure is 60 cm.

Cover the UW profiles on the floors and ceilings with self-adhesive tape for sound insulation and the screws for the floor and ceiling with screws with plastic dowels.

The screws for attaching plasterboard panels to the substructure should be at a distance of 25 cm. The heads of the screws should be sunk into the depth of the plate by about 1mm. The supporting profiles are fixed at least in three places and at distances of no more than 1m.

The door substructure is additionally reinforced with UA profiles if the wall is higher than 2.8m, if the door is wider than 90cm or if the door weighs more than 25kg.

The Drywall Partitions and lightweight internal walls shall be installed in strict adherence to material manufacturers' recommendations.

## Suspended Ceilings

The Contractor shall provide all material and perform all operations required for suspended ceilings as shown on the design documentation and finishing schedules and as is evidently necessary to complete the work.

All suspended ceiling systems shall be obtained from a manufacturer specialized for production and of this kind of material, and approved by the Engineer.

The Contractor shall prepare detail drawings showing suspension grid, ties, bolts and all fixings, perimeter edge fixing and suspension height incorporating position of lighting fitting, air condition grills, fire alarm or other services outlets that are shown on the final drawings. The drawings shall be submitted for approval to the Engineer.

The Contractor shall submit samples for approval to the Engineer.

All applied materials must comply with the provisions of valid standards and be certified by an authorized organization for the purpose for which they are used.

Suspended ceilings must meet the aesthetic, thermal, acoustic and fire protection requirements defined in the design documentation.

Suspended ceilings shall be suspended from the structural concrete slabs or beams and shall not be supported on the walls and/or partitions.

When installed suspended ceilings shall be rigid without showing any signs of sagging, bending or twisting with all fittings for services incorporated.

# CARPENTRY WORKS

## Generally

This chapter refers to carpentry works for construction of a wooden roof structure.

The Contractor shall provide all material and carry out the wooden roof structure in accordance with the Design documentation.

## Materials

Wooden roof structures should be made of monolithic wood and wood-based materials (for example: glued laminated wood, laminated veneer, etc.).

For wooden structures, materials and construction products specified in Serbian standards SRPS EN 1995-1-1 and SRPS EN 1995-2 (monolithic wood and wood-based materials) shall be used, whose performance is in accordance with the appropriate technical specifications to which these standards refer.

For connection of wood structures elements, mechanical fasteners (screws, wood screws without nuts, nails, mandrels, clamps, dowels and toothed metal plates) and adhesives shall be used, as listed in Serbian standards SRPS EN 1995-1-1 and SRPS EN 1995- 2, whose performance is in accordance with the relevant technical specifications to which these standards refer.

## Protection of wood structure

Technical characteristics of the wood structure protection depend on the wood structure usability class determined according to Serbian standard SRPS EN 335. Also, a balanced moisture content during the calculated service lifetime of the building has to be ensured, with the moisture content always being such as to ensure protection against fungi as a cause of rot and enable dimensional stability, without the appearance of permanent deformations.

The wood structures protection includes construction, structural, organizational and chemical protection measures against atmospheric influences, internal climate influences, the influence of leachate and other waters, as well as biological influences and the effects of fire, in order to preserve the mechanical resistance and stability and fire resistance of the building.

Protection shall be carried out in accordance with SRPS EN 599-2- Durability of wood and wood-based products - Efficacy of preventive wood preservatives as determined by biological tests - Part 2: Labelling

The wood structure protection must include protection of all individual wood structure elements (wooden, metal and others), as well as protection of the wood structure as a whole.

The protection of certain elements of the wood structure must not adversely affect the protection of other elements.

Corrosion protection of metal parts that make an integral part of the wood structure shall be carried out in accordance with the Serbian standard SRPS EN ISO 2081 and in accordance with the relevant provisions of the Serbian standards from the SRPS EN 1992 and SRPS EN 1993 series, as well as examples of the minimum corrosion protection of metal parts depending on the given usability class in the Serbian standard SRPS EN 1995-1-1.

## Workmanship

Prior to installation of the wood structure, the contractor shall:

1) examine every bill of lading and documentation accompanying wood products, mechanical fasteners, adhesives, protective agents and other construction products that are to be installed in a wood structure,

2) visually inspect wood products, packaging of mechanical fasteners, adhesives, protective products and packaging of other construction products in order to determine possible damage,

3) determine the moisture content of wood elements, i.e. prefabricated products.

The moisture content of wood products shall be determined immediately before the installation of wood structure elements in accordance with Serbian standards from the SRPS EN 13183 series.

Prior to installation of wood structure elements, control tests of construction products shall be carried out in case of doubts about their performance.

The wood structure elements shall be marked with the assembly plan, if this is not clearly visible from their shape.

The wood structure elements and other products that are to be installed in the wood structure shall be transported and stored until the moment of installation in the manner determined by the wood structure design, that is, the manufacturer's technical instructions.

Wood based products shall be cut on a specially prepared and covered surface, i.e. a table, on which the structure is drawn with all the details and overhangs in natural size with the use of precise tools.

As for trusses, it is necessary to inspect the ends of individual truss elements for presence of lumps and cracks, and discard elements that do not meet the requirements for installation.

Cuts, holes and notches for fasteners must be made with such precision to ensure the design properties of a connection.

Installation of fasteners and connectors shall be carried out in such a temporary position of the structural elements that ensures the designed overhang.

During execution, the wood structure must be secured and temporarily stiffened against overturning.

All temporary stiffeners and supports must be retained in the wood structure until it has been constructed to a degree that allows their safe removal.

## Glued wood structures

Gluing on the construction site is allowed only in controlled conditions in accordance with the technical instructions of the adhesive manufacturer, the requirements of the wood structure design and the provisions of this article.

Only elements whose surface has been previously prepared (dried, cleaned, degreased, etc.) may be glued in accordance with the wood structure design and the manufacturer's technical instructions.

When gluing the joints, it is not allowed to repair uneven surfaces with sandpaper.

When gluing the joints, the moisture content of wood products at the joints must be controlled immediately prior to gluing.

The maximum difference in the moisture content of the wood product at the connection point must not be greater than 2% in relation to the moisture content defined by the design.

In the case of glued laminated supports, all joints must be made with adhesive of the same origin as the adhesive used to glue the lamellas together.

During the adhesive curing, it is not allowed to move the elements.

The control of the glued joint and the strength of the adhesive in the glued structure must be controlled even after the gluing is finished, which is achieved by testing the samples made under the same conditions and identical circumstances as for the main glued structure or by taking test samples from the main structure with the appropriate application of Serbian standards from the SRPS series EN 15416 and SRPS EN 302.

## Restrictions during wood structure execution

During the wood structures execution, the following shall not be allowed:

1) installation of soft structural wood of strength class lower than C18,

2) installation of wood-based elements made of monolithic wood and glued laminated wood for which it is determined that the initial flaw in the middle of the element exceeds the values determined in the Serbian standard SRPS EN 1995-1-1,

3) installation of wood products whose moisture content is higher than 22%,

4) installation of wood elements that are not protected by organizational protection measures in such a way as to prevent wetting of wood during transport, processing, intermediate storage, assembly and use, by avoiding direct contact with water and soil, correct stacking of elements and covering,

5) installation of mechanical fasteners when making a glued joint in such a way that they are considered as load-bearing fasteners. If nails, screws or wood screws without a nut are used during the production of the glued joint, they are considered only as fastening (auxiliary) connecting means,

6) gluing a wooden product whose moisture content is different from 12% ±3%, that is, from the defined moisture content that corresponds to the technical instructions of the glue manufacturer, with the fact that the largest difference in the moisture content of the elements to be glued does not exceed ±2%,

7) the use of different types of adhesives for the execution of a glued wood structure,

8) welding, on the construction site or in the factory, of steel elements that are in contact or in such close proximity to wood elements that the heat of welding and/or sparks can damage the wood elements or their protective coating.

# ROOFING

## General

Roofing shall be fully designed and executed in compliance with the Rulebook on Technical Standards for Designing and Carrying out of Finishing Work in Civil Engineering, Part 3.1.

The type of roof covering/system shall be in accordance with Employer’s Requirements.

The Contractor shall submit samples and references to the Engineer for his approval of the materials he intends to use before ordering these materials.

## Roof Panel

The Contractor shall provide a sandwich panel where it is defined, consisting of liner sheet, sub-girt system, exterior panelling, all closures, fasteners, flashing, sealing and all accessories, including all items incidental thereto, as specified herein, as is evidently necessary to complete the work and to provide weather proof construction.

Deflection shall be limited to 1/240 of the span and stresses shall be below the allowable stress point under the specified loading for the purlin spacing used. Panel lengths shall be the maximum practical lengths for handling and uniform in length insofar as possible to provide alignment over main supports only. The thermal filling of the roof panel is in accordance with the calculation of the Elaboration of Energy Efficiency and the fire protection conditions for the building.

Installation shall be in accordance with the directions of the manufacturer. No panels shall be installed until the required back painting of structural steel has been performed. No aluminum shall be allowed in contact with bare carbon steel. Any carbon steel not isolated by back painting or galvanizing shall be taped or mastic coated at points of contact. Horizontal fastening shall be at every girt. All closures and flashings shall be installed as necessary for weathertight construction.

For basic material and material for all exterior caulking, the Contractor shall submit to the Engineer, literature, certificates and samples for approval.

Dented, deformed, misaligned or off-color panels shall not be accepted.

## Profiled trapeze Steel Sheet

The Contractor shall provide a galvanized, plastificate profiled trapeze sheet steel, for roofing of a buildings, where is it defined.

The profiled steel sheet used complies with the following groups of standards:

- SRPS EN 10346, Continuously hot-dip coated steel flat products for cold forming - Technical delivery conditions

- SRPS EN 10143, Continuously hot-dip coated steel sheet and strip - Tolerances on dimensions and shape

- SRPS EN 13501-1, Fire classification of construction products and building elements - Part 1: Classification using data from reaction to fire tests

Installation shall be on the prepared roof structure and substructure.

## Membrane Roofing System

The Contractor shall provide a waterproofing vapor permeable UV resistant membrane where it is defined.

Material for waterproofing sheet shall conform to the requirements of the standards listed in part “Moisture protection”.

Waterproofing vapor permeable UV resistant membrane have to satisfy the following characteristics:

- Outstanding resistance to weathering, including irradiation

- High resistance to ageing

- Resistant to all common environmental influences

- High resistance to mechanical influences

- High tensile strength

- High water vapour permeability

- Outstanding weldability

- Recyclable.

Roofing work shall not commence until parapets, caps, cants, sumps and all work pertaining thereto are completed in the area to be roofed. Roof surfaces shall be carefully examined for defects detrimental to the function of the roofing system.

No roofing system shall be applied until all above requirements are met and all defects are repaired.

The roof surfaces shall be free of stored and waste materials and broomed free of dirt, nails and any other foreign matter. The roof surface shall be thoroughly dried out before any membrane roofing is applied.

Application shall be performed by carefully supervised, skilled and experienced personnel only, in such manner as to construct a continuous and impervious membrane roofing system with weathertight flashings.

The work shall be performed in such a manner that will finish, at the end of each day’s work, a portion of completed roof.

Installation procedure shall be carried out according to the valid installation instructions from the manufacturer of this type of system for mechanically fastened roofs.

## Roof Domes

The Contractor shall provide factory made domes glazed as specified, with the two-layer acrylic glass completely in accordance manufacturer's detail and all items incidental thereto and as evidently necessary to complete the work.

Thermal characteristics are required by calculation in the Elaborate on energy efficiency. The method of opening shall be provided according to fire and functional requirements.

The dome shall be completely protected from getting rain - wet with the rubber gasket with dripstones, all necessary flashings with dripstones between the structure of the dome, roof and substructure made of factory-painted aluminium sheet in the tone with the roof's panels.

## Canopies

Above the entrance doors of the buildings, where it is defined, the Contractor shall provide canopies.

Predict canopies with polycarbonate or acrylic sheet infill.

The construction of the canopy is according to the static calculation.

## Steel Sheet Flashing and External Roof Gutters

The steel sheet flashing shall be provided to cover the joints, such as expansion joints, joints of dissimilar material etc.

The Steel sheets shall be in accordance with relevant EN standard, low carbon steel sheet, hot dipped zinc of appropriate type and plastificated in colour as exterior units.

The flashings shall be bent and shaped as shown on the drawings, and shall provide adequate lapping over under-flashing or with roofing felts. Flashing shall be fixed with galvanised nails, or clips. The flashings shall be turned into grooves or collars of roof outlets and shall be finished with neat pointing in cement mortar if specified or other approved sealing material.

## Roof Accessories

The Contractor shall provide all roof accessories and items incidental thereto, as is necessary to complete the work.

### Rainwater Outlets

Contractor shell provide water drainage from all roofs. External gutters (horizontal and vertical) are made of steel galvanized plastic sheet.

Applicable standards are as follows:

- SRPS U.N9.055		Prefabricated elements for buildings - Sheet metal flashing outside parts of building - Technical requirements

- SRPS U.N9.054	 	Prefabricated elements for buildings - Sheet metal roofing - Technical requirements

- SRPS U.F4.010	 	Roof covering with concrete tiles - Technical requirements

Rainwater roof outlets shall comply with the relevant standards. They shall be fitted with circular gratings and sized for the down pipes. A sample of the type of rainwater outlet to be used shall be submitted to the Engineer for approval.

### Vent pipes

Ventilation pipes will extend through the roof and terminate at an effective height and as agreed by the Engineer. The ventilation pipes passing through the roofs must be watertight and equipped with PVC covers for venting on the roof. If necessary, PVC gratings are placed on the ceilings.

## Galvanized Steel Sheet

Galvanized steel sheet for covering roof movement joints shall comply with the SRPS U.N9.055 and be 20 gauge (1.00 mm thick).

## Movement Joint Sealant

Sealant for protecting joints in movement joint covers shall be one-part gun grade polysulfide.

# FAÇADE WORKS

## Metal cladding facade system

### Facade thermal panel

Sandwich wall panel system shall consist of liner sheet, sub-girt system, exterior panelling, all closures, fasteners, flashing, sealing and all accessories, including all items incidental thereto, as is necessary to complete the work and to provide weather proof construction.

The thermal filling of the wall panel is in accordance with the calculation of the Elaboration of Energy Efficiency and the fire protection conditions for the building.

Wall panel assemblies shall be fabricated at the factory, ready for field assembly as for follows:

- Thickness and a width as described on the drawings

- Side joints shall be tongue and groove, shiplap design. Fasteners shall not be exposed from the exterior but concealed within the side joint.

- Tolerance shall be 2.5 mm plus or minus adjustment feature.

- Interior female joints shall be factory caulked.

Trim at gravel stop and corners shall be the same embossed material, finish and colour as exterior face units.

All required extruded trim of the same finish and colour at the bottom of wall shall be provided.

Installation shall be in accordance with the directions of the manufacturer. No panels shall be installed until the required back painting of structural steel has been performed. No aluminum shall be allowed in contact with bare carbon steel. Any carbon steel not isolated by back painting or galvanizing shall be taped or mastic coated at points of contact. Horizontal fastening shall be at every girt. Vertical fastening shall be through girts and sub-girts only spaced evenly. All closures and flashings shall be installed as necessary for weathertight construction.

For basic material and material for all exterior caulking, the Contractor shall submit to the Engineer, literature, certificates and samples for approval.

Dented, deformed, misaligned or off-color panels shall not be accepted.

### Profiled trapeze Steel Sheet facade system

The Contractor shall provide a galvanized, plastificate profiled trapeze sheet steel, for cladding façade walls of buildings, where it is defined.

The type i.e. dimension of profiled trapeze sheet steel, shall be according to the static calculation.

This system consisting of liner sheet, fasteners, flashing, sealing and all accessories, including all items incidental thereto, as specified herein, as is evidently necessary to complete the work and to provide weather proof construction.

The profiled steel sheet used complies with the standards listed in chapter “Profiled trapeze Steel Sheet”.

Installation shall be on the prepared wall structure and substructure as described in the previous part for facade panels.

## Contact thermal facades

The Contractor shall perform contact thermal facade where it is defined.

The contact thermal facade is made by doweling and polyurethane glue, glued with hard mineral wool panels, finally treated with embossed plaster in the colour and texture selected by the Engineer, over a double layer of building glue with an imprinted mesh with glass fibers.

The thickness and type of mineral wool panels, elements of the facade system that ensure thermal conductivity, vapor permeability of the facade, are determined in accordance with the requirements of the Elaborate on the energy efficiency of buildings as well as fire protection requirements.

The decorative layer (embossed plaster) must be silicone, silicate or silicone-silicate, i.e. compatible with stone mineral wool, in accordance with the manufacturer's recommendation.

The complete facade system, as well as the basic and auxiliary material for the installation of the facade system, must be certified and approved by the Engineer (mineral wool, dowels, initial, drip corner moldings, glue, mesh with glass fibers, embossed plaster).

If the design documentation provides, the skirts of the buildings should be made with acrylic marble plaster.

The execution of the works is in accordance with the standard SRPS U.F2.010, Final work in building - Specifications for frontside works.

## Scaffold

The contractor is obliged to provide scaffolding and all necessary auxiliary structures for the execution of the final works, in the time period until the completion of the work.

Scaffolding and auxiliary structures must comply with all valid technical regulations and valid HSE    measures. Scaffolding must be statically stable, anchored to the building and properly grounded. Build working platforms every 2.5 m with a protective fence. The scaffolding must have a permit for use.

# WINDOWS AND DOORS

## Materials

Windows and doors shall be of good quality and robust and shall be to the approval of the Engineer. Weather-stripping shall:

- Be made from materials aluminum except for the fire proofing ironmongery, which is made of steel,

- Not shrink or warp nor adhere to sliding surfaces or closing surfaces

- Not promote corrosion when in contact with the aluminum alloy used,

- Be resistant to deterioration by weathering.

Flashings, weather bars, drips, storm moulds, caulking and pointing shall be installed so that water is prevented from penetrating the building between the frame of external doors or windows and the building structure under the prevailing service conditions, including normal structural movement of the building.

External doors and windows shall be made of the thermally insulated profile according to the calculation of Energy efficiency Elaborate. For external doors and windows flashings and weatherings shall be used which are corrosion resistant, compatible with the other materials in the installation, and coated with a non-staining compound where necessary.

Door bottoms for external doors shall be full mortised type with tubular neoprene and glass fibre core and shall close the entire gap between the door and the floor. Door bottoms shall ensure a continuous, positive, reliable seal at the floor with minimum friction, drag, and roll of the assembly on the floor.

Joints in frames shall be made neatly and accurately either by welding or by mechanical means (e.g. cleating and screwing) and may have flush stepped or lapped surfaces. Welded joints shall be cleaned off smooth on the surfaces which are exposed when the window or door is in the closed position or where they come into contact with glazing. Flush joints formed by mechanical means shall be in line to within the limits permissible.

Hinges and pivots shall be either of suitable corrosion resistant materials or if not compatible with the frame material shall be separated from the frame by materials that are compatible with it. Not less than 3 hinges per door shall be applied. For doors with clearance greater than 2 m2, the number of hinges shall be as per static calculation.

Hardware including its fittings shall be of suitable corrosion resistant materials. Materials or finishes, which are not compatible with the frame materials, shall not be used unless they are satisfactorily separated from the frame by materials that are compatible with it. Screws (self-tapping and wood) nuts, bolts, washers, and other fastenings shall be of stainless steel or aluminum.

All external and office doors as well as the doors for laboratory and control room shall be fitted with tabular 5 level cylinder security locks incorporating separate dead bolts. Passage doors shall have no lock. Toilet cabin doors shall have a bolt on inside. All other doors shall have a normal lock.

All security locks in all buildings shall receive master keys. Three keys for each security lock shall be delivered. For normal locks as well three keys shall be delivered.

All keys shall be clearly labelled with metal or plastic tags size approximately 50 x 20 mm securely fixed to the keys.

Door closers shall be of heavy duty type and installed on all external doors on the inside.

Door stops shall be floor or wall mounted type with rubber cover.

Provision shall be made for suitable fixing devices. Where such devices are built in and not exposed directly to the weather they may be made from steel which has been hot-dip galvanised or zinc sprayed or zinc plated and passivated.

Emergency doors where shown on the Drawings, shall be fitted with an approved panic bolt to the inside of the doors and the doors shall be designed to open outwards.

Windows and doors shall be such that glazing or re-glazing on site is possible without the need to remove the outer frame from the structure of the building. Glazing beads gaskets glass adapters and glazing compounds shall be of materials compatible with the frame material and finished thereon.

All windows shall be pivot type window (tilt and turn). Both opening modes shall be controlled with the same lever handle.

All opening windows shall be fitted with suitable insect screens.

All windows shall be provided by aluminum sheet sills.

The Contractor shall submit details of manufacture including sections of frame members and no orders shall be placed until such details have been approved by the Engineer.

## Standards

Windows and doors shall comply with but not limited to the following standards:

- SRPS EN 1125-Building hardware - Panic exit devices operated by a horizontal bar, for use on escape routes - Requirements and test methods

- SRPS EN 1154- Building hardware - Controlled door closing devices - Requirements and test methods

- SRPS EN 1155- Building hardware - Electrically powered hold-open devices for swing doors - Requirements and test methods

- SRPS EN 1158- Building hardware - Door coordinator devices - Requirements and test methods

- SRPS EN 12209- Building hardware - Locks and latches - Mechanically operated locks, latches and locking plates - Requirements and test methods

- SRPS EN 13241- Industrial, commercial and garage doors and gates - Product standard - Part 1: Products without fire resistance or smoke control characteristics

- SRPS EN 13561-External blinds and awnings - Performance requirements including safety

- SRPS EN 13659- Shutters - Performance requirements including safety

- SRPS EN 14351-1- Windows and doors - Product standard, performance characteristics - Part 1: Windows and external pedestrian doorsets

- SRPS EN 14846- Building hardware - Locks and latches - Electromechanically operated locks and striking plates - Requirements and test methods

- SRPS EN 16034- Pedestrian doorsets, industrial, commercial, garage doors and openable windows - Product standard, performance characteristics - Fire resisting and/or smoke control characteristics

- SRPS EN 179- Building hardware - Emergency exit devices operated by a lever handle or push pad, for use on escape routes - Requirements and test methods

- SRPS EN 1935- Building hardware - Single-axis hinges - Requirements and test methods

## Glass

Glazing of openings is performed with glass in thermal package with low-emissivity glass (U glass factor according to EN, should be according to the Elaborate on energy efficiency), mild reflections with argon filling. As required in exposed positions, the inner glass with a thickness of 6 mm is made as a Pamplex safety glass. The window's glass of toilets and showers shall be frosted.

The glass used complies with some of the following groups of standards:

- SRPS EN 1096, Glass in building - Coated glass

- SRPS EN 12150, Glass in building - Thermally toughened soda lime silicate safety glass

- SRPS EN 12337, Glass in building - Chemically strengthened soda lime glass

- EN 1279, Glass in building - Insulating glass units

- SRPS EN 13024, Glass in building - Thermally toughened borosilicate safety glass

- SRPS EN 14178, Glass in building - Basic alkaline earth silicate glass products

- SRPS EN 14179, Glass in building - Heat soaked thermally toughened soda lime silicate safety glass

- SRPS EN 14321, Glass in building - Thermally toughened alkaline earth silicate safety

- SRPS EN 14449, Glass in building - Laminated glass and laminated safety glass

- SRPS EN 15681, Glass in Building - Basic alumino silicate glass products

- SRPS EN 15682, Glass in building - Heat soaked thermally toughened alkaline earth silicate safety glass

- EN 15683, Glass in building - Thermally toughened soda lime silicate channel shaped safety glass

- SRPS EN 1863, Glass in building - Heat strengthened soda lime silicate glass

- SRPS EN 572, Glass in building - Basic soda lime silicate glass products

## Roller Shutter Doors

Roller Shutter Doors shall be electrically powered, with a control system for detecting and automatically stopping the door, with the possibility of manual opening in the event of a power outage.

The relevant sections of the following codes and standards shall be complied with:

Regulations and standards for structural steel in building:

- Regulations and standards for hot-dip galvanized coatings on iron and steel articles

- Regulations and standards for construction hardware,

- Regulations and standards for electric drive and electric devices for holding the door in a certain position,

- Other standards for industrial doors.

The Contractor shall submit to the Engineer for approval:

- Manufacturer’s published specifications.

- Workshop detail and erection drawings

- Detailed painting and coating specifications and procedures.

- Delivery and Storage

Doors and materials shall be delivered to the jobsite in packages or bundles which are clearly marked, to identify fully the contents. Prefinished materials shall be enclosed and interleaved as required to prevent damage or defacement caused by handling or weather. Door shall be stored off the ground, under cover, and accessible at all times for piece by piece inspection.

### Materials of Construction

#### Door Curtain

The door curtain shall be constructed of interlocking, roll formed steel slat of flat configuration. Size and gauge shall be as required to provide the curtain with adequate stiffness. Slats shall be hot-dip galvanized and painted.

Two galvanized steel angles of equal weight shall be securely fastened back to back to the bottom of curtain for reinforcement.

#### Accessories

Doors shall be equipped with the following accessories:

- Loop-type rubber or neoprene astragal attached to bottom bar.

- Rubber or neoprene hood baffle.

- Weather seal at jambs.

#### Miscellaneous

Mechanisms, box, motor covers and manual control gear shall be coated during manufacture in accordance with relevant standards.

Lintels and structural steelwork shall be coated during manufacture in accordance with relevant standards.

Finishing

After installation all exposed elements of the roller shutter doors shall be painted.

Operation

Doors shall be motorized and operated by an electric motor of sufficient power to raise the door with a velocity of not less than 250 mm per second.

Doors shall have a standard 3 push button control station mounted on the inside wall together with a weatherproof, key operated control station mounted on the exterior side.

Doors shall have a manual emergency stand-by system, consisting of a hand chain, sprocket and reduction gear arranged to raise the door with a pull of approximately 150 N.

## External Doors and Frames

External doors and frames shall be of good quality, and robust.

External doors shall be so designed that they swing to the closed position unless deliberately held open. The doors and frames shall be fitted with efficient draught excluders.

All external glass shall be thermally insulated glass units with low-emissivity glass (U glass factor according to EN, should be according to the Elaborate on energy efficiency), mild reflections with argon filling, to the approval of the Engineer.

## External Windows

External windows and frames shall be of good quality, and robust.

All hardware shall be supplied and fixed by the manufacturer and shall match the finish of the surfaces of the units and shall be replaceable without removing the outer frame from the structure. Fasteners shall be designed so that they cannot be released from the outside by the insertion of a thin blade or other simple tool.

Windows shall meet the performance requirements of the Rulebook on Technical Standards for Designing and Carrying out of Finishing Work in Civil Engineering, Part 3.3.

All surfaces in contact with blockwork, concrete render or other alkaline materials shall be coated with two coats of black bitumen solution or similar approved protective coating. All unit surfaces which will be visible when the window is fixed in position shall be protected after manufacture by low tack tape or other suitable means capable of being removed after installation of the window to leave clean undamaged anodised surfaces.

All external glass shall be thermally insulated glass units with low-emissivity glass (U glass factor according to EN, should be according to the Elaborate on energy efficiency), mild reflections with argon filling, to the approval of the Engineer.

## Flush Doors

Internal and external flush doors shall comply with ICS 91.060.50, SRPS EN 16034:2015-Pedestrian doorsets, industrial, commercial, garage doors and openable windows - Product standard, performance characteristics - Fire resisting and/or smoke control characteristics and other EN and SRPS standards for it.

Door seals to the outer stiles, the frame and the meeting stiles of double action swing doors shall be of the neoprene brushing type set in with aluminum screws the seals to brush onto PVC inserts in an aluminum alloy channel section similarly fixed.

Threshold seals in neoprene to the bottom of doors shall be set in upstand type aluminum holding channel.

All door seals shall be to the approval of the Engineer.

# IRONMONGERY

## Generally

The Contractor shall provide and install all metal doors, metal frames and all items incidental thereto, as necessary to complete the work.

The Contractor is obliged to prepare shop drawings showing all dimensions, sections, materials, reinforcements, thicknesses, finish hardware sets, anchors and all other information necessary for proper evaluation shall be submitted to the Engineer for review.

## Metal Doors

### General

Doors shall be as shown on drawings which shall include Door Schedules. All metal doors and frames shall be manufactured by a firm normally engaged in the manufacture of such items, having a proven experience record of successful installations and acceptable to the Engineer. Template for door hardware shall be furnished by the Contractor to the door manufacturer in order that doors and frames may be mortised, machined, reinforced and prepared for the hardware.

### Construction

All metal doors and metal frames shall be constructed of prime quality cold rolled steel. Quality, weights and sizes specified herein are considered to be the minimum that will be acceptable. Doors shall be 45 mm minimum thickness flush type with face sheets of 1.5 mm minimum thickness stretcher levelled steel, all welded construction with perimeter stiles of not less than 1.2 mm steel. Face sheets shall be securely welded to interlocking vertical and horizontal frame members spaced no more than 150 mm on centres. Tops shall be flush closed. All exposed welds shall be ground smooth. All door cavities shall be filled with suitable sound deadening and insulating material. Doors having glass lites shall have snap-in mouldings with no visible fastenings. Louvres shall be provided as required or where indicated on the construction drawings and shall be fixed slat type.

### Erection

Doors shall be erected plumb and true with all hardware left in proper working order. Erection shall be by competent door erectors in accordance with the manufacturer's recommendations.

Painting shall be in accordance with relevant standards approved by the Engineer.

### Metal Frames

Pressed metal frames shall be wrap around or butted, as detailed, 1.9 mm minimum thickness rolled steel, with integral stops and rebates, sizes as noted on the final drawings. All frames shall have all hardware cut outs reinforced with 3.2 mm minimum plate welded to frame and 4.8 mm minimum plate hinge reinforcement. Frames shall be mortised, reinforced, drilled and tapped for mortise type hardware reinforced for surface hardware and provided with silencers. Frames used in masonry walls shall have tapped holes protected by steel plaster boxes welded behind reinforcement. Heads and jambs shall be notched, mitred, welded and finished smooth. Not less than three (3) adjustable wall anchors shall be provided at each jamb, plus welded-on clip angles with two (2) holes for anchoring to floor at bottom of each jamb. Frames for doors with leaves over 900 mm wide shall have additional anchorage and reinforcement where recommended by the frame manufacturer. Frames shall have removable angle spreaders securely fastened to the bottom of jambs to ensure rigidity during shipping and handling. All frames shall be galvanized, bonderized and shop painted with one (1) coat of rust inhibitive primer.

## Fire Rated Doors

Metal fire doors where indicated on drawings, Door Schedules or where required by design.

The doors should be made in accordance with SRPS U.J1.240 and meet all legal requirements.

The doors shall be made of galvanized sheet with fireproof filling and fireproof cassette for the lock. The door frame shall be made of sheet steel with a bedding for sealing rubber and an expanding strip. The doors shall be equipped with 3 hinges (one of which with a spring for self-closing), a fireproof lock and a handle. The doors have no threshold.

The doors shall be  equipped with a suitable automatic device that keeps it in a permanently closed position. If the doors are located on a path of egress, they have to be provided with a push bar (exit doors opening mechanism) in the direction of exit.

The doors must have a certificate issued by a local accredited laboratory.

## Metal Lathing, Expanded Metal and Wire Mesh

Metal lathing and wire mesh should be in galvanized steel. Samples of lathing etc., shall be submitted to and be approved by the Engineer before the use in the work.

## Indoor and outdoor Fences

The Contractor shall carry out the fences, as follows:

On the stairs inside the buildings and

On ramps and entrance stairs to buildings, outside the building.

The fences shall be made of stainless steel, completely in accordance with the design documentation.

The height of the fence is 1.1 m.

Fences must be built in accordance with the Rulebook on technical standards for planning, designing and building buildings, which ensure unhindered movement and access for people with disabilities, children and the elderly ("Official Gazette of RS", no. 22/201.

Fences must meet all requirements for functionality and safety.

The Contractor is obliged to submit shop drawings and fence samples to the Engineer for approval.

# FINISHING WORKS: WALLS, CEILINGS

Finishing work shall be designed and carried out in compliance with the Rulebook on Technical Standards for Designing and Carrying out of Finishing Work in Civil Engineering.

## Paintings works

The surface of the plastered walls and ceilings, plasterboard wall and ceiling surfaces, as well as internal concrete beams, ceiling and columns shall be painted with the polymer dispersion washable paint, with previous two-fold trowelling with the polymer putty and preparation for the paint application.

The paint to be used shall be the best quality emulsion paint available. The colour will be selected by the Engineer.

In any case, the paint has to be spread in accordance with the manufacturer's instructions. Painting works are done by hand or by machine, by coating or spraying, and it is done several times. The resulting tone must be clean, uniform, cover the substrate well, and be free of brush or roller marks. All finishes of painted surfaces must be correct, the paint must not peel or rub off.

## Wall- tiling

In general, ceramic tiles shall be of best quality available on the local market.

The quality and colour shall be approved by the Engineer. The tiles shall be true to shape, flat, free from flaws, cracks and crazing, uniform in colour, acid resistance where required, therefore the Contractor shall submit some samples to the Engineer before ordering the tiles.

The tiles used complies but not limited with the following groups of standards:

- SRPS EN 14411:2015, Ceramic tiles - Definitions, classification, characteristics, evaluation of conformity and marking

- SRPS EN ISO10545 -1, Ceramic tiles - Part 1: Sampling and basis for acceptance

- SRPS EN ISO10545 -2, Ceramic tiles - Part 2: Determination of dimensions and surface quality

- SRPS EN 10545 -3, Ceramic tiles - Part 3: Determination of water absorption, apparent porosity, apparent relative density and bulk density

- SRPS EN 10545 -4, Ceramic tiles - Part 4: Determination of modulus of rupture and breaking strength

- SRPS EN 10545-5, Ceramic tiles - Part 5: Determination of impact resistance by measurement of coefficient of restitution

- SRPS EN 10545-6, Ceramic tiles - Part 6: Determination of resistance to deep abrasion for unglazed tiles

- SRPS EN 10545-7, Ceramic tiles - Part 7: Determination of resistance to surface abrasion for glazed tiles (required minimum PEI 4 for floors),

- SRPS EN 10545-8, Ceramic tiles - Part 8: Determination of linear thermal expansion

- SRPS EN 10545-9, Ceramic tiles - Part 9: Determination of resistance to thermal shock

- SRPS EN 10545-10, Ceramic tiles - Part 10: Determination of moisture expansion

- SRPS EN 10545-11, Ceramic tiles - Part 11: Determination of crazing resistance for glazed tiles

- SRPS EN 10545-12, Ceramic tiles - Part 12: Determination of frost resistance

- SRPS EN ISO10545-13, Ceramic tiles - Part 13: Determination of chemical resistance

- SRPS EN ISO10545-14, Ceramic tiles - Part 14: Determination of resistance to stains.

- DIN 51130:2004-06 testing of floor coverings - determination of the anti-slip property

- DIN 51097:02.80- Determination of anti-slip characteristics /slipperiness classification

- SRPS EN 12004, Adhesives for ceramic tiles - Part 1: Requirements, assessment and verification of constancy of performance, classification and marking

The minimum required chemical resistance of ceramic tiles for laboratories and the rooms in contact with chemicals matters is class LA, while for other rooms it is class A.

Ceramic tiles are laid on previously cleaned and prepared wall surfaces with appropriate certified adhesives. The tiles are grouted with water-repellent grouting compound. The joints shall be narrow and of uniform width and color.

The execution of works is in accordance with the standard SRPS U.F2.011 Final work in building - Ceramic works - Technical requirements.

# INTERNAL FLOORING

## General

All materials and structural components for flooring systems shall be used only with the approval of the Engineer.

Before starting the work, the Contractor shall ascertain the Engineer's selection of patterns and colours and the Contractor shall furnish the Engineer with duplicate samples of the patterns and colours of the materials selected by the Engineer.

The surfaces must be cleaned prior to flooring. The base for covering to be placed without underlay shall be smoothed with filler compound. In the case of major unevenness a suitable levelling compound shall be used.

Any filler or levelling compound shall be applied so that it will bond firmly and durably to the base, will not crack and will adequately withstand pressure. Any screeds such shall receive a priming coat.

The courses of flooring systems shall be laid towards the main window wall and in halls and corridors in longitudinal direction, unless otherwise specified.

Deviations in colour which are not of minor importance and not due to the flooring pattern shall not be allowed if they mar the overall appearance of the flooring.

Where courses run towards doors, recesses and the like, they shall be laid so as to cover also the floor areas such door openings, recesses etc.

All finished surfaces shall be properly protected until completion of the Contract.

## Ceramic tile flooring

The ceramic tiles for paving are to be even in thickness, truly square, free from cracks, twists and blemishes, uniform in color, well and evenly burned.

The kind, quality and color shall be approved by the Engineer, therefore the Contractor shall submit some samples to the Engineer before ordering the tiles.

Ceramic tiles are laid over a cement screed and shall be fixed with an approved adhesive of a thickness not exceeding 4 mm thick. The grounds to receive adhesive shall be smooth and without any irregularities.

A tile skirting, with the same kind of tiles, shall be provided for all areas where the floor is tiled.

The Tiles are grouted with water-repellent grouting compound.

The tiles used complies with the standards listed in part “Wall- tiling”.

The minimum required conditions that must be met by ceramic tile floors according to some of the above standards are as follows:

- The minimum required chemical resistance of ceramic tiles for laboratories and the rooms in contact with chemicals matters is class LA, while for other rooms it is class A.

- The minimum class of slip resistance at the entrances to buildings and laboratories is R11, and in other areas it is R10, slipperiness classification B.

The execution of works is in accordance with the standard SRPS U.F2.011 Final work in building - Ceramic works - Technical requirements.

## PVC Flooring

PVC flooring shall comply with the respective Local Standard, SRPS EN ISO 10581.

The minimum thickness of the floor covering is 2 mm.

PVC flooring shall be temperature resistant, waterproof, abrasion resistant, flameproof, pigment or colour proof to light, evenly coloured throughout, resistant to chemicals, fats, acids and alkalines, odourless, easily laid and flexible, non-porous and slip proof.

All adhesives shall have suitable properties to ensure a firm and durable bond. They must not adversely affect either the flooring nor the underlays or the base and shall be odourless once applied.

All fillers and levelling compounds shall have a firm and durable bond to the base, provide a good bonding surface for the adhesive and be of suitable property so as to give an adequate support to the covering. They must have no adverse effect on base, adhesive, underlay, or covering.

PVC flooring shall be laid perfectly true and even fixed with approved adhesive edges closely butt jointed. Floor covering shall be bended and shall be, over the PVC cove former, elevated along the wall. On the joint of PVC covering and other finish of the wall it is necessary to place the capping strip. PVC shall be placed by gluing with the adequate attested adhesives.

Colour and pattern are in accordance with the Engineer's choice and selected sample.

## Anti-static Flooring and Computer Room Flooring

Over the cement screed, copper strips are placed, in a grid layout according to the required conditions for electrical conductivity.

Before applying the glue, the substrate shall be coated with an electrically conductive primer.

Gluing Anti static PVC flooring will be by conductive adequate attested adhesives.

Anti static PVC flooring shall be bent and shall be, over the PVC cove former, elevated along the wall in the height of h=150 mm.

In Computer rooms and in areas with a large concentration of cables in the floor, it is necessary to do Anti-static PVC flooring on a property modular flooring system in which square floor panels are fitted into a gridded support overlying a cavity containing power and telemetry cables. The removable panels shall not be less than 50 cm or more than 70 cm square form, and shall be non-conducting and carpeted with anti-static material (PVC).

The grid system and its supports shall be of approved materials, and shall be designed such that the deflection of the floor under personnel loading does not exceed 1 mm at any point.

The Contractor shall, if required, hand over to the Engineer two special tools for lifting anti-static flooring panels.

After installing Anti-static PVC flooring, it is mandatory to measure and prove the electrical resistance of the floor.

## Textile flooring

Materials for laying textile floors must comply with the following groups of local or EN standards:

- ISO 2424, Textile floor coverings — Vocabulary

- SRPS EN 1307, Textile floor coverings - Classification

- SRPS EN 985, Textile floor coverings - Castor chair test

- EN 986, Textile floor coverings - Tiles - Determination of dimensional changes due to the effects of varied water and heat conditions and distortion out of plane

- SRPS ISO 1765, Machine-made textile floor coverings — Determination of thickness

- SRPS ISO 1766, Textile floor coverings — Determination of thickness of pile above the substrate

- SRPS ISO 1763, Textile floor coverings — Determination of number of tufts and/or loops per unit length and per unit area

- SRPS ISO 8543,Textile floor coverings — Methods for determination of mass

Textile floor coverings must be 100% recyclable, permanently antistatic. In accordance with the requirements of the Main Fire Protection Design, they must meet the flammability, smoke density and surface flammability classes.

The minimum thickness of the floor covering is 8.5 mm.

Flooring is laid by gluing with appropriate adhesives to the prepared cement screed base.

The coverings are glued to an absolutely clean and dry substrate with appropriate certified adhesives, which must ensure a firm and permanent bond between the substrate and the floor covering.

In the case of the composition of different types of floors (textile floor-ceramic tile floor) at the same level, install an aluminum molding with a "T" section.

The type of carpet, quality, color and pattern are determined by the Engineer based on the submitted samples.

All carpet joints must be made completely straight, without noticeable deviations in color, pattern, weave and direction of stretching of the fibers. Built-in extensions, in rooms where width and length dictate, must not be narrower than 500mm.

Along all perimeter walls, if the project does not specify otherwise, it is planned to install a PVC skirth.

## Aluminum entrance mat

Aluminum entrance mat, made of rubber and aluminum strips shall be provided at the entrances of buildings. It is installed in a frame placed in the floor and made of stainless steel. The mat can be removed from the frame for cleaning. Slip resistance minimum R11 as per DIN 51130.

## Industrial flooring with additive spread

Industrial flooring system must be applicable for middle to heavy traffic load and should provide following:

- High wearing resistance

- Endures very heavy loads

- Extremely sturdy

- Impact resistant

- Easy to clean and maintain

- Oil and hydro-carbonate resistant

- Homogeneous, smooth and anti-slip surface

- Noncorrosive product – surface does not require any special treatment

- Light additional sealing is possible, although the surface does not require any special treatment

The floor system is performed on fresh concrete (the reinforced-concrete flat base slabs) with dry shake topping.

The top layer should be made of mineral granular grit, which is a specially designed compound of hydraulic binder, specially selected quartz sand, corundum based synthetic aggregates and of special additives.

The concrete quality, type and quantity of reinforcement shall be determined in design documentation (static calculation), but minimum concrete class is C30/37.

The finish layer of the mineral grit shall be applied to the fresh concrete and smoothened with the mechanical trowel to the trowelling finish.

On work interruptions of concrete, it is necessary to install the metal formwork with the openings for key joints and installation of the necessary key joints with the sliding pipe on one side. The slitting of "joints" shall be done at 1/3 of the slab thickness when the concrete reaches the necessary strength. The joints shall be filled with the acrylic putty. The finished floor shall be treated with the anti-dust coating.

The floor system has to be protected right after the process of production, i.e. covering with PE foil along with the humidity control during 7 days minimum.

The Control of the flatness of the finished floor system is carried out according to DIN 18202, table 3. For permitted deviations of the flatness of the floor, depending on the requirements for the accuracy of any equipment that is installed on the floor system, the data from a certain row of the table will be applied.

## Granolithic Flooring

Granolithic flooring shall have a minimum thickness of 75 mm.

## Workmanship

Floorings shall be placed without underlays unless otherwise specified. The courses shall be laid towards the main window wall, in halls and corridors, however, in longitudinal direction, unless otherwise specified.

Deviations in colour which are not of minor importance and not due to the flooring pattern shall not be allowed if marring the overall appearance of the flooring. Courses with pattern repeats shall be laid so as to suit these.

Where courses run towards doors, recesses and the like, they shall be laid so to cover also the floor areas such door openings, recesses etc. Strips of slabs may be used as coverings of such floor areas.

# SIGNS

Room designation sign, name plates and fire exit direction signs shall be made from engraved plastic laminate, screw fixed in required positions. All signs shall be in Serbian lettering to the approval of the Engineer.

# SANITARY SYSTEM

## Scope of Work

The work covered under this section comprises the providing of all design, labour, materials, equipment, accessories, and installation and testing, necessary and requisite for complete and adequate systems.

The Contractor shall submit full details, together with drawings, of his proposals for approval of the Engineer before commencing the work and shall carry out all tests and inspections of the finished work as may be considered necessary by the Engineer.

The word “complete” whenever used in these specifications shall mean, in addition to the major items of plant, all the incidental sundry components necessary for the complete operation of the installation, whether or not these components are mentioned in details. The word "piping" in these specifications shall mean the inclusion of all pipes, fittings, valves, and all required accessories, supports, anchors, guides, etc. for a complete, safe and operational network.

## General

All materials and equipment provided by the Contractor shall be new and of the various qualities as required by these specifications.

All workmanship shall be of the highest standard and to the satisfaction of the Engineer.

## Pipes and Fittings

The materials to be used for piping shall be of materials specified within Employer’s Requirements and in accordance with relevant standards.

## Joints and Connections

Joints and connections in the sanitary system shall be gastight and watertight for the pressure required by test. Leaky joints shall be remade by using new materials. Welding and bending are strictly prohibited on galvanized pipes.

Joints in PVC pipes shall be made with rubber rings and shall be carried out according to the manufacturer's recommendations.

## Unions

All galvanized steel distribution pipes shall be provided with unions at adequate intervals to permit easy disassembly for alterations and repairs.

Unions shall be provided near valves and equipment which need to be taken out for servicing or repairs. The unions shall be of material corresponding to the pipes in which they are installed, and of the same weights and eating.

## Hangers, Spacing and Support

Piping shall be installed without undue strains and stresses and provisions shall be made for expansion, contraction and structural settlement. A sufficient number of horizontal and vertical supports shall be provided at proper intervals.

## Manholes and Inspection Pits

The dimensions of the manholes or inspection pits shall be as approved by the Engineer.

## Sleeves

The Contractor shall furnish and install all sleeves to be built in for the passage of pipes through structures.

The Contractor shall co-ordinate placing of the necessary sleeves, of the appropriate sizes for his requirements, at the time the concrete is being poured. It is strictly prohibited to break through reinforced concrete beams for the passage of pipe unless prior approval is obtained.

Pipe sleeves shall be of adequate size to allow free movement of pipes due to expansion and contraction, whether bare or insulated.

Pipe sleeves shall be finish flush with floors and roofs and shall project at least 3 cm above floors and approximately 15 cm above roofs or as otherwise agreed by the Engineer.

After the installation of pipes, the Contractor shall caulk the space between pipe and sleeve with an approved product to prevent the passage of air and vermin. The caulking shall be made in such a manner as to prevent it from coming off with pipe expansion or contraction.

## Protection and Cleaning

The inside of all pipes, valves, etc. shall be clean and free from dirt or other objectionable matters when erected. All lines shall be blown before placing in service. If necessary, all openings in the piping shall be closed during construction in order to keep the lines free from dirt, etc.

## Installation of Pipes

Pipes passing through walls shall be protected from breakage. A soil or waste pipe passing through a foundation wall shall be fitted into a PVC-pipe cast in the concrete and furnished with sockets at both ends. The length of the cast-in pipe including sockets shall be according to the thickness of the wall. No piping shall be laid parallel to footings or outside bearing walls closer than 1 m. Water service pipes or any underground water pipes shall not be run or laid in the same trench as the sewer lines.

Drainage pipes can be allowed to discharge at a height of 450 mm maximum above the bottom of a manhole. If the vertical drop in the manhole should exceed 450 mm, a drop manhole shall be used. Where it is required to cut rigid pipes, it shall be done by a suitable pipe cutter so as to leave a clean and square end to the axis of the pipe.

## Inspection, Storage and Connections

All pipes shall be thoroughly inspected prior to laying and any suspected cracks or damaged material shall be rejected. The pipes shall be stacked horizontally during storage and the sockets must be prevented from resting on the ground. All connections shall be made watertight and gastight. Where vent pipes connect to a horizontal soil or waste pipe, the vent shall be taken off above the centre-line of the pipe, and the vent pipe shall rise vertically.

No work of breaking into an existing public sewer and forming a connection shall be carried out until after prior indication and approval of the Engineer. Breaking into a sewer shall be effected by a careful enlargement of a small hole, and every precaution shall be taken that no material shall enter the main sewer.

If any bedding or protection is removed to make a connection into a sewer or drain, the damage shall be made good.

It is preferable to connect into sewers at existing manholes wherever possible.

## Main Cold Water Supply Pipe

The Contractor shall furnish and install the main water supply pipe from the nearest source.

The main shall be buried with a minimum cover of about 800 mm, unless otherwise ordered by the Engineer.

## Water Distribution and Plumbing

The Contractor shall obtain the Engineers approval to his proposal for the potable water distribution system on the Site.

When galvanized steel pipes used underground all pipes and fittings shall be coated with coal tar enamel and the threaded joints shall be coated and wrapped after installation and testing. All precautions shall be taken to protect water supply and distribution pipes against contamination from the sanitary system.

Underground water service pipes and sewer lines shall be not less than 1 meter apart horizontally and shall be separated by undisturbed or compacted earth when they cross each other. Concealed pipes shall be installed in such a way as to permit easy access for maintenance. This applies particularly to valve locations.

All valves shall be fixed in neatly arranged vertical lines and adequately pitched horizontal lines to allow the system to be properly vented and drained. Air pockets, traps and sags shall be carefully avoided. Pipes shall not be welded.

Gate valves shall be provided on all main and branch pipes for isolating sections of piping for maintenance. Each sanitary fixture shall be provided with a stop valve for washer replacement. The stop valve shall match the trim provided with the fixture.

The Contractor shall install hot and cold water plumbing systems, generally conforming to:

- SRPS EN 806-1 Specifications for installations inside buildings conveying water for human consumption - Part 1: General

- SRPS EN 806-2 	Specification for installations inside buildings conveying water for human consumption - Part 2: Design

- SRPS EN 806-3 Specifications for installations inside buildings conveying water for human consumption - Part 3: Pipe sizing - Simplified method

- SRPS EN 806-4 Specifications for installations inside buildings conveying water for human consumption - Part 4: Installation

## Testing of Sanitary System

The sanitary system shall not be accepted until it has been tested as specified below. All tests shall be conducted in the presence of the Engineer. No part of the sanitary system shall be painted, covered or enclosed until it has been tested, inspected and accepted. All equipment, materials, instruments and labour necessary for testing and inspection shall be provided by the Contractor, to execute the work as directed.

## Pressure Tests of Drainage

The piping of the drainage system shall be tested with water. After the fixtures have been set and their traps filled with water, the entire drainage system shall be submitted to a final test. The water test shall be applied to the drainage system in its entirety or in sections. If applied to the entire system, all openings in the piping shall be tightly closed, except the highest opening, and the system filled with water to the point of overflow. If the system is tested in sections, each opening shall be tightly plugged except the highest opening of the section under test. Each section shall be filled with water but no section shall be tested with less than 3 meters head of water.

The Contractor has to install temporarily a pipe of 3 meters height in order to apply 3 meters head at the uppermost sections of the system. The water shall be kept in the system, or in the portion under the test, for at least 4 hours before inspection starts. The system shall then be tight at all points.

Underground sewers outside the building shall be tested by plugging the end of the sewer pipe filling with water, and testing with not less than 3 meters head of water.

## Pressure Tests of Water Supply Pipes

Upon completion of the potable water distribution system, it shall be tested and proved tight under a water pressure of 10 bar or 150% of the working pressure, whichever is higher. Care shall be taken that no appliance or fitting shall be pressurised higher than its rating. If such an appliance is included in the testing circuit, it shall be blinded prior to applying the pressure. A hand pump shall be used for this purpose. All lines shall be properly plugged or capped, making sure that all air has been vented from the system before pressure is applied. The pressure shall remain constant without pumping for a period of eight hours.

If any leaks in joints or evidence of defective pipe or fitting is disclosed, the defective work shall be immediately corrected by replacing defective parts with new joints or materials. No makeshift repairs or application of patching compounds shall be permitted. After the correction is made, supplementary tests shall be run until a satisfactory working condition is obtained.

## Flow Test

A flow test shall be made of all the sanitary system components and in case any obstructions are encountered in the piping or equipment, the Contractor shall disassemble, clean, repair and reassemble such piping or equipment.

A watertight test for sleeves and the passage of pipes through floor and roof shall be made. The contractor shall repair any leaks.

## Cleaning and Disinfection of the Pipelines

The cleaning and disinfection shall take place with requirements of local PUC, or in accordance in four stages complying with AWWA C651:

### Preliminary Flushing

All pipes from 100 to and including 600 mm diameter shall be preliminarily flushed at least once at high rates of flow (velocity shall exceed 1.5 m/sec). The Contractor shall prepare a flushing plan and submit it to the Engineer for approval.

### Cleansing

All pipes shall be cleaned with clean water for duration of at least five minutes at a rate of flow sufficient to obtain a velocity exceeding 1 m/sec. This cleansing procedure shall be repeated until any trace of taste or smell has disappeared from the water.

### Disinfection

Following the satisfactory cleansing the Contractor shall with the use of a portable dosing system or by some other approved method introduce a solution of a sterilizing chemical containing chlorine into the pipeline. The solution shall be introduced at a very slow rate and shall be of such strength as to give a chlorine concentration of not less than 50 parts per million (ppm) throughout the length of the pipelines.

All fire hydrants (or tees where appropriate) on the distribution system shall be opened successively, working progressively away from the place where the solution is introduced. Each hydrant shall be closed when the water discharged begins to smell of chlorine. The whole system shall then remain charged for 24 hours, after which the water shall show a residual chlorine contents of not less than 10 ppm. If no residual chlorine is found or if the residual chlorine is less than 10 ppm, the sterilization process shall be repeated until a satisfactory result is obtained.

### Bacteriological Testing

After the disinfection period of 24 hours the water shall be evacuated from the pipes and the pipe system shall then be refilled with potable water having a concentration of residual chlorine of about 0.1 ppm. A number of water samples to be determined by the Engineer shall then be taken and subjected to laboratory tests for coliform bacteria. If the tests show presence of coliform bacteria, the whole cleaning and disinfection process from preliminary flushing shall be redone until the result is negative.

The Contractor shall in his rates and prices for pipe laying include for all costs of labor, transport, materials, equipment, chemicals and water necessary for the satisfactory completion of the cleansing and sterilization operations.

# ROADWORKS

The standards applied to the roadworks are ICS 93.080, and for certain elements of roadworks (but not limited to):

|  | SRPS EN 1340 | Concrete kerb units - Requirements and test methods |
| --- | --- | --- |
|  | SRPS EN 1339 | Concrete paving flags - Requirements and test methods |
|  | SRPS EN 1338 | Concrete paving blocks - Requirements and test methods |
|  | SRPS EN 13877 | Concrete pavements |
|  | SRPS EN 12697 | Bituminous mixtures - Test methods for hot mix asphalt |
|  | ICS 93.080.20 | For making of bitumen / asphalt pavements |
|  | ICS 93.080.30 | For road drainage and equipment |
|  | SRPS EN ISO 22475 | Geotechnical investigation and testing - Sampling methods and groundwater measurements |
|  | SRPS CEN ISO/TS 17892 | Geotechnical investigation and testing - Laboratory testing of soil |
|  | SRPS EN 13286-47 | Unbound and hydraulically bound mixtures - Part 47: Test method for the determination of California bearing ratio, immediate bearing index and linear swelling |
|  | SRPS EN 1341 | Slabs of natural stone for external paving - Requirements and test methods |
|  | SRPS EN 1343 | Kerbs of natural stone for external paving - Requirements and test methods |
|  | SRPS EN 1936 | Natural stone test methods - Determination of real density and apparent density, and of total and open porosity |
|  | SRPS EN 13108 | Bituminous mixtures - Material specifications |
|  | SRPS EN ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles - Specifications and test methods |
|  | SRPS EN ISO 2081 | Metallic and other inorganic coatings - Electroplated coatings of zinc with supplementary treatments on iron or steel |
|  | SRPS EN ISO 2082 | Metallic and other inorganic coatings - Electroplated coatings of cadmium with supplementary treatments on iron or steel |

## Geodetic Works

The Contractor shall, prior to the commencement of works, on the basis of the design and the accepted terrain, survey cross sections and notify the Engineer service about possible discrepancies, which will specify that in the job record.

The Contractor shall receive from the Employer /Engineer in the field the staked out route with all the necessary written data. The route in the field must be marked by wooden 4 x 4 cm stakes, steel 0 10 mm pegs or cut in stone with a chiselled cross, which must be painted with minium or red oil paint.

The main points on a stake must have a nail.

On the right-hand side in the direction of the chainage, at a distance of 20 cm from a stake, there shall be a wooden table with the marking of the number of the cross section.

Hand over shall be carried out with the takeover minutes. The staked out axis shall be at spacing’s, which are determined by the characteristics of the terrain, but not exceeding 30 m.

The Employer/Engineer shall hand over to the Contractor in the field polygonal points for which concrete 12x12x50 cm stakes shall be used with a hole in the middle and underground center, or a pipe 2.5 cm in diameter (one inch) in inhabited places, or on roads. In special cases, traverse points shall be cut in stone and marked with a cross. The traverse system shall be tied to trigonometric points calculated with a deviation in accordance with the Rulebook for I Class Traverse Network.

Upon completion of road foundation, the Contractor shall restore the route (layout-wise and level-wise) based on the sketch of staking out with traverse points. The accuracy of the restored route shall be inspected by the Engineer.

The axis shall be restored prior to placing of asphalt concrete or concrete carriageway.

  - Demolition and removal of road facilities

The works include:

- demolition and removal of road surface,

- scraping and transport of asphalt surfacing,

- cutting asphalt layers,

- demolition and removal of curbs.

All works within demolition and removal of the existing road facilities are to be specified in detail in plans. Each deviation is to be approved by the Engineer.

All the works within demolition and removal of road and other facilities are to be executed with minimum damage to the adjacent facilities, vegetation and the remained roadway, while the demolition area is functional for purposes envisaged by the project and provisions specified by the Engineer.

Removal of curbs, dismantling of crossing facilities, buildings and similar obstacles is to be performed in the manner that such obstacles are completely removed so there are no obstacles remained to disturb proper execution of works, nor ones affecting the esthetical appearance of the road and surroundings.

## Top Soil Stripping

Within the belt covered by the earth work and on borrow pits, top soil shall be stripped in a layer of designed thickness and maximum in a layer 50 cm thick. If, in the course of work, it is established that it is necessary to strip the top soil in a thicker or a thinner layer, the Engineer shall record the change in the daily diary, and the Contractor shall act upon it.

Stripped top soil shall be deposited on both sides of the road belt in approximately regular shape. Top soil must not be used to make the fill. Instead, upon completion of earth works, it shall be used to cover slopes, ditches, shoulders, and borrow pits.

Surplus top soil shall be transported to the place designated by the Engineer.

## Bulk Excavation of Soil

Prior to commencement of works, the Contractor shall exercise control of designed cross sections and notify the Engineer about possible discrepancies, who shall exercise repeated control together with the Contractor. The necessary amendments must be made in the cross sections and the amendments made shall be recorded in the daily diary. Amended cross sections shall be signed by the Contractor – the site manager and the Engineer whereby correctness of cross sections for the payment certificate shall be recognized.

Bulk excavation of soil shall be carried out up to the level of the road foundation and with right grades and flat slopes corresponding to the designed ones, or to the established levels established during the work.

Accuracy of excavation must be ± 5 cm, and extra excavated quantities shall not be paid for.

The Contractor shall make the necessary corrections where exceeding the tolerance of ± 5 cm at its own cost.

Intersections of slopes with the terrain shall be rounded fully in compliance with the details from the design.

Prior to and during the work, on all changes in excavation, or the quality of changed materials, corresponding samples shall be taken for testing of usability of materials for the intended purpose.

A certificate shall be obtained from an authorized institution concerning the usability of materials from every considerably bigger cutting.

## Distribution of Earth Quantities and Stockpiles

According to the design, for execution of the fill, material from excavation for facilities shall be envisaged, and disposition and place of the borrow pit shall be determined by the Engineer on the spot depending on whether the construction is phased. The material for which it is proven that it is inadequate for construction of the road structure must be eliminated. The Contractor shall form the stockpile where it is designated by the Engineer.

## Treatment of Subsoil

After top soil stripping on the parts underneath the fill, compaction and possible previous ripping of earth shall be carried out for the purpose of drying or wetting of natural soil to the thickness that is determined in the design of approximate thickness of around 30 cm.

Maximum compactness of virgin soil shall be required according to the standard Proctor procedure to a layer thickness of 30 cm specifically:

- For the subsoil underneath the fill of the height up to 2.0 m measured from the level of level reference line of the carriageway

- 100 % of the maximum laboratory compactness according to the standard Proctor procedure

- For the subsoil underneath the fill over 2.0 m measured from the level of the level reference line of the carriageway, 95% of the maximum laboratory compactness according to the standard Proctor procedure

- Quality control of compactness of the subsoil may also be exercised, in case of loose materials, using the test plate Ø30 cm according to the Swiss regulations SNV 40317 whereby the minimum value of the modulus of compressibility of MS = 30.000 – 40.000 KN/m2 shall be required.

- Required individual values of the modulus of compressibility within given limits shall be determined by the field geomechanics laboratory based on bulk densities, granulometric composition.

- Test by the plate should be made on materials the humidity of which is closed to the optimal one.

- For testing of subsoil compactness using the plate, the Contractor shall put at the disposal free of charge a vehicle or a machine weighing over 5 tons, as counterweight during performance of the test.

- Quality control of materials shall be conducted prior to treatment of subsoil for every change of material, or at every 4,000 m2 and shall be exercised in accordance with relevant standards.

- Control of treated and compacted subsoil shall be exercised at every 50 m in accordance with relevant standards.

## Construction of the Fill – Replacement Layer

Spreading of materials for construction of the fill shall be done in layers of 20-30 cm depending on applied mechanical means of compaction, whereby the required degree of compaction must be achieved on the entire length of the layer made.

Manual compaction shall not be allowed.

When executing the fill the layers shall be given double-sided or one-sided inclination of 3 – 5 % for the purpose of a better drainage of precipitation. For the reason, when work is interrupted, when there are chances for rain, the surface of the compacted layer shall be rolled using smooth wheels.

The height of every individual consecutive layer shall be in line with the effect of compaction, or the depth effect of applied means of compaction, type of materials, and segregation phenomena.

If there are requirements and possibilities to place the fill in layers thicker than 30 cm, then the Engineer service may approve such a request if the Contractor meets the following requirements: on the test section 30-50 meters long using mechanical means to carry out compaction of the fill, the thickness, mechanical means, number of travels, properties of materials with the humidity and compaction at five places shall be established out of which minimum two in the lower half of the layer.

Based on results, the Engineer shall record the necessary results and issue order through the daily diary. These costs of work on the test road section shall be borne by the Contractor, whereby the constructed layer of the fill, if it is on the route and if compaction is satisfactory, shall be recognized as the executed fill.

If there are no verified experiences concerning possibilities of compaction of certain materials and means of compaction, the thickness of the layer shall also be determined on the test section.

Based on the testing of the test section for each type of materials, the layer thickness, mechanical means, number of travels, physical and mechanical characteristics of materials (humidity, bulk density, the modulus of compressibility) shall be established.

The Employer shall record the necessary findings in the daily diary.

Extra costs of work on the test section shall be borne by the Contractor, whereby the constructed layer of the fill on the test section, if satisfying the criteria of compactness, shall be recognized as the executed fill.

Wherever possible, control of achieved compactness of executed layers shall be exercised according to the standard Proctor procedure whereby the following levels of compactness shall be required:

- For the fill layers of height of up to 2.0 m measured from the level of the level reference line of the carriageway, 100 %, for loose and bound materials, of the required maximum compactness.

- For the fill layers of height above 2.0 m measured from the level of the level reference line of the carriageway, 95 %, for loose and bound materials, of the required maximum compactness.

The finished fill must have designed slopes, of the width and dimensions with the accuracy of ± 5 cm. Widths and slopes shall be measured after stripping of a possible layer from the slope, which shall not be paid for separately because that work is calculated in the price of the finished compacted fill.

If materials for the fill contain a higher percentage of humidity than the optimal one, drying of the spread layer should be waited for any only then it shall be proceeded with compaction.

Wider and higher executed fills due to error of the Contractor shall not be calculated, and the Contractor shall carry out proper adjustment to the designed dimensions with the accuracy of ± 5 cm.

## Quality Control Concerning the Fill

For execution of the fill, inorganic materials of certain qualities and cuttings, cuts, borrow pits or dumpsites may be applied.

Quality control of materials for the fill shall be exercised according to the relevant standards:

- SRPS EN ISO 17892 - Geotechnical investigation and testing - Laboratory testing of soil

- SRPS CEN ISO/TS 22475- Geotechnical investigation and testing - Sampling methods and groundwater measurements

- SRPS EN 12697-5 - Bituminous mixtures - Test methods - Part 5: Determination of the maximum density

- SRPS EN 933-1 - Tests for geometrical properties of aggregates - Part 1: Determination of particle size distribution - Sieving method

- SRPS U.B1.016 - Testing of soils - Determination of density of soil in place by rubber balloon method

- SRPS U.B1.024 - Testing of soils - Determination of the combustible and organic matter content of a soil

- SRPS EN 13286-1 Unbound and hydraulically bound mixtures – Part 1: Test methods for laboratory reference density and water content – Introduction, general requirements and sampling

- SRPS EN 13286-2 Unbound and hydraulically bound mixtures – Part 2: Test methods for laboratory reference density and water content – Proctor compaction

- SRPS EN 13286-47 - Unbound and hydraulically bound mixtures - Part 47: Test method for the determination of California bearing ratio, immediate bearing index and linear swelling

- SRPS U.B1.046 - Testing of soils - Determination of compression modulus by circular slab method

- SRPS EN 1744-1 - Tests for chemical properties of aggregates - Part 1: Chemical analysis

Tests shall be performed for every change of materials, or at every 4,000 m of the executed fill.

### Criteria for assessment of quality of material for the fill

On the stretches along the route where the fill is executed over previously treated, compacted, and accepted subsoil, materials that meet the following criteria may be applied:

- Maximum bulk density according to the standard Proctor test of Wopt 25 %.

- Liquid limit W must be below 65 %

- Plasticity index JP must be below 30 %.

### Control of treated and compacted layer of the fill

Control of treated and compacted layer of the fill shall be exercised by determining the degree of compactness at every 50 m according to the relevant standards (stated above).

Repetition of the test due to unsatisfactory results shall be at the expense of the Contractor.

## Mechanically Stabilized Underlying Load-Bearing – Subbase Layer

This work shall include procurement and placing of materials for load-bearing layers at places designated in the design.

All the work must be carried out in compliance with these technical requirements and required dimensions.

All works and materials shall be in accordance with the relevant standards.

Applicable standards are (but they are not limited to):

| - SRPS EN 933-4 | Tests for geometrical properties of aggregates - Part 4: Determination of particle shape - Shape index |  |
| --- | --- | --- |
| - SRPS EN ISO 17892-4 | Geotechnical investigation and testing - Laboratory testing of soil - Part 4: Determination of particle size distribution |  |
| - SRPS EN ISO 17892-1 | Geotechnical investigation and testing - Laboratory testing of soil - Part 1: Determination of water content |  |
| - SRPS EN 1936 |  | Natural stone test methods - Determination of real density and apparent density, and of total and open porosity |
| - SRPS U.B1.016 |  | Testing of soils - Determination of density of soil in place by rubber balloon method |
| - SRPS EN 13286-1 |  | Unbound and hydraulically bound mixtures – Part 1: Test methods for laboratory reference density and water content – Introduction, general requirements and sampling |
| - SRPS EN 13286-2 |  | Unbound and hydraulically bound mixtures – Part 2: Test methods for laboratory reference density and water content – Proctor compaction |
| - SRPS U.B1.046 |  | Testing of soils - Determination of compression modulus by circular slab method |

### Materials

For mechanically stabilized underlying load-bearing – subbase layers, gravel or stone crushed materials shall be used.

Gravel materials shall consist of grains of gravel, sand and filling, in such a ratio that the requirement from relevant standard shall be met, depending on the size of the biggest grain in the material.

Crushed stone material shall consist of grains of crushed stone material, which as required may be added to the natural material, in order to get the required granulometric composition according to relevant standard. Mixing of materials can be done when sieving and crushing.

#### Quality of Stone Material

Materials for mechanically stabilized underlying load-bearing – subbase layers must be composed of grains that correspond to prescribed requirements according to the following:

| Item No | Type of Testing | Required Results |  |
| --- | --- | --- | --- |
|  |  | Gravel-sand Aggregate | Crushed Aggregate |
| 1 | 2 | 3 | 4 |
| Stone Testing |  |  |  |
| 1 | Compression strength | - | Min.1200 kp/m |
| 2 | Water absorption | - | Max. 1 % |
| 3 | Stability in Frost | - | Stable after 25 cycles |
| 4 | Abrasion according to Los Angeles | - | Max. 40 % |
| 5 | Mineralogical-petrographic analysis | - | Meeting |
| 6 | Opinion on usability | - | Favourable |
| Aggregate Testing |  |  |  |
| 1 | Grain shape | Unfavourable up to 50 % | Unfavourable up to 40 % |
| 2 | Dilapidating grains | Up to 7 % | Up to 7 % |
| 3 | Contents of sludge – clayey and organic particles | Up to 5 % | Up to 5 % |
| 4 | Sensitivity to effect of frost (particles of 0.02 mm) | According to relevant standard | According to relevant standard |
| 5 | Stability of aggregate in frost | Stable, loss in weight | Stable, loss in weight |
|  | - For a fraction of up to 8 mm | Up to 10 % | Up to 10 % |
|  | - For a fraction in excess of 8 mm | Up to 12 % | Up to 12 % |
| 6 | Bulk density | Subject to the origin of material | Subject to the origin of material |
| 7 | Specific weight | “ | “ |
| 8 | Granulometric composition | According to relevant standard | According to relevant standard |
| 9 | Degree of unevenness | Min.15 | Min.15 |
| 10 | Abrasion according to Los Angeles | Max. 50 % | Max.40 % |
| 11 | Mineralogical-petrographic |  |  |
|  | analysis |  |  |
|  | a) Composition of rocks and minerals in weight percentages | Meeting | Meeting |
|  | b) Appearance of grain surface in weight percentages | Meeting | Meeting |
|  | - Rough, fine to coarse |  |  |
|  | - Smooth-glass-like |  |  |
|  | - Cellular |  |  |
|  | c) Degree of grain alternation | Meeting | Meeting |
|  | - Fresh |  |  |
|  | - Poorly alternated grains |  |  |
|  | - Dilapidating grains |  |  |
|  | d) Opinion on usability | Favourable | Favourable |
| 12 | Opinion on usability on the basis of all tests completed | Favourable | Favourable |

The mineralogical-petrographic analysis should provide share of certain types of rocks by types and quantities, particularly of those that are considered to be unfavorable for the pavement structure (marl, clayey slates, soft clayey sandstones, dilapidated rocks, conglomerates, gneisses).

Based on the mineralogical-petrographic analysis and mineralogical-petrographic spectrum further to Exhibit 1 (for a mixture, and not by fractions), data in point 11 of this overview shall be processed. For every certificate of previous testing, minutes of taking samples shall be submitted signed by the Engineer, authorized persons of the institution that conducts the testing of the Contractor.

Mineral aggregate for the underlying load-bearing layer (subbase) shall be considered to meet requirements with respect to sensitivity to effect of frost (share of particles of 0.02 mm) if it meets the requirements as follows:

- Percentage of particles below 0.02 mm calculated on the whole mass of dry mixture may amount to maximum 6 % for the lower, and 10 % - 12% for the upper limit, in case the content of coarse fractions ranges from 0-80 % of the dry mass of the entire mixture.

- If the content of coarse fractions is from 80 – 90 % of dry mass of the entire mixture, then the lower limit of particles below 0.02 mm with respect to the entire mixture may amount to 6-3 %, and the upper limit 10-5 % and over, if it meets the requirement with respect to swelling.

The lower limit yields the share of particles below 0.02 mm in a binder that can be tolerated, and thereby there should not occur any damage of the road base because of the effect of frost under the most unfavorable conditions with respect to soil humidity, ground water level, etc. The upper limit yields the biggest share of finer particles of 0.02 mm that can be tolerated and that thereby there should not occur any damage of the road base due to the effect of frost, under favorable conditions with respect to soil humidity, ground water level, climate, and the like.

| Square sieve aperture in mm | Mark of coarseness |  |  |
| --- | --- | --- | --- |
|  | 0.35 | 0.50 | 0.60 |
|  | Sieving through the sieve of weight % with respect to the weight of total material |  |  |
| 0.09 | 0 - 12 | 0 - 8 | 0 - 8 |
| 0.2 | 3 - 11 | 2 - 13 | 2 - 12 |
| 0.63 | 8 - 30 | 6 - 21 | 5 - 19 |
| 2.0 | 18 - 48 | 13 - 34 | 11- 29 |
| 5.0 | 32 - 65 | 23 - 48 | 21- 42 |
| 8.0 | 40 - 75 | 21 - 57 | 27- 50 |
| 12.5 | 51 - 84 | 41 - 68 | 27- 59 |
| 18.0 | 61 - 92 | 51 - 78 | 46 - 67 |
| 25.0 | 71 -100 | 61 - 88 | 55 - 76 |
| 35.00 | 84 -100 | 74 -100 | 67 - 87 |
| 50.00 | 100 | 90-100 | 82 -100 |
| 60.00 | 100 | 100 | 90 -100 |
| 70.00 | 100 | 100 | 100 |

Note on Table:

Granulometric composition for the underlying load-bearing (subbase) layer may also be used in other boundary curves, if a positive opinion has been given for them by a registered institution and designer of the pavement structure, whereby the consent to this shall also be given by the Employer. At the beginning of placing on the test section 50/100 meters long, the following shall be established: granulometric composition, degree of unevenness in compacted condition, achieved compactness (5 min results), straightness measured by ropes or crosses, data on plant and equipment (type and number of machines, number of travels of every machine and with which vibrations).

If stone material, in compaction, is prone to re-crushing, in addition to the above data, additional tests shall also be conducted by taking samples from the place where compactness was measured, specifically:

- Sensitivity in frost – frost effects

- Contribution of particles of 0-2 mm in granulometric composition and Los Angeles in all gradations.

Minutes for the test section shall be signed by the Contractor and the Engineer. Based on the above results and the point on quality control from these technical requirements, the Engineer shall give the necessary documents to the Contractor.

### Execution

#### Supply of Materials

The place from which the Contractor shall provide the material for the underlying layer must be reported to the Engineer prior to commencement of exploitation.

Borrow pits of materials and quarries must be previously well cleaned from waste rock and other noxious materials.

#### Preparation of road foundation surface

Road foundation surface – formation level of substructure must be prepared prior to the commencement of placing of materials of the base course in line with the requirements of the design and the point in which the road foundation is dealt with in these requirements.

#### Transportation of material for the underlying load-bearing layer

On adequately prepared surface of the road foundation, it may be started with delivery of subbase material immediately upon acceptance of the road foundation and with the consent of the Engineer. As a rule, transportation of material may not be affected on the prepared and taken over the road foundation – formation level of the road bed, but by the frontal and lateral tipping off on the already spread layer of material for the load-bearing layer.

#### Adding of material

In case of a need to add materials for the purpose of improving of granulometric composition according to the requirements of this description, additional materials must be evenly spread using adequate units for spreading, which must be tested at the request of the Engineer.

#### Mixing and Trimming

After spreading of every layer of the load-bearing layer of material, necessary adding of material in the layer shall be performed using adequate machines which shall be approved by the Engineer. During the mixing of material adequate quantity of water shall be evenly added in order to provide the optimal humidity of materials required for compaction.

Homogenized mixture shall be levelled according to the Design.

As a rule, levelling and compaction of the mixture must be done on the same day as mixing.

#### Compaction

After completing the mixing and trimming, every layer must be compacted along the entire width using rollers with smooth steel or rubber wheels, or using vibro-tampers. Rolling must be done from a lower edge towards the higher one. The number of travels of rollers needed for optimal compaction of layers has been determined earlier subject to the quality control for the subbase layer. Compaction of materials must be controlled through current tests.

All irregularities established during the rolling must be eliminated at the request of the Engineer.

Places inaccessible by the roller must be compacted to the required compactness using other means for compaction, the use of which shall be determined by the Engineer who shall on that occasion also determine the conditions in which such means should be used.

The thickness of compaction of the underlying load-bearing layer (subbase) shall be determined by way of the test section.

#### Depositing of materials

If the Contractor deposits subbase material prior to placing, it shall be necessary to previously adequately prepare and clean that space.

### Method of Control and Criteria for Quality Assessment

#### Compaction

Usability of means of compaction and the technological procedure must be previously tested by way of the test section according to the following:

- Compactness and density of the constructed underlying load-bearing layer shall be determined by testing according to Proctor (SRPS U.B1.046). Density of placed material shall be determined on minimum 5 samples according to Proctor and with minimum 30 measurements using isotopes (if they are used) on a part of the road 50 – 100 m long.

- When placing, minimum 100 % must be obtained of average value f density according to the specified Proctor procedure.

- Minimum required values of the modulus of compressibility MS measured using round plate of 0 16 cm shall be 80,000 kN/m² if, on the underlying load-bearing subbase layer, there comes the upper load-bearing layer 10 cm or less thick, then the minimum modulus of compressibility should be 100,000 KN ⁄ m2

- If the underlying load-bearing layer is done in a number of layers of the same or of inter-layers, MS shall be established by means of the test section with the aim to achieve the required modulus of compressibility on the finish layer. Minimum control tests that shall be conducted shall include:

- Testing of the level of compactness and humidity of the materials and tested layer at every 500 m² using densitometers with a membrane or sand (as required)

- Testing of bearing capacity of a layer at every 60 – 100 Of the road (test with the plate), as the result, two measurements made in close vicinity shall be taken.

- Testing of the granulometric composition of materials from a layer at every 4000 m² and, in case of change of granulometric composition, even more frequently.

- Testing of sensitivity of the subbase on frost effect; this test shall be conducted at every 4000 m² of the placed layer.

In case the Engineer, on the occasion of the following control tests, establishes bigger deviations from the result, the scope of tests may also be subsequently changed.

Compactness of a constructed layer may also be determined by applying other recognized methods. In such a case, the Engineer must specify criteria for assessment of compactness.

#### Layer Evenness

The surface of the subbase layer may deviate from the measured plane maximum 10 mm, measured with a rope or crosses in an arbitrary direction, on the road axis. Measuring points and the method of measurement of evenness shall be determined by the Engineer, whereby measurement shall be made minimum on every section.

#### Levels

Levels of the underlying load-bearing layer may, at any taken place, deviate from the designed ones by maximum + 10 mm. Levels of individual measured points must be determined by benchmarking on cross sections.

### Acceptance of Constructed Load-bearing Layer

The Engineer shall accept the constructed layer according to the criterion from the design and the point on control and criteria for assessment of quality from this description. The Contractor shall eliminate and make good all the deficiencies with respect to the specified requirements.

## Asphalt Pavements

Asphalt pavements shall be made in compliance with the Serbian standards ICS 93.080.20.

### General

- The laying of top bituminous layers, binders and base course shall include the supply of ready mix bituminous material, the placing and compaction of the bituminous material and the removal of surplus material.

- The final re-surfacing of asphalt public roads and pavements are included in the rates and prices.

- The Contractor shall when laying the temporary reinstatement ensure that levels of manholes and surface boxes shall match the final road surface level.

- Asphalt roads within the site(s) shall be surfaced in accordance with these Technical Requirements.

- All the tests required by the requirements of Serbian Road Authority shall be carried out.

### Bituminous Works

Bituminous mixture shall be manufactured until a job-mix formula has been submitted by the Contractor and approved by the Engineer in writing.

The formula shall indicate the exact percentage of each sieve fraction and the exact percentage of bitumen to be used in the mixtures, including the mix temperature. The laying of levels shall include the supply of bituminous material in a quality corresponding to ZTVA-STB, the placing and compaction of the bituminous layer with appropriate machines and the removal of surplus material.

### Weather Limitations

Bituminous courses shall be constructed only when the base is dry and when the weather is not rainy. Such courses shall not be constructed when the atmospheric temperature is below 10°C and falling, but may be constructed when the atmospheric temperature is at least 8°C and rising, unless otherwise directed by the Engineer.

### Preparation

Immediately before applying a bituminous pavement, the surface of the underlying course shall be thoroughly cleaned of all loose or foreign material. The underlying layer shall be coated with a tack-coat of the liquid asphalt rapid curing type. The tack-coat to be used shall be to the Engineer’s approval. The tack-coat shall be applied just sufficiently in advance of the placement of the bituminous top layer asphalt concrete mixture so as to provide a thin adhesive film of bituminous cement to ensure a good bond. Tack coat shall be asphalt emulsion (50% water, 50% bitumen).

The tack-coat shall be uniformly applied by means of a pressure hand spray, in quantities of 0.3 l/m2 of surface, unless otherwise directed by the Engineer. Stakes for alignment control shall be furnished, set and maintained by the Contractor, subject to checking and correction by the Engineer, in order that the works shall conform to the lines shown on the Drawings.

The stakes shall be set in lines parallel with the center line of the area to be paved, offset and spaced, as directed by the Engineer.

Asphalt at the plant shall have min. 150°C just before the delivery.

### Transportation

All bituminous mixtures shall be transported from the mixing plant to the spreader in trucks having tight, clean, smooth beds which have been oiled with a minimum amount of approved thin oil to prevent adhesion of the mixtures to the trucks. Each load shall be covered with canvas, or other suitable material, to protect it from dust or rain, and to prevent the loss of heat. Deliveries shall be arranged so that spreading and rolling of all the mixtures prepared for a day’s run can be completed during daylight, unless artificial light satisfactory to the Engineer is provided. Any excessively wet loads will be rejected. Hauling over freshly laid material will not be permitted.

### Placing

The asphalt pavement shall be constructed in accordance with the thickness as present prior to removal and excavation work or as shown on the Drawings with a minimum thickness as specified. The temperature of each mixture when dumped into the spreader shall be as directed by the Engineer, plus or minus 10°C. Asphalt mixture shall have a minimum of 90°C.

The spreader shall be adjusted and the speed regulated, so that the surface of the course will be smooth and of such depth that, when compacted, it will conform to the cross section shown on the Drawings. The length of any lane before placing the adjacent lane shall be as directed by the Engineer. Where two spreading machines are operating in staggered position, no single lane shall be laid in advance of the adjoining lane further than will permit a satisfactory hot longitudinal joint between the lanes.

Where forming a hot longitudinal joint, the 150 mm strip along the edge against which additional material is to be laid shall not be rolled until such additional material is placed, except when the work is to be discontinued. After the first lane has been placed and rolled, the adjacent lane shall be placed while the unrolled 150 mm strip is hot and in readily compatible condition. Rolling of the adjacent lane shall begin along the joint. Placing of the mixture shall be as continuous as possible.

Rolling shall be carried out using at least two machines, one three wheel roller having a weight of 10 t, and the other rubber wheel roller having a weight of 20 t.

In areas where the use of machine spreading is impractical, the mixture may be spread by hand and dressed with rakes. The loads shall not be dumped any faster than can be properly handled by the shovellers and rakers.

Contact surfaces of previously constructed pavement kerbs, manholes and similar structures shall be painted with a thin tack-coat prior to placing the bituminous mixture.

### Compaction of Mixtures

Compaction shall be effected by three-wheel rollers and tandem rollers.

Rolling of the mixture shall begin as soon as after placing as the mixture will bear the roller without undue displacement. Delays in rolling freshly spread mixtures will not be permitted. Initial rolling shall be effected by tandem rollers, followed immediately by the three-wheel rollers. Rolling shall start at the extreme sides of the lanes and proceed toward the center of the pavement, overlapping on successive strips by at least one-half the width of the rear wheel of the three-wheel roller. On the super-elevant curves, rolling shall begin at the low side and progress toward the high side. Alternative trips of the roller shall be slightly different lengths. Tests for conformity with the smoothness will be made immediately after initial compaction, any deviations in excess of the specified tolerances shall be corrected by loosening the hot surface with rakes and removing or adding material as directed before continuing the rolling.

Generally, rolling shall be executed in such a manner as to produce a smooth surface and shall be continued until a density of at least 100% has been obtained.

During rolling, the wheels of the rollers shall be moistened to prevent adhesion of the mixture to the wheels, but an excess of water will not be permitted. The Contractor shall furnish additional and sufficient rollers if it is found that the pavement density specified is not obtained. In all spaces not accessible to the roller, the mixture shall be thoroughly compacted with hot hand tampers weighing not less than 10 kg, with a tamping face of not more than 300 cm². Skin patching of an area that has been rolled will not be permitted.

- Any mixture that becomes mixed with foreign material, or is in any way defective, shall be removed, replaced with fresh mixture and re-compacted.

- The rollers shall not be permitted to stand on pavement which has not been fully compacted.

- All Necessary matters on the pavement, either when the rollers are in operation or standing are forbidden to stay on fresh asphalt layer.

- The Contractor shall provide competent workmen who are capable of performing all work, incidental to the correction of all pavement irregularities.

The constructed asphalt layer must be executed in accordance with SRPS U.E9.021 (item 10) – Construction of hot-mix bituminous base courses.

After completion of the final rolling, the smoothness of the course will be checked, and any irregularities that exceed the tolerance or that retain water on the surface, shall be corrected by removing the defective area and replacing with new pavement. If the asphalt layer is not constructed in accordance with the conditions from SRPS U.E9.021, the deficient pavement shall be removed and replaced with satisfactory pavement with no additional payment.

All joints shall present the same texture, density and smoothness as other areas of the course. The joints between old and new lanes or sections shall be carefully made in such manner as to ensure a continuous bond between the old and new pavement. All trimmed contact surfaces of previously constructed pavement shall be painted with a thin, uniform tack coat before the fresh mixture is placed. When the edges of joints are irregular, honeycombed, or poorly compacted, all unsatisfactory sections of joint shall be trimmed to expose an even, vertical, or sharply sloping surface for the full thickness of the course. Fresh mixture shall be raked uniformly against the joint, followed by rolling; no vehicular traffic of any kind shall be permitted on the pavement for at least 24 hours.

## Kerb Laying

Precast concrete kerbs shall be produced according to the relevant standard.

The kerbs shall be laid to the relevant Standards, true to line and level and any kerb found to be more than 5 mm out of line or level at either end shall be lifted and relaid.

Where practicable, kerbs shall be laid before paving. In reinstatement, the original kerbs shall generally be re-used except where these are damaged. They shall be thoroughly cleaned before replacement and laid to suit the line and level of the undisturbed kerbs.

Kerbs laid on stabilised pavement shall be bedded on a layer of 2:1 sand-cement mortar 150 mm thick and shall be backed with concrete, cast over and around steel dowels previously driven into the green pavement material and shaped up to the required cross section.

Kerbs laid otherwise than on concrete pavement shall be bedded on a layer of 2:1 sand-cement mortar 150 mm thick and shall be backed with concrete shaped up to the required cross-section.

Specially, cast circular kerbs shall be used on curves of 13 m radius or less.

Kerbs shall be jointed with cement mortar except at expansion joints which shall be made with preformed joint filler 13 mm thick. Expansion joints shall be carried through the concrete backing and foundation.

## Construction of shoulders

Shoulders are longitudinal strips/elements along the outer edges of the pavement that are not intended for traffic but only ensure the stability of the pavement structure and serve for the installation of traffic signs and road equipment.

Shoulders should be executed in the dimensions defined in the project documentation and in compliance according to the relevant standard.

The execution of shoulders also includes the placement of all the appropriate materials for the shoulder structure in locations defined by the project documents.

The works may be executed when the air temperature exceeds 2 °C and when there is no rainfall.

The top soil material should be active in order to ensure a durable layer.

For shoulders with top soil, the basic aggregate layer should have a minimum thickness of 20 cm, while the thickness of the upper top soil layer should not exceed 10 cm.

## Footpaths

If it is not otherwise required by the Employer’s Requirements, sidewalks shall be paved either with:

- Pre-cast concrete pavers shall be produced according to the relevant standard

- Pre-cast concrete pavers of a color approved by the Engineer with a minimum thickness of 5 cm to be laid on a sub-base of 3 cm of sand over 10 cm of good quality material levelled and compacted;

- Pre-cast concrete paving flags with a color approved by the Engineer with a minimum thickness of 3 cm to be laid on a sub-base consisting of 5 cm of lean mix concrete over 10 cm of good quality material levelled and compacted;

- Natural stones to be laid on a sub-base of 5 cm of sand. Natural stones shall be sound, durable, hard, and have such properties that they will not disintegrate from the action of weather in handling and placing. The density of stones shall be not less than 2.2 t/m³ and their size range between 15 and 20 cm.

The pavement shall be laid evenly according to the lines and levels of the adjacent pavement. All tiles or stones shall be of approved type, design and make and shall be firmly bedded on the underlying course and shall be laid against each other. Upon completion of the tiling sand shall be strewed.

# TECHNICAL CONTAINERS

Container for equipment installation shall be constructed in accordance with ISO standard:

## The floor and bottom frame

Metal frame: cold-rolled, welded steel profiles, thickness of 3 mm, welded in accordance with the ISO standard. Container floor: on the lower side protected by plastic - galvanized steel sheet 0.55 mm thick. Floor: chipboard, 18 mm thick, waterproof; on top - PVC floor (i.e. linoleum) with thickness of 2 mm. Loads of the floor, min.: 1.8 kN/m2. Insulation in the floor: 100 mm mineral wool, with density of 18 - 22 kg/m3, flammability class - non-flammable, smoke density class Q1 - low smoke emission. Thermal insulation coefficient of the floor, min.: 0.39 W/m2·K.

Container floor shall be designed to accept all the loads from the equipment foreseen to be installed in it.

## Roof container frame

Metal frame: cold-rolled, welded steel profiles, thickness of 3 mm, welded in accordance with the ISO standard. All inlet-outlet connections: retracted into the upper container frame. The roof of the container: it shall be covered with a plasticized galvanized steel sheet with thickness of 0.55 mm. The ceiling of the container: a panel filled with polyurethane, 30 mm thick + mineral wool insulation 100 mm thick. In order to avoid cold areas, all corners of the container shall be insulated. Roof load capacity, min.: 1.0 kN/m2.

## Container columns

Profile: cold-rolled, welded steel profiles, with thickness of 3 mm, the dimensions of the steel columns, as well as the floor and roof frames are 150/180 mm.

Connection: four container columns shall be welded to the floor and roof container frames.

Column insulation: in order to avoid cold areas, the corners of the columns shall be insulated with mineral wool plates with a density of 18 - 22 kg/m3.

## External walls of the container

It shall be constructed from sandwich panels filled with polyurethane with thickness of 50 mm. External wall: it shall be made of profiled galvanized sheet, plasticized on the outer side and thickness of 0.50 mm.

Thickness of the coating layer shall be min. 25 microns. Internal wall: it shall be made of smooth or profiled galvanized sheet, plasticized on the outside and thickness of 0.50 mm. The thickness of the coating layer shall be min. 25 microns. The standard color shall be RAL 9002. Thermal insulation of at least 50 mm thick polyurethane-filled panels should be 0.55 W/m2·K.

## Anti-corrosive protection

All steel parts made of steel shall be degreased, coated with base color and finishing varnish.

## The door

Single-leaf metal door shall be with dimensions of 875 x 2000 mm in white color, insulated with mineral wool, made of galvanized sheet with a thickness of min. 1.5 mm. The thickness of the door itself shall be min. 40 mm. The door shall be completed with a lock, cylinder, three keys and handles for opening and closing.

## Windows on the container

Container shall be equipped with min. 2 standard PVC windows, with dimensions of 850 x 1,000 mm. The window shall be capable for full and tilt opening, with double insulating glass.

## Electrical installation:

All parts shall correspond to the relevant CEE standards. External connection shall be: CEE plug/socket UKO - UTO 5P/16A, inserted into the boxes of the upper container frame. Distribution board with fuses and feed switch. Electrical equipment per container shall be: OG single-phase sockets 6 pcs., OG light switch and LED lighting 2x16 W in 2 pieces. Cables shall be installed through channels along the panel walls.

# FENCES AND LANDSCAPING

## Submissions

Prior to commencement of any landscaping work, the Contractor shall submit to the Engineer for approval his detailed proposals for landscaping including the proposed species of grass, trees and shrubs.

## Materials

### Fences and Gates

The fence shall be made of prefabricated concrete columns and wire mesh.

The columns must meet the conditions of the standard SRPS EN 12839 - Precast concrete products - Elements for fences.

Metal wire fabric must be hot galvanized according to the relevant standard and plastic-coated with ecological powder protecting it against UV radiation.

Access to the complex shall be provided through three gates - truck entrance, administration entrance and service entrance.

The truck entrance and administration entrance shall be equipped by automatic sliding gates. Gates shall be made of steel sections, frame and filling, hot-dip galvanized and plastic coated for protection against UV radiation

The service entrance shall be provided with a classic manual two-wing gate Тhe frame shall be made of steel sections, while the filling shall be made of DUO profiles. The gate frame shall be hot-dip galvanized and plasticized for protection against UV radiation.

Each gate shall be supplied with a padlock and three keys all to the Engineer’s approval.

### Top Soil

Existing top soil stripped from the site and stored in heaps adjacent to the Works may be reused provided it has not become contaminated and is free of rubble and debris.

Where insufficient site top soil is available humus shall be imported from an approved source. Samples shall be submitted to and be approved by the Engineer before landscaping work is commenced.

### Grasses

Grassing shall be carried out using a mixture of grasses, such as Festuca rubra, Lolium perenne and Dactilis glomerata or alternative species proposed by the Contractor and approved by the Engineer.

### Trees and Shrubs

Trees and shrubs shall be of the species proposed by the Contractor in accordance with ER and approved by the Engineer and shall be of the best quality and free from disease. All must be sufficiently mature to survive transplanting from the supply nursery.

The root systems of all plants shall be maintained intact in the soil in which they have been grown and may be supplied in containers.

### Gravel

Gravel for use on the site for landscaping shall be of 28 mm nominal size

## Erection of Fences and Gates

The Contractor shall to erect the fence around the complex in accordance with the drawings and to be approved by the Engineer.

Marking and setting out the fence route shall be carried out in accordance with chapter “Setting out of the works”.

Clearing the terrain, excavations for foundations, construction of a buffer and backfilling of the foundation shall be compliant with the chapters relating to those types of works.

The fence shall be made of prefabricated concrete posts with a section of 10 cm x 10 cm, height 3.40 m, prefabricated RC crossbars with a section of 10 cm x 10 cm, wire mesh with tension wire (minimum of 3 rows) and two rows of barbed wire.

The total height of the fence above foundation (i.e. terrain) shall be 3 m.

The fence pillars shall be embedded into the reinforced concrete foundation. The foundation is to be carried out in accordance with the provisions of the chapter “Concrete and reinforcement concrete works”.

The fence wire mesh shall be installed up to a height of 2.3 from the ground and 2 rows of barbed wire on top at a distance of 30 cm. The wire mesh shall be tensioned with three rows of tension wire.

The truck entrance and administration entrance shall be equipped by automatic sliding gates. The truck entrance gate shall be 16 m wide (in two parts) and administration gate shal be 6.80 m wide. Gates shall be made of steel sections, frame and filling, hot-dip galvanized and plastic coated.

The service entrance shall be provided with a classic manual two-wing gate with a span of 6.30 m. Тhe frame shall be made of steel sections, while the filling shall be made of DUO profiles. The gate frame shall be protected by hot-dip galvanization plastic coating.

The gates shall be 2 m high.

## Landscaping

### Tree Felling

Existing trees and shrubs where directed by the Engineer or indicated on the drawings shall be cut down and all stumps and main roots shall be grubbed up. All planting thus dealt with shall be either burnt in situ or removed from the site.

### Inspection of Retained Trees

All trees and shrubs to be retained shall be inspected jointly by the Engineer and the Contractor at the commencement of the Contract and a list of trees to be retained shall be agreed. Any tree found to be diseased, dead, dying or unsafe shall be felled and uprooted subject to the prior approval of the Engineer.

### Protection of Retained Trees

Existing trees and shrubs that are to be retained shall be adequately protected by the Contractor during the course of the Contract from all operations and from goats and other animals.

Small trees and shrubs generally shall be surrounded by adequate temporary fencing to safeguard trunks and foliage.

Large trees shall have suitable screening round stems, and low branches shall be protected by temporary fencing or barriers to prevent damage from building plant and equipment.

Construction materials shall not be stored close to or within the branch spread of any tree or shrub. Existing ground levels shall be maintained.

### Maintenance of Retained Trees

Retained trees and shrubs shall be maintained during the Contract and pruned at completion having due regard to the appropriate time of year for such work to be carried out.

Maintenance shall include removing snags, dead wood and fronds, sealing cavities and irrigating as required to ensure the continued health of existing planting.

### Replacement of Damaged Trees

Should any retained tree or shrub be damaged or killed as a result of the building operations then it shall be replaced by the Contractor by an equivalent mature tree or shrub of the same variety.

### Preparation of Ground

Where so required, landscaping of the Site shall be undertaken after the Contractor has completed all other earthworks apart from replacing top soil. The areas to be landscaped shall be brought to final ground levels less the depth required for top soil or other surfacing and all surplus material shall be disposed of off-site.

All areas of the Site which are to be finished with gravel shall be excavated to a level of 150 mm below final ground level. After excavation is complete the area shall be filled to final ground level with compacted gravel.

All areas of the Site which are to be finished with sand shall be excavated to a level of 400 mm below final ground level. After excavation is complete the area shall be filled to final ground level with lightly compacted sweet sand. In this filling the Contractor shall make allowance for any consolidation and shrinkage which may subsequently occur.

The Contractor shall submit to the Engineer’s approval all material and equipment for fills and grassing the area.

### Cultivation of Ground

The Contractor shall, prior to commencing work, excavate to a depth of 250 mm below existing ground level over all areas which are to be regraded to remove top soil. This top soil shall be retained for re-use. After construction is complete relevant areas shall be filled and reinstated to a level of 250 mm below final ground level with lightly compacted approved material. In this filling the Contractor shall make allowance for any consolidation or shrinkage which may subsequently occur. The Contractor shall then relay the 250 mm thick top soil. Any deficiency in the top soil shall be made up with imported top soil. Prior to replacing topsoil areas of the Site which are to be prepared for grass, plants and roots shall be thoroughly broken up by deep raking and cross raking to a depth of 450 mm. Retained top soil may be used as fill to final ground level subject to the approval of the Engineer being first obtained. Imported top soil shall be used if the existing top soil is insufficient or unsuitable.

Where new or replacement trees or shrubs are to be planted by the Contractor in positions shown on the drawings and in agreement with the Engineer, holes 1000 mm deep below final ground level and 1000 mm square shall be excavated in each case. These shall be filled with sweet sand topped with 250 mm of top soil. Sand filling shall be thoroughly mixed with 10 kg manure before placing.

### Time for Planting

In programming the planting work the Contractor shall take due regard of the accepted seasons for planting. Should the time for completion be such that landscaping works would be carried out at a time when planting is inadvisable then the Contractor may apply to the Engineer for permission to postpone the planting until a more suitable time of year.

Should this delay mean that the planting has to be carried out after the date of completion of the Works then the Contractor shall give satisfactory undertakings to carry out the outstanding landscaping during the Defects Notification Period.

### Leaching

Immediately prior to planting and at the direction of the Engineer the Contractor shall irrigate areas for planting to leach out remaining traces of salt. Irrigation water shall be applied uniformly over the ground for 7 consecutive days at a rate of not less than 15 liters/m² per day.

### Grassing

Areas to be grassed shall be drilled 50 to 100 mm deep at 150 mm centers in each direction. Each drill shall be filled with grass or sedge rhizomes and a soil covering provided so that 40 mm only of the upper foliage remains above ground level.

The different species of grasses and sedge shall be planted in the areas indicated on the drawings. After planting the areas shall be rolled and trodden over.

### Irrigation

After planting of native tree and shrub species they shall only be irrigated twice and thereafter only as required. Non-indigenous species shall be irrigated regularly until Completion of the Works.

Grassed areas shall be irrigated immediately after planting and regularly thereafter until handover. Watering of grass shall preferably be by night time sprinkler system. If watering is carried out during the daytime the area should be flooded.

Irrigation shall be from overhead in all cases.

### Maintenance

All new plants and grasses shall be maintained for not less than 12 months after planting. This shall take the form of irrigation, retaking, pruning, weeding, tilling, etc. to ensure sufficient growth is achieved by all plants until Completion of the Works.

Once grassed areas are sufficiently established they shall be kept cut or mown to provide a uniform depth of growth. Edges of grassed areas shall be trimmed as necessary.

All new plants and grassed areas shall be protected to prevent damage from workmen, builder’s plant and equipment, goats and other animals, by the use of temporary fencing or other suitable means.

### Replacement

Any trees, shrubs or areas of grass which fail to show satisfactory growth or wither and die shall be replaced by the Contractor. The responsibility for the irrigation and maintenance of these replacement plants shall remain with the Contractor until such time as they exhibit satisfactory growth.

### Soil Testing

If so required by the Engineer the Contractor shall arrange for samples of existing and/or imported top soils and sweet sand to be tested by an independent laboratory to assess salinity levels. These tests shall be carried out prior to leaching.

# Landfill Cassette

Landfill cassette shall be constructed fully in accordance with ER and other chapters of GTS.

## Compacted soil (2 x 25 cm) (k = 1.0×10-6 – 1.0×10-8 m/s)

The work includes delivery, placement and compacting of a layer of 0.5 m, consisting of two sub-layers each 25 cm thick, with permeability coefficient of k = 1.0×10-6 – 1.0×10-8 m/s, placed over the levelled and compacted natural soil.

Compacted soil layer shall be of proper materials, placed and compacted properly. The soil should be 98% compacted according to Proctor's test.

Clay liner thickness should be at least 50.0 cm after compaction. Soil liner must be well compacted and the surface of liner must be smooth and plain so that the next layer can be easily applied.

## Geo-synthetic clay – GCL (к <≤1.0×10-11 m/s)

The watertightness of the bottom of the landfill shall be ensured by the installation of GCL on the both, base and slopes of the bottom of the landfill.

Geosynthetic bentonite films (GCL - Geosynthetic Clay Liner) shall be reinforced waterproof geosynthetic materials that consist of two layers of special geotextiles between which natural sodium bentonite in the form of extremely fine powder is permanently incorporated - encapsulated by a special needling process.

The geosynthetic bentonite liner shall meet the following technical conditions:

- The geosynthetic bentonite liner must consist of a continuous layer of natural sodium bentonite in the form of powder, evenly distributed over its entire surface, permanently encapsulated between two layers of geotextile (woven - supporting polypropylene (PP) geotextile and non-woven - covering polypropylene (PP) geotextile, which are connected to each other by the needling process uniformly on its entire surface).

- An additional layer of natural sodium bentonite in the form of powder of identical quality and composition to that found in the core of the geosynthetic bentonite film must be factory impregnated during the production process along its edges in a non-woven covering PP geotextile - in the surface of the overlap zone, 500 mm wide.

- The geosynthetic bentonite liner must have on its underside, on the woven supporting PP geotextile, a clearly marked - drawn overlap zone, in order to ensure the precision of the overlap and avoid additional unnecessary consumption of the geosynthetic bentonite liner during installation. The optimal overlap that needs to be made during installation is 30 cm.

- Overlaps - the overlapping zones of the geosynthetic bentonite liner must be specially tested in an independent and certified accredited laboratory, as proof of the waterproofness of particularly important positions in the system. Before delivery and before installation, the manufacturer must submit valid evidence in the form of the results of lap testing issued by an independent, certified and accredited laboratory to the representatives of the main Contractor, the Engineer.

- Mutual joining of unrolled rolls of geosynthetic bentonite liner is done exclusively by overlapping in the marked places, without gluing, welding or any addition of bentonite pastes, powders, tapes, glues, etc.

- The geosynthetic bentonite liner, in addition to the manufacturer having to test it in its own laboratories, must be controlled by an independent and certified and accredited laboratory in accordance with DIN 18200, for which the manufacturer/Contractor must provide valid evidence in the form of certificates issued by an independent and certified and accredited laboratories for that.

- Geosynthetic bentonite liner must have valid certificates.

- Installation of geosynthetic bentonite shall be fully in accordance with manufacturer’s detailed instructions. Prior to installation, the Contractor shell submit these detaled instruction to the Engineer.

- The dimensions of the rolls of geosynthetic bentonite liner should be as large as possible, in order to reduce as much as possible, the surfaces that are used for folding and trimming during installation.

- Each roll of geosynthetic bentonite liner must be properly marked and contain the following information:

- Length and width of the roll;

- Total weight of the roll;

- Product Type;

- Clear name of the manufacturer;

- Production lot number;

- Individual roll number.

Each roll must be packed in plastic-nylon packaging resistant to moisture. The shaft on which each roll is wound must be strong enough and resistant to physical impacts during transportation and manipulation at the construction site during installation.

When unloading, care should be taken not to damage the rolls.

The GCL layer should meet the characteristics presented in the following table.

| Performance/Characteristic | UNIT | REQUIREMENTS | TESTING METHOD |
| --- | --- | --- | --- |
| GCL |  |  |  |
| Permeability, Hydraulic conductivity | m/s | > 1.0 x 10-11 | EN 16416 |
| Flow rate | (m3/m2)/s | 3.0 x 10-9 | EN 16416 |
| Mass per unit area | kg/m² | 5.3 | EN ISO 14196 |
| Tensile strength longitude/transverse | kN/m | 12.0/12.0 | EN ISO 10319 ASTM D6768 |
| Elongation at break, MD/CMD | % | 15 | EN ISO 10319 ASTM D6768 |
| Peeling resistance | N/m | 600 | ASTM D 6496 |
| Static puncture strength, CBR | kN | 2.0 | EN ISO 12236 ASTM D6241 |
| Thickness | mm | 7.0 | EN ISO 9863-1 |
| Bentonite layer |  |  |  |
| Bentonite mass per unit area | kg/m² | 5.0 | EN ISO 14196 |
| Free swelling index | ml/2g | 25 | ASTM D5890 |
| Fluid loss, maximal | ml | ≤18 | ASTM D 5891 |
| Montmorillonite content | % | 70 | XRD VDP 69/NF X 31 130 |
| Geotextile layers |  |  |  |
| Cover layer, polypropylene nonwoven |  |  |  |
| Mass per unit area | g/m² | 200 | EN ISO 9864 |
| Carrier layer, polypropylene woven |  |  |  |
| Mass per unit area | g/m² | 110 | EN ISO 9864 |

Geocomposite clay liner shall be placed over a layer of chemically stabilized soil. The connection of GCL should be made with lap joints (30 cm). All joining, cutting and trimming details should be according to the manufacturer's installation instructions. Anchoring of the panels of geosynthetic clay liner shall be into the anchor trench, excavated around the perimeter of the landfill. When performing the works, technical conditions for this type of work shall be followed.

## HDPE membrane integrity grid of sensors

The system shall consist of a grid of sensors installed permanently under the HDPE geomembrane with a grid of minimum 5m x 5m. In case of a leakage through geomembrane, the system notifies the operator with a visual and audible alarm, as well as by sending SMS message. The mobile control device works on the principle of registering damage to the geomembrane using electric signal. The system shall be possible to register damage up to 1 mm2.

The sensors are non-metal, made from specially developed conductive polyethylene (HDPE) with specific electrical parameters what allows to monitor the distribution of the current flow below the geomembrane. It is online 24/7 system which means that the integrity of the geomembrane can be tested and measuring data can be acquired by the manufacturer and Employer/Engineer remotely. Any defects shall be detected and located in testing phase and then exposed and repaired by the Contractor.

As a minimum, system should have built-in following features:

- Local video and audio alarm,

- SMS/Email warnings,

- Warning of unauthorised system door open (with picture of the person),

- 24/7 monitoring of geomembrane,

- 10” HD display with system status,

- Data storage for 12 months,

- Battery back up in case of electrical outage (up to 2 days).

During construction phase, two main controls of integrity shall be performed; the first one after installation of the geomembrane/before installation of leachate drainage layer, and the second one after installation of leachate drainage layer.

## HDPE membrane d ≥ 2.5 mm thick

HDPE geomembrane shall be installed of base and slopes of the landfill bottom.

The high-density polyethylene (HDPE) liner shall be installed on top of the non-permeable layer in the landfill cassette.

The liner must be a minimum 2.5 mm thick HDPE liner, smooth on both sides, UV resistant.

The HDPE liner shall fulfill presented requirements and shall be tested in accordance with the standards presented in the following table:

| Performance/Characteristic | UNIT | REQUIREMENTS | TESTING METHOD |  |
| --- | --- | --- | --- | --- |
| Appearance |  | Smooth on both sides with no visible defects | Visual examination |  |
| Thickness | mm | 2.5 | EN ISO 9863-1 and EN 1849-2:2019 |  |
| Density | g/cm³ | >0.94 | EN ISO 1183-1/A |  |
| Tensile strength longitude/transverse | N/mm | ≥30 | EN ISO 527-1,3 |  |
| Elongation at break | % | 750 | ASTM D 6693-tip IV |  |
| Tear strength | N | 340 | ASTM D 1004 or corresponding applicable standard |  |
| CBR Puncture resistance | kN | ≥6 | EN ISO 12236 |  |
| Carbon black content | % | 2≤x≤3 | EN ISO 11358 |  |
| Carbon black dispersion | Category | 1 - 2 | ASTM D5596 |  |
| Dimensional Stability | % | 2 | EN ISO 1107-2 |  |
| Crack resistance | h | ≥500 | EN ISO 14576 |  |
| Resistance to oxidation | % | reduction of tensile strength <25% of original value | EN ISO 14575 |  |
| UV resistance | % | ≥50 | ASTM D 5885 |  |
| Permeability | m/s | > 1 x 10-14 | ISO 11058 |  |
| Linear coefficient of thermal expansion | Category | 1.76 x 10-4 | ASTM D 696 |  |
| Fluid leakage | m3/m2d | 1.66 x 10-6 | EN 14150 |  |
| Gas leakage | m3/m2d | 3.29 x 10-3 | ASTM D 1434 |  |
| Strength of welded seams |  |  |  |  |
| Type of welding | Assembly of the essential fabrics by double welding with central channel on all the welds+automatic single-welding or extrusion on particular points (triple points and special fittings) |  |  |  |
| Tensile Shear tests (kN/m) to welds | % | Min 90% of tensile strength at point of yield – Tensile shear tests (kN/m) for welds | ISO 527-3-1993 ISO 37:1994 ASTM D6392 |  |
| Peel traction tests (kN/m) for welds | % | Breaking of 65%(extrusion) and 70% (double welding) of the tensile strenght of the new product used. Out of seem failure | ISO 527-3-1993 ISO 37:1994 ASTM D6392 |  |

The HDPE geomembrane should be produced from the highest quality high-density polyethylene (HDPE), produced by the extrusion process of flat strips - the extrusion of the purest (''virgin'') polyethylene hexane co-monomer, which is completely free of plasticizers or other fillers. It is not allowed to use HDPE geomembranes produced by the blowing process or any other production method other than previously described.

### Control of the liner base

Before installing the geomembrane, a detailed visual inspection of the surface of the buffer layer on which the geomembrane is installed shall be performed. All objects (branches, waste, etc.) must be removed/cleaned from the surface of the buffer layer. The geomembrane shall not be spread and digest when the air temperature is lower than 5°C or higher than 35°C, when the air humidity is higher than 70% and when the wind speed is higher than 3 m/s.

Before installation, the Contractor should also carefully check compaction properties. It must be proven that the final surface has been compacted to at least 95 % Standard Proctor. Furthermore, the surface must fulfil the following requirements:

- The surface must be smooth and free of stones larger than 50 mm.

- Deviation from design levels: +/- 0.05 m.

- Maximum deviation on a 3 m long straight edge: 0.02 m.

- The installation must commence as soon as possible after control of the liner base.

### Delivery and storage of the HDPE liner

The geomembrane will be delivered in rolls of different lengths and widths of at least 5 m. It is necessary that the width dimensions of the roll be as large as possible, in order to reduce the number of formed welds, which directly leads to a reduction in the number of critical points and an increase in the degree of safety and impermeability of the entire waterproofing system.

HDPE geomembranes should be of such size and shape as to enable controlled installation with minimal folds and stress on the HDPE geomembrane itself. It must have a uniform color (black), thickness, texture, and there must not be any physical or chemical damage or irregularities on its surface. The geomembrane on the bottom of the new landfill and the slopes of the landfill is a smooth geomembrane on both sides with a thickness of ≥2.5 mm, which must be free of stains and damage and must be resistant to UV radiation, atmospheric influences, the effects of bacteria, and must be waterproof.

Any recycled materials, used geomembranes or waste from previously produced geomembranes cannot be used for the production of geomembranes.

As proof of meeting the required technical specifications, it is necessary for the manufacturer to submit an official, valid report from an independent laboratory certified and accredited for that type of testing.

A certificate of its quality must be delivered to the construction site with each roll of geomembrane.

The rolls of HDPE liner must be delivered and stored in such a way, that they are not exposed to unnecessary risk of damage, and they must be covered as protection against dirt and sunshine.

Liner material must not be stored directly on the ground. It should be placed on pallets or similar constructions.

Detailed technical requirements related to raw materials for geomembrane production, factory quality control, installation and welding procedures, quality control at the construction site, etc. shall be delivered by the manufacturer of the geomembrane, i.e. a company specialized in its installation. These detailed technical conditions must be approved by the Engineer.

### Installation of the HDPE liner

Rolled geomembranes will be installed on the slopes exclusively in the direction of the slope. The main contractor will require the geomembrane manufacturer to deliver the geomembrane in rolls of different lengths so that horizontal welds are generally avoided even on the longest slopes

Installation of HDPE liners must start from the lowest point (i.e. at the leachate collection well).

Installation of the HDPE liner must take place in accordance with the instructions of the supplier, the design and with the approval of the Engineer.

The Contractor must prepare a plan drawing for the installation of the liner. The plan shall set out all sections of liner and clearly indicate the lengths to be welded. The plan must be approved by the Engineer before commencement of the installation work.

The installation must be carried out only in dry weather conditions. On slopes the orientation of panels shall be parallel to the slope. The panels shall be secured in an anchor trench at the top of the slope.

On the liner, the name of the welder, the roll number and the welding temperature must be marked. Further, it must be marked on each liner length, whether the liner is approved and tested for the sake of installation of drainage material on the liner.

The HDPE liner shall be anchored at the top of slopes, also to prevent wind lifting the HDPE liner over time.

During installation, the liner must be kept in place by adequate loading (e.g. sand bags or similar items that will not damage the liner) to prevent uplift by wind (in case of high winds, continuous loading is recommended along edges of panels to minimise risk of wind flow under the panels).

The Contractor carries the full responsibility for the keeping in place and for storm damages. Sand bags must be removed in time with the installation of drainage material on the liner.

At his choice of working method and equipment, the Contractor must make sure that the liner is not damaged or exposed to traction. Prior to commencement the Engineer must be informed on the planned working method etc. for commenting.

### Anchoring

Anchoring of the foil (together with the geotextile) shall be in a trench with dimensions of 50 cm × 40 cm excavated along the perimeter of the embankment.

### Welding of the HDPE liner

All welding joints must be made by hot air welding equipment or contact heat welding equipment, and where this is not possible by use of automatic extrusion welding.

The liner must be clean and dry before welding is commenced.

Welding is performed with an overlap of minimum 15 cm.

The laps of adjacent rolls and the weld formation area should be marked with a clear line along the outer longitudinal edge to ensure adequate lap size and to minimize lap losses.

Joining (welding) of the geomembrane will be done by a self-propelled machine for forming a double weld with a channel between the welds. Rolls of geomembranes will overlap at a width of about 15 cm and will be welded by heating to a temperature lower than the melting point of polyethylene. In places where welding with double welding cannot be applied, single welding with filling can be applied.

Welding control will be carried out by non-destructive and destructive methods.

Non-destructive methods will be used to test all performed double welds. This test will be performed on the entire length of the weld using an apparatus for blowing air under pressure. In a period of 10 minutes, the pressure drop in the channel between the welds must not exceed 10% of the initial air pressure.

Destructive testing of welds will be performed in order to test the strength of the welds. It will be performed on samples that will be cut directly from the installed and welded geomembrane. This test will be carried out, as an orientation, every 300m of welds, that is, according to the requirements of the Engineer. The tensile strength of the weld must be equal to or greater than the tensile strength of the geomembrane.

### Installation of drainage layer

The surface of the HDPE liner at the side areas for drainage installation must be clean from soil and other items.

The geotextile shall be installed on top of the HDPE liner.

The HDPE drainage pipe shall be installed on the geotextile and connected to the installations at the leachate collection shaft at the lowest point of the disposal area. Drainage pipes shall be perforated, in accordance with DIN 4262/1. Leachate collection shafts shall be placed outside perimeter embankment and equipped with inspection lids.

Upon installation of the drainage pipes, silicate aggregate drainage material shall be installed in the 10 m wide geotextile covered areas. Other areas then covered.

Driving on the HDPE liner or the geotextile layer by means of any vehicle is strictly forbidden! Before driving on the drainage layer, elevated interim roads consisting of a minimum 0.70 m thick drainage fill layer (above the HDPE liner) must be established. After final installation of the aggregate drainage layer, surplus material used for interim roads must be removed.

Driving directly on the 0.50 m thick aggregate drainage layer is only allowed with equipment with limited contact load, i.e. tracked vehicles.

The aggregate fill layer must not be installed by bulldozing, but must be installed by a front-end loader (Bob-Cat) or similar, in order to ensure that no folds or tensions are introduced at the liner.

Blades or buckets of construction plant must not be allowed to come in to contact with the fabric during filling operations.

### Performance Report for HDPE liner works

For each working day, the Contractor must prepare a performance report for the Engineer. The report must include information on:

- Weather conditions (temperature and rainfall).

- Installation plan with specification of roll number, location, welding equipment, welding operator, welding temperature, welding speed etc.

- Tests carried out (see below).

- Special conditions (repairs, rejected welding etc.)

### Quality control on welding works

Table: Minimum of Tests required for Quality control on HDPE welding works

| Area | Item | Test Method | Extent | Acceptance Criteria |
| --- | --- | --- | --- | --- |
| Delivery control | Data sheets | Test certificates. | Per each roll |  |
|  | Welding made at factory | Tightness 2). | 1 per 100 m | Tight |
| Receiving control | Liner | Visual appearance. | 1 per 1,000 m2 | Faultless |
|  |  | Thickness. | 1 per 1,000 m2 | As specified |
|  |  | Strength parameters (Elongation at yield and Elongation at break). | 1 per 5,000 m2 | As specified |
|  | Welding made at factory | Tightness 2). | 1 per 1,000 m2 | As specified |
|  |  | Shear mode test. | 1 per 5,000 m2 | As specified |
|  |  | Peel mode test 1). | 1 per 5,000 m2 | As specified |
| Tests at commencement of works | Joints | Tightness 2), shear mode test and peel mode test 1). | 1 per each welding equipment/welding operator | Tight |
| Tests during liner installation | Liner | Visual examination. |  | Faultless |
|  | Joints | Tightness 2). | 100 % | Tight |
|  | Joints | Cut out sample with shear mode test, peel mode test 1) and tightness 2). | 1 test per 5,000 m2 | Tight joint. Seam strength maximum negative deviation: 10 % at shear mode tests and 25 % at peel mode tests. |

1) Peel mode tests are performed both for upper liner/under lap and lower liner/overlap.

2) Tightness tests are performed by vacuum test, pressure test or by spark test.

Table: Description of Control and Tests of HDPE liner works:

| Delivery Control: | The Engineer must approve the sub-contractor that performs the installation and welding of the liner. The welding operators must provide references on relevant experience from similar works. Lining Team Manager The Lining Team Manager will be an engineer or technologist with not less than 5 years’ experience in the installation of HDPE geomembrane liners. Master Welder The Master Welder will be responsible for the installation of the panels and will have installed not less than 100,000 m2 of HDPE geomembrane using the same welding equipment to be used on this Contract. The Master Welder will be present at the works area whenever welding works are in progress. Welders Welders will be experienced in the installation and seaming of HDPE and will have installed not less than 25,000 m2 of HDPE geomembrane using the same seaming equipment to be used on this Contract. The above mentioned must be documented by means of a reference list or similar. |
| --- | --- |
| Receiving Control: | A programme of testing will be carried out by a laboratory of the Contractor’s choosing, to confirm that the geomembrane supplied to the site comply with the manufacturers’ specification. The Engineer will approve the choice of laboratory, and thus details of the laboratory should be attached to the Geosynthetics Subcontractor’s bid, and if possible, be discussed at the pre-bid meeting. A 1 m wide sample will be removed from rolls chosen randomly by the Engineer or his representative for each 5,000 m2 of liner to be installed. For each liner roll delivered, a laboratory certificate from the factory must be available, in which, at a minimum, the product, type, tensile strength, elongation at break and the thickness is stated. No rolls of HDPE liner should be accepted with welds. |
| Control at Commencement of Installation: | Before commencement of the installation works, each welding operator must perform a test welding with all welding equipment foreseen to be used during the installation. The Engineer must be present at the test weldings. The weldings shall be tested on Site by the Contractor in the presence of the Engineer. A welding operator/welding equipment must not commence welding on the HDPE liner before approval from the test institute is available. |
| Control and Tests during Installation of the HDPE Liner: | At daily commencement of the welding works and at possible technical interruptions, welding tests for all welding equipment in use must be undertaken. The Contractor performs the tests on his own and the results are documented and handed over to the Engineer. On a daily basis, the surface of the installed HDPE liner is inspected in cooperation with the Engineer. The inspection may also be conducted periodically in time with the installation of drainage material on the liner. The result of the inspection is noted on a form and by clear marking on the liner, where the welding has been approved. Possible suspected areas are tested by vacuum tests and it is marked on the liner when possible failures have been repaired. The Contractor must test all weldings either by vacuum tests, by compressed air where weldings are made as double weldings or by spark tests with inserted copper wire. |
| Control Forms: | The controls performed must be noted on forms and be handed over to the Engineer continuously as part of the work report. Control forms must include all data from the tests performed in accordance with the table above. The following forms must be prepared with a statement of the data mentioned: Delivery control form: Roll number. Data sheet per each roll (certificate from the manufacturer). Tightness of possible weldings made at factory. Receiving control form: Roll number. Each roll is checked for possible transport damages. Liner control (visual appearance, thickness, yield strength/break strength). Possible weldings made at factory (tightness, shear mode strength and peel mode strength). Form for test of weldings: Test of joint prior to commencement of the installation (tightness, shear mode test and peel mode test). Test of each joint for each start-up of welding equipment. Form for control of installed liner: Visual inspection of liner surface. Test of joints (tightness). Sample taking at joint (a sample cut out is tested for shear mode strength, peel mode strength and tightness). Control form for work status: Statement of finished liner area. |

Control of the installed material (HDPE geomembrane) implies the following:

Table: Control of the installed HDPE geomembrane

| Control | Type of control | Control matter | Frequency of testng |
| --- | --- | --- | --- |
| General control | Visual control | Control of surface, liner layout, anchors etc.. | For all surface of geomembrane |
| Double seam tightness control | Air pressure in center control channel | Loss of pressure less than 10% after 3 minutes (under 2.5 bars pressure) | All seams |
| Extrusions control | Vacuum bell jar and/or drypoint | Check for leaks | All extrusions |
| Destructive test: tensile strength, peel test | Weld resistance | 65%(extrusion) and 70% (double welding) of the liner reference specimen value | 1 sample every 2000 m2 of liner |
| Destructive test: sheer strength | Weld resistance | 90% of the liner reference specimen value | 1 sample every 2000 m2 of liner |

### Monitoring of the quality of HDPE installation

Control of the integrity of the installed HDPE geomembrane shall be performed on two occasions. The first control shall be carried out immediately after the installation of the geomembrane, and before the installation of the layer of drainage gravel, while the second control shall be carried out after installing a layer of drainage gravel, when the largest number of geomembrane damages occurs. The mobile control device works on the principle of registering damage to the geomembrane using electric signal. With this system, it is possible to register damage up to 1 mm2.

## Geotextile of minimum 1,200 g/m2 and of minimum 300 g/m2

Quality assured geotextile protection layer shall be installed above HDPE liner of minimum 1,200 g/m2. The geotextiles should be of non-woven construction, manufactured from approved polymeric fibres such as polypropylene (PP) and not produced of the secondary row materials.

Requirements for the geotextile of minimum 1,200 g/m2 and testing methods given in the following table:

Table: Geotextile of minimum 1,200 g/m2

| Performance/Characteristic | UNIT | REQUIREMENTS | TESTING METHOD |
| --- | --- | --- | --- |
| Polymer |  | Polypropylene |  |
| Mass per unit area | g/m2 | 1,200 | EN ISO 9864 |
| Thickness | mm | 7.0 | EN ISO 9863-1 |
| CBR Static Puncture | N | 15,500 | EN ISO 12236 |
| Maximal Tensile strength longitude/transverse | kN/m | 81/87 | EN ISO 10319 |
| Elongation at max. tensile strength | % | ≥50 | EN ISO 10319 |
| Dynamic perforation | mm | 6 | EN ISO 13433 |
| Protection efficiency at 300kPa | % | ≤ 1.2 | EN 13719 |
| Pyramidal puncture resistance | N | ≥950 | EN 14574 |

Requirements for the geotextile of minimum 300 g/m2 which shall be be installed over geosynthetic leachate drainage liner at the slopes of landfill bottom are given in the following table:

Table: Geotextile of minimum 300 g/m2

| Performance/Characteristic | UNIT | REQUIREMENTS | TESTING METHOD |
| --- | --- | --- | --- |
| Polymer |  | Polypropylene |  |
| Mass per unit area | g/m2 | 300 | EN ISO 9864 |
| Thickness | mm | 1,5 | EN ISO 9863-1 |
| CBR Static Puncture | N | 3,500 | EN ISO 12236 |
| Maximal Tensile strength longitude/transverse | kN/m | 22/22 | EN ISO 10319 |
| Elongation at max. tensile strength | % | 60/60 | EN ISO 10319 |
| Dynamic perforation | mm | 7.5 | EN ISO 13433 |
| UV stabile | months | 12 |  |

Before installing the geotextile, the Contractor is obliged to submit to the Engineer for approval appropriate certificates confirming that the geotextile has the properties prescribed by these technical requirements.

When laying the geotextile, it shall be overlapped in a width of about 20 cm.

### Delivery and storage

Procurement, labelling, delivery and storage of geotextiles must comply with standards. Product labels must clearly show the product name, roll number, Manufacturer's name, etc. Each document supplied with the geotextile must contain a note proving that the material complies with the Manufacturer's certificate. Each geotextile roll delivered will be wrapped in a material that will protect the geotextile from shipping damage, water, sunlight and contaminants. The protective cover will be hold during transport and storage. During storage, the geotextile rolls shall be raised off the ground and adequately covered to protect them on site from: damage, precipitation, solar radiation, chemicals such as strong acids or strong bases, flames including welding sparks, high temperatures and any other conditions that may to damage the geotextile.

### Installation

The geotextile shall be placed directly on the HDPE geomembrane. All objects must be removed from the surface.

During the rolling out into position of the geotextile, sufficient allowance shall be made in order to provide an overlap at least 200 mm between adjacent sheets. Installation of geotextile, the edges shall be joined by either sewing, loistering or welding. This will prevent the material becoming displaced when the drainage layer is placed and also prevent wind lifting of the geotextile if the edges are not connected.

The geotextile shall be anchored at the top of slopes, also to prevent wind lifting of the geotextile over time.

Once the geotextile is laid it shall not be trafficked until an adequate layer of drainage material is placed over it. Blades or buckets of construction plant must not be allowed to come into contact with the geotextile during operations of drainage layer placement. The edges of the fabric shall be laid on the ground at the edges of the surface to be covered by adequate loading (e.g. sand bags or similar items that will not damage the bottom layer materials) to prevent uplift by wind (in case of high winds, continuous loading is recommended along edges of panels to minimise risk of wind flow under the panels).

During the process of drainage layer placement, no attempt shall be made to restrain the top of the fabric.

### Anchoring

The installation of geotextile of 1,200 g/m2 shall be done on berms with an overlap of approx. 100 cm on the slopes.

Joints of geotextiles should be made with an overlap of at least 20 cm, with anchoring in a trench measuring 50x40 cm or by underlaying under a layer of gravel d=100 cm.

### Control of installed material

Control of the installed material means visual control (check application surface, product conformity, liner layout, lateral overlay between each liner rolls) on 100% of the surface.

The Contractor shall supply a compliance certificate from an independent testing laboratory to the effect that the geotextile supplied complies with the specifications.

## Geosynthetic leachate drainage liner

The liner shall be installed over HDPE geomembrane. The geocomposite drainage layer should consist of a single HDPE drainage board inserted between two geotextile layers. The drainage core should be capable of accepting leachate from one side only. The side that rests on the HDPE geomembrane should be flat and impermeable. Drainage cores that are permeable on both sides are not allowed. The upper geotextile should be UV stable for exposure to the sun for a minimum of 12 months. The drainage geocomposite should have equal flow capacity in both directions.

Geosynthetic leachate drainage liner is three-layered, three-dimensional, filter stable and high compression resistance drainage system consisting of an extruded wave-shaped monofilament core and a needle-punched UV-stabilized nonwoven fully bonded at on both sides.

Requirements for the Geosynthetic leachate drainage liner which shall be installed over HDPE geomembrane at the slopes of the landfill bottom are given in the following table:

Table 8: Basic design criteria for Geosynthetic leachate drainage liner

| Performance/Characteristic | UNIT | REQUIREMENTS | TESTING METHOD |
| --- | --- | --- | --- |
| Water flow rate, in plane, at a load of 250 kPa | l/m/s | 1.16 at i=1.0 (longitude/transverse) ( | EN ISO 12958 |
| Thickness, at 2kPa | mm | 9.8 | EN 964-1 Annex B EN ISO 9863-1 |
| CBR Static Puncture | N | 7,500 | EN ISO 12236 |
| Maximal Tensile strength longitude/transverse | kN/m | 47/40 | EN ISO 10319 |
| UV stability | months | minimum 12 |  |

## Drainage gravel

The leachate drainage layer shall be placed above geotextile and it shall be made of drainage gravel, 0.5 m thick.

Gravel granulation should be 16/32mm with a maximum of 5% of grains smaller than 2.0 mm. Grains larger than 40 mm will not be embedded in the drainage layer. The layer will be formed from rolled clean (washed) gravel. The water permeability of the layer should be minimum kx≥1x10-4 m/s. Gravel shall be free of mud and clay, with organic matter content smaller than 1%. Carbonate content in the gravel must not exceed 10%. Gravel shall be spread with a bulldozer in layers with planning and rolling (accuracy ± 1 cm).

Acceptance of delivered gravel shall be based on shape, granulometry content and coefficient of permeability.

The quality of drainage gravel layer shall be tested (1 sample per 50 m3 of installed material) as well as by testing filtration coefficient.

The gravel shall be filled to a height of about 1.5 m from the bottom of the landfill, along the slope of the embankment, as far as possible to prevent the slipping of gravel, and then, a geocomposite drainage material shall be installed. Over geocomposite drainage material a 300 g/m2 geotextile shall be lined to protect the geocomposite drainage material from UV radiation.

# PIPEWORK

## General

These Specifications are to be considered for both civil and mechanical applications!

All pipework, valves and fittings shall be to a class in excess of 1.5 times the maximum pressure they will attain in service including any surge pressure, and shall be supplied by a manufacturer approved by the Employer/Engineer.

The pipework installation shall be so arranged to offer ease of dismantling and removal of pumps or other major items of equipment.

Flange adaptor or detachable couplings shall be included in the connecting pipework of all items of Works to facilitate dismantling and provision shall be made for flexible joint arrangements adjacent to all structures.

The ends of pipes for use with flange adaptors and couplings shall be faced squared and sized to the tolerances required by the manufacturer of the coupling.

All pipework shall be adequately supported in trenches or with purpose-made fixings in structures and when passing through a wall, shall incorporate a puddle flange or other suitable purpose-made sealing device.

All loose flanges shall be secured to fixed flanges by suitable tie-bolts.

Flange adaptors shall be supplied and fitted in the pipework wherever necessary to permit the simple disconnection of flanges, valves and equipment without the need to spring long runs to remove valves, equipment and the like.

Flexibility shall be provided in the pipework at joints in the main structures to allow for differential settlement and thermal stresses which shall not be transferred to the anchor blocks.  Flexible joints or collars and cut pipes shall also be allowed on all pipework where necessary to allow for some margin of error in the building work.

The pipework system shall be so designed to enable the necessary anchorage at blank ends, bends, tees and valves may be kept to a minimum. The Contractor shall indicate on his detailed drawings the blocks and supports required to anchor pipework supplied by him.

Each force and moment that may occur in the works may be compensated by an appropriate location of solid fixations, expansion joints and sliding supports. Buried pipes of stainless steel should be protected against cathodic corrosion.

Pipelines in the open-air delivering sludge or water should be insulated with mineral wool or rigid foam and accompanying heating should be provided for. Protect the insulation with weatherproof aluminum shell.

Removable pipe sections are recommendable at places where assembling and dismantling of the pipeline - due to pipe layout - is not possible in any other way.

Threaded surfaces (nuts) should receive a coat of corrosion preventing grease and closed with plastic cap, sealing strip and ring clamp. The same holds true for screw joints of stainless steel.

In case of each pipeline (in case of full-section medium delivery), following maximum velocities of flow should be considered:

| Streaming medium | Type of pipeline | Flow velocity (m/s) |
| --- | --- | --- |
| Cold water | Suction pipe Delivery pipe | - - 1.0 - - 2.5 |
| Mix of sand-water | Suction pipe and Delivery pipe | 2 - 5.0 |
| Compressed air | Control air pipe and Delivery pipe | 10 - 15 |
| Hot air | Suction pipe Delivery pipe | 0.8 - 1.0 0.8 - 10 |

## Standards

The applicable standards are listed below, but they are not limited to the following:

General standards

| - SRPS EN 805 | Water supply - Requirements for systems and components outside buildings |
| --- | --- |
| - SRPS EN 806 | Specifications for installations inside buildings conveying water for human consumption |
| - SRPS EN 1610 | Construction and testing of drains and sewers |
| - ATV-DVWK-A 127 | Rules and standards for the static calculation of sewage pipes and pipelines. |
| - SRPS EN 253 | District heating pipes – Bonded single pipe systems for directly buried hot water networks – Factory made pipe assembly of steel service pipe, polyurethane thermal insulation and a casing of polyethylene |
| - SRPS EN 476 | General requirements for components used in drains and sewers |

Steel Names and QC standards

- SRPS EN 10027		Steel names and numbers

- SRPS EN 10204 		Metallic products - Types of inspection documents

- SRPS EN 10088-1 	Stainless steels - Part 1: List of stainless steels

- SRPS EN 10088-2 to 5 	Stainless steels: Technical delivery conditions

Covers, Step Irons, Ladders

- SRPS EN 124		Gully tops and manhole tops for vehicular and pedestrian areas - Design requirements, type testing, marking, quality control

- DIN 1229 		Gully tops and manhole tops for vehicular and pedestrian areas - Mass per unit area and pull-out force

- DIN 1211 		Step irons for staggered manhole steps

- DIN 1212 		Step irons with upstand for staggered manhole steps

- SRPS EN 13101		Steps for underground man entry chambers - Requirements, marking, testing and evaluation of conformity

- DIN V 1264	 	Steps for underground man entry chambers - Application in construction works for wastewater disposal

- DIN 19555 		Step irons for straight manhole steps in in-situ concrete manholes

- SRPS EN 14396		Fixed ladders for manholes

- DIN 3580		Surface boxes and ground plates; requirements and testing; DVGW code of practice

Steel Pipes

| - SRPS EN 10216 | Seamless steel tubes for pressure purposes - Technical delivery conditions |
| --- | --- |
| - SRPS EN 10224 | Non-alloy steel tubes and fittings for the conveyance of aqueous liquids including water for human consumption - Technical delivery conditions |
| - SRPS EN 10296 | Welded circular steel tubes for mechanical and general engineering purposes - Technical delivery conditions |
| - SRPS EN 10297 | Seamless circular steel tubes for mechanical and general engineering purposes - Technical delivery conditions. |
| - SRPS EN 10255 | Non-Alloy steel tubes suitable for welding and threading - Technical delivery conditions |
| - SRPS EN 10220 | Seamless and welded steel tubes - Dimensions and masses per unit length |
| - DIN 2460 | Steel pipes for water pipelines with cement lining ex factory |
| - SRPS EN 10217 | Welded steel tubes for pressure purposes - Technical delivery conditions |
| - SRPS EN 10226 | Pipe threads where pressure tight joints are made on the threads |
| - SRPS EN ISO 3183 | Petroleum and natural gas industries - Steel pipe for pipeline transportation systems |
| - SRPS EN 10311 | Joints for the connection of steel tubes and fittings for the conveyance of water and other aqueous liquids |

Fittings

- SRPS EN 10241	 	Steel threaded pipe fittings

- SRPS EN 10253		Butt-welding pipe fittings

Material Tests

- SRPS EN ISO 6892 	Metallic materials - Tensile testing

- SRPS EN ISO 6506 	Metallic materials - Brignell hardness test

- SRPS EN ISO 6508 	Metallic materials - Rockwell hardness test

- SRPS EN ISO 8491 	Metallic materials - Tube (in full section) - Bend test

Corrosion Protection

| - SRPS EN ISO 12944-1 | ‘til Part 8 Paints and varnishes - Corrosion protection of steel structures by protective paint systems |
| --- | --- |
| - SRPS EN ISO 14916 | Thermal spraying - Determination of tensile adhesive strength (ISO 14916:2017) |
| - SRPS EN ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles - Specifications and test methods (ISO 1461:2009) |
| - SRPS EN ISO 2063 | Thermal spraying - Metallic and other inorganic coatings - Zinc, aluminum and their alloys |
| - SRPS EN 10240 | Internal and/or external protective coatings for steel tubes - Specification for hot dip galvanized coatings applied in automatic plants |
| - SRPS EN 13144 | Metallic and other inorganic coatings - Method for quantitative measurement of adhesion by tensile test |
| - SRPS EN 10298 | Steel tubes and fittings for on shore and offshore pipelines - Internal lining with cement mortar |
| - SRPS EN 545 | Ductile iron pipes, fittings, accessories and their joints for water pipelines - Requirements and test methods |
| - DIN 2880 | Cement mortar inside lining for ductile cast iron and steel pipes and fittings, application |
| - DIN 30670 | Polyethylen coatings of steel pipes and fittings - Requirements and testings |
| - DIN 30675 | External corrosion protection of buried pipes; corrosion protection systems for steel pipes |
| - SRPS EN 10288 | Steel tubes and fittings for onshore and offshore pipelines - External two layer extruded polyethylene based coatings |
| - SRPS EN 10289 | Steel tubes and fittings for onshore and offshore pipelines - External liquid applied epoxy and epoxy-modified coatings |
| - SRPS EN 10290 | Steel tubes and fittings for onshore and offshore pipelines - External liquid applied polyurethane and polyurethane-modified coatings |
| - SRPS EN 10300 | Steel tubes and fittings for onshore and offshore pipelines - Bituminous hot applied materials for external coating |
| - SRPS EN 10310 | Steel tubes and fittings for onshore and offshore pipelines - Internal and external polyamide powder based coatings |
| - SRPS EN ISO 21809-3 | Petroleum and natural gas industries – External coatings for buried or submerged pipelines used in pipeline transportation systems – Part 3: Field joint coatings (ISO 21809-3:2016) |

Welding General

| - DIN 1910 | Welding and allied processes - Vocabulary - Part 100: Metal welding processes with additions to DIN EN 14610 |
| --- | --- |
| - SRPS EN ISO 9606-1 | Qualification test of welders - Fusion welding – Part 1: Steels |
| - API 1104 | Welding of Pipelines and Related Facilities |
| - SRPS EN ISO 15607 | Specification and qualification of welding procedures for metallic materials - General rules |
| - SRPS EN ISO 14731 | Welding coordination - Tasks and responsibilities |
| - SRPS EN ISO 3834 | Quality requirements for fusion welding of metallic materials |
| - SRPS EN 1011-1 | Welding - Recommendations for welding of metallic materials - Part 1: General guidance for arc welding |
| - SRPS EN ISO 4063 | Welding and allied processes - Nomenclature of processes and reference numbers |
| - SRPS EN ISO 5817 | Welding - Fusion-welded joints in steel, nickel, titanium and their alloys (beam welding excluded) - Quality levels for imperfections |
| - SRPS EN ISO 9692 | Welding and allied processes - Recommendations for joint preparation |

Welding Consumables

| - SRPS EN ISO 14341 | Welding consumables - Wire electrodes and weld deposits for gas shielded metal arc welding of non-alloy and fine grain steels - Classification |
| --- | --- |
| - SRPS EN ISO 14171 | Welding consumables |
| - SRPS EN ISO 18275 | Welding consumables - Covered electrodes for manual metal arc welding of high-strength steels |
| - SRPS EN ISO 2560 | Welding consumables - Covered electrodes for manual metal arc welding of non-alloy and fine grain steels - Classification |
| - SRPS EN ISO 17632 | Welding consumables - Tubular cored electrodes for gas shielded and non-gas shielded metal arc welding of non-alloy and fine grain steels - Classification |
| - SRPS EN ISO 544 | Welding consumables - Technical delivery conditions for filler materials and fluxes - Type of product, dimensions, tolerances and markings |
| - SRPS EN ISO 14174 | Welding consumables - Fluxes for submerged arc welding and electroslag welding |
| - SRPS EN ISO 636 | Welding consumables - Rods, wires and deposits for tungsten inert gas welding of non-alloy and fine-grain steels |
| - SRPS EN 12074 | Welding consumables - Quality requirements for manufacture, supply and distribution of consumables for welding and allied processes |
| - SRPS EN ISO 20378 | Welding consumables - Rods for gas welding of non-alloy and creep resisting steels – Classification |

Welding Tests

| - SRPS EN ISO 4136 | Destructive tests on welds in metallic materials - Transverse tensile test |
| --- | --- |
| - SRPS EN ISO 5173 | Destructive tests on welds in metallic materials - Bend tests |
| - SRPS EN ISO 17637 | Non-destructive testing of welds - Visual testing of fusion-welded joints |
| - SRPS EN ISO 23277 | Non-destructive testing of welds - Penetrant testing of welds - Acceptance levels |
| - SRPS EN ISO 3452 | Non-destructive testing - Penetrant testing |
| - SRPS EN ISO 17638 | Non-destructive testing of welds - Magnetic particle testing |
| - SRPS EN ISO 23278 | Non-destructive testing of welds - Magnetic particle testing of welds - Acceptance level |
| - DIN EN ISO 17636 | Non-destructive testing of welds - Radiographic testing |
| - SRPS EN ISO 17636 | Non-destructive testing of welds - Radiographic testing |
| - SRPS EN ISO 17643 | Non-destructive testing of welds - Eddy current examination of welds by complex plane analysis |
| - SRPS EN ISO 11666 | Non-destructive testing of welds – Ultrasonic testing - Acceptance levels |
| - SRPS EN ISO 23279 | Non-destructive testing of welds - Ultrasonic testing - Characterization of discontinuities in welds |
| - SRPS EN ISO 17640 | Non-destructive testing of welds - Ultrasonic testing - Techniques, testing levels, and assessment |
| - SRPS EN ISO 10893 | Non-destructive testing of steel tubes |
| - SRPS EN ISO 17635 | Non-destructive testing of welds - General rules for metallic materials |
| - DIN EN ISO 10675 | Non-destructive testing of welds - Acceptance levels for radiographic testing |

Stainless Steel Pipes

| - SRPS EN ISO 1127 | Stainless steel tubes - Dimensions, tolerances and conventional masses per unit length |
| --- | --- |
| - SRPS EN ISO 14175 | Welding consumables - Gases and gas mixtures for fusion welding and allied processes |
| - SRPS EN ISO 3506 | Mechanical properties of corrosion-resistant stainless steel fasteners |
| - SRPS EN 10027 | Designation systems for steels |
| - SRPS EN 10305 | Steel tubes for precision applications - Technical delivery conditions |
| - EN ISO 14343 | Welding consumables - Wire electrodes, strip electrodes, wires and rods for arc welding of stainless and heat resisting steels – Classification |
| - SRPS EN 10312 | Welded stainless steel tubes for the conveyance of aqueous liquids including water for human consumption - Technical delivery conditions |
| - SRPS EN 10297 | Seamless circular steel tubes for mechanical and general engineering purposes - Technical delivery conditions |

Ductile Iron Pipes

| - SRPS EN 545 | Ductile iron pipes, fittings, accessories and their joints for water pipelines - Requirements and test methods |
| --- | --- |
| - SRPS EN 598+A1 | Ductile iron pipes, fittings, accessories and their joints for sewerage applications - Requirements and test methods |
| - SRPS EN 969 | Ductile iron pipes, fittings, accessories and their joints for gas pipelines - Requirements and test methods |
| - DIN 2880 | Cement mortar inside lining for ductile cast iron and steel pipes and fittings, application |
| - ISO 8179 | Ductile iron pipes - External zinc-based coating |
| - ISO 4179 | Ductile iron pipes and fittings for pressure and non-pressure pipelines -- Cement mortar lining |

Plastic Pipes

| - SRPS EN ISO 12162 | Thermoplastics materials for pipes and fittings for pressure applications - Classification, designation and design coefficient |
| --- | --- |
| - SRPS EN ISO 9969 | Thermoplastics pipes - Determination of ring stiffness |
| - ISO 161 | Thermoplastics pipes for the conveyance of fluids |
| - SRPS EN 13476-1 | Plastics piping systems for non-pressure underground drainage and sewerage - Structured-wall piping systems of unplasticized poly(vinyl chloride) (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 1: General requirements and performance characteristics |
| - SRPS EN 13476-2 | Plastics piping systems for non-pressure underground drainage and sewerage - Structured-wall piping systems of unplasticized poly(vinyl chloride) (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 2: Specifications for pipes and fittings with smooth internal and external surface and the system, Type A |
| - SRPS EN 13476-3 | Plastics piping systems for non-pressure underground drainage and sewerage - Structured-wall piping systems of unplasticized poly(vinyl chloride) (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 3: Specifications for pipes and fittings with smooth internal and profiled external surface and the system, Type B |
| - SRPS EN 13598-1 | Plastics piping systems for non-pressure underground drainage and sewerage - Unplasticized poly(vinyl chloride) (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 1: Specifications for ancillary fittings including shallow chambers |
| - SRPS EN 13598-2 | Plastics piping systems for non-pressure underground drainage and sewerage - Unplasticized poly(vinyl chloride) (PVC-U), polypropylene (PP) and polyethylene (PE) - Part 2: Specifications for manholes and inspection chambers |
| - DIN 4262-1 | Pipes and fittings for subsoil drainage of trafficked areas and underground engineering - Part 1: Pipes, fittings and their joints made from PVC-U, PP and PE |

uPVC Pipes

| - DIN 1187 | Unplasticized polyvinyl chloride (PVC-U) drainpipes; Dimensions, requirements, testing |
| --- | --- |
| - EN ISO 1452 | Plastics piping systems for water supply and for buried and above-ground drainage and sewerage under pressure - Unplasticized poly(vinyl chloride) (PVC-U) |
| - SRPS EN 1401-1 | Plastics piping systems for non-pressure underground drainage and sewerage - Unplasticized polyvinyl chloride (PVC-U) - Part 1: Specifications for pipes, fittings and the system |
| - ISO 1452-3 | Plastics piping systems for water supply and for buried and above-ground drainage and sewerage under pressure - Unplasticized polyvinyl chloride (PVC-U) – Part 3: Fittings |
| - SRPS EN 1451-1 | Plastics piping systems for soil and waste discharge (low and high temperature) within the building structure - Polypropylene (PP) - Part 1: Specifications for pipes, fittings and the system |

HDPE Pipes

| - DIN 8074 | Polyethylene (PE) - Pipes PE 80, PE 100 – Dimensions |
| --- | --- |
| - DIN 8075 | Polyethylene (PE) pipes - PE 80, PE 100 - General quality requirements, testing |
| - SRPS EN 1519 | Plastics piping systems for soil and waste discharge (low and high temperature) within the building structure - Polyethylene (PE) |
| - SRPS EN 1555 | Plastics piping systems for the supply of gaseous fuels - Polyethylene (PE) |
| - SRPS EN 12201 | Plastics piping systems for water supply, and for drainage and sewerage under pressure - Polyethylene (PE) |
| - SRPS CEN ISO/TS 15875 | Plastics piping systems for hot and cold water installations - Crosslinked polyethylene (PE-X) |
| - SRPS EN 12666 | Plastics piping systems for non-pressure underground drainage and sewerage - Polyethylene (PE) |

GRP Pipes

- SRPS EN ISO 23856 Plastics piping systems for pressure and non-pressure water supply, drainage or sewerage - Glass-reinforced thermosetting plastics (GRP) system based on unsaturated polyester (UP) resin

- DIN 16868 	Glass fiber reinforced unsaturated polyester resin (UP-GF) pipes

- SRPS CEN/TS 14578 Plastics piping systems for water supply or drainage and sewerage - Glass-reinforced thermosetting plastics (GRP) based on unsaturated polyester resin (UP) - Recommended practice for installation

Flanges

| - SRPS EN 1092-1 | Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 1: Steel flanges |
| --- | --- |
| - SRPS EN 1092-2 | Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 2: Cast iron flanges |
| - SRPS EN 1092-3 | Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 3: Copper alloy flanges |
| - SRPS EN 1092-4 | Flanges and their joints - Circular flanges for pipes, valves, fittings and accessories, PN designated - Part 4: Aluminum alloy flanges |
| - SRPS EN 1514 | Flanges and their joints - Dimensions of gaskets for PN-designated flanges |
| - SRPS EN 1591 | Flanges and their joints - Design rules for gasketed circular flange connections |
| - EN 681 | Elastomeric seals - Materials requirements for pipe joint seals used in water and drainage applications |

Valves

- SRPS EN 558+A1	Industrial valves - Face-to-face and center-to-face dimensions of metal valves for use in flanged pipe systems - PN and Class designated valves

- SRPS EN 1984	Industrial valves - Steel gate valves

- SRPS EN 1171 	Industrial valves - Cast iron gate valves

- SRPS EN 593+A1 	Industrial valves - Metallic butterfly valves

- SRPS EN 19 	Industrial valves - Marking of metallic valves

Concrete Pipes

- SRPS EN 1916 	Concrete pipes and fittings, unreinforced, steel fibre and reinforced

- SRPS EN 1916:2007/AC:2011 	Concrete pipes and fittings, unreinforced, steel fibre and reinforced

Cathodic protection

| - SRPS EN 12068 | Cathodic protection - External organic coatings for the corrosion protection of buried or immersed steel pipelines used in conjunction with cathodic protection - Tapes and shrinkable materials |
| --- | --- |
| - SRPS EN ISO 12696 | Cathodic protection of steel in concrete |
| - SRPS EN 12954 | General principles of cathodic protection of buried or immersed onshore metallic structures |
| - SRPS EN 13509 | Cathodic protection measurement techniques |
| - SRPS EN 13636 | Cathodic protection of buried metallic tanks and related piping |
| - SRPS EN ISO 18086 | Corrosion of metals and alloys – Determination of AC corrosion – Protection criteria |
| - SRPS EN 50162 | Protection against corrosion by stray current from direct current systems |

## Quality Certificates

Before starting with construction, certificates and documents as follows should be submitted to the Engineer:

- Pipe layout drawings and isometric and/or longitudinal drawings with item list;

- Wall thickness calculations, of course, with static calculations of supports and fixing;

- Welding drawing;

- Descriptions on material listing basic and auxiliary materials;

- Certificates of welders;

- Technological examination, if necessary;

- Staff requirement naming the manager, indicating among others the name and qualification of person supervising welding; - Manufacturer’s certificate;

- Certificate attesting the durability (sustained loading) of the given material (for materials in contact with the medium such as pipelines, pipe shapes, sealing, fittings, etc.) in case of given medium, given temperature and given operational pressure; - Instructions for gluing.

Quality certificates are required for all for materials used.

On the assembly drawings pipelines of ≤ ND 80 should be indicated by one single line, those of >ND 80 by triple line. Any deviation from the foregoing should be fixed in the Contract.

Only welders having appropriate certificate should be engaged. Before starting to work, a copy of the welder’s certificate should be submitted to the Engineer without notice. Welder repeatedly failing in producing the agreed quality of welded joint should be replaced if so required by the Employer/Engineer.

In bad weather, additional measures are requested in the course of welding consequently, in case of rainy weather, provision shall be made to keep the places of welding dry. In weather with temperatures below 5 °C, a strip of 100 mm should be preheated to 50 °C, on both sides of the welded joint in case of both seams and tack welds.

Splash, burning-in, uneven arc, oversized root edges at corner joints, unsatisfactory seam or any crack are impermissible in the course of welding. Surfaces should be free from any marks of impact, indentation and deformation.

## Wall Passing

Where pipes pass through a concrete wall or structure they shall project from the external face(s) of the structure by 300 mm for pipes with nominal bores of 500 mm or less and 500 mm for pipes with nominal bores larger then 500 mm and the surface of such pipes shall be prepared to the approval of the Engineer to ensure a satisfactory bond between pipes and concrete.

Wall sleeves for water retaining structures shall be completed watertight. Puddle flanges, wall pieces with flange and/or standard wall sleeves form internationally accepted manufactures would be approved, only.

## Support of Pipework and Valves

All necessary supports including structural steelworks foundations, hangers, saddles, sliding shoes, slings, expansion pieces, fixing bolts, foundation bolts, fixing and anchor points and all attachments shall be supplied to support the pipework and its associated equipment in an approved manner.

Valves, flow meters, strainers and other devices mounted in the pipework shall be supported independently of the pipe to which they connect.

## Adapters

Adapters shall be provided to all valves in order to ensure a simple dismantling. They shall be lockable in position.

Adapters shall be flanged according to relevant standards.

The flexible/flange adapters used for jointing the plain ended pipe and bends shall be gasket, sleeve type with diameter to properly fit onto a pipe/flange forming permanently tight joints under all reasonable conditions of expansion, contraction, shifting and settlement in buried or above ground condition.

Flexible couplings shall connect pipes without flanges of the same or different materials.

Flange adapters shall be used for connection of pipes, one with flange and one without flange of the same or different materials.

## Rubber Compensators

Rubber compensators shall be provided to all pipework at the access to machines. Rubber compensators shall be capable of balancing thermal expansions, discrepancies of assembling, vibrations of machinery and settlements.

| Direction | Diameter | Excursion/value |
| --- | --- | --- |
| Axial | up to ND 50 mm |  + 10 mm |
|  | from ND 65 mm |  + 20 mm |
| Lateral | Displacement |  ± 15 mm |
| Angular |  |  7.5 ° |
| Compression |  |  30 mm |

Rubber compensators shall be flanged according to relevant standards. Screws shall not protrude in the direction of the rubber. Rubber parts shall not be painted.

## Ductile Iron Pipes, Laying and Testing

### General

Iron pipes and fittings shall be ductile iron and comply with the relevant Standards. Non-standard specials shall be avoided. Unless otherwise specified, puddle flange thickness and diameter shall be similar to the flange of the corresponding diameter.

Spigot and socket joints shall be flexible and of an approved “push-in” or bolted gland type unless otherwise specified.

Flexible couplings shall be of a type approved by the Engineer.

#### Norms and Standards

Pipes and fittings in ductile iron for use with sewerage and wastewater shall conform to the relevant standard and shall withstand successfully any test described therein.

#### Quality of Pipes, Fittings and Accessories

Pipes, fittings and accessories must not have any defects likely to be detrimental to their use.

Pipes, fittings and accessories showing small imperfections inseparable from the method of manufacture and in no way affecting their use, shall not be rejected. The Manufacturer may, on his own responsibility, remedy such slight surface imperfections in a suitable manner.

#### Socket and Spigot Pipes and Fittings

All buried pipes shall, unless otherwise specified, required or indicated, be of the socket and spigot type with the manufacturer’s standard rubber gasket.

#### Flanged Pipes and Fittings

All flanges shall conform to relevant standards. Flanges shall be drilled to PN16 unless otherwise specified or required.

Flanged joints shall be made, unless specified otherwise, with full face rubber joint gaskets and cadmium plated or galvanised steel bolts and nuts which shall include two washers per bolt. Joint gaskets shall be made from 3mm thick rubber and of such physical properties as to be capable of forming permanent watertight joints in accordance with relevant standards. The use jointing paste or grease will not be permitted. No jointing material shall be left protruding into the bore of the pipework.

#### Coatings and Linings

All pipes and fittings shall be supplied with factory-applied coatings and linings.

Coatings shall be in accordance with relevant standards. Cement mortar linings shall comply with relevant standard.

Pipes shall be externally coated with zinc spray and bituminous coating.

Pipes shall be internally lined with high alumina cement mortar. Socket areas that come into contact with sewage or wastewater shall receive a reinforced coating of epoxy paint.

Fittings shall be coated and lined with epoxy paint to 150 microns DFT (minimum).

All non-buried flanged pipes and fittings (in pumping stations, etc.) shall be with internal coatings as specified above. The external coating shall be the factory coating specified, excluding the bituminous coating, supplemented by a number of paint coats as specified in the General Mechanical and Electrical Specification, with a finishing coat of a color to be specified by the Engineer.

#### Transport and Storage

During transport, pipes shall be solidly supported not only under the lower layer and between the layers, but also laterally and at the ends and the top in wooden crates to prevent accidental damage.

Storage of pipes, fittings and jointing materials on site shall be strictly in accordance with the manufacturer’s instructions or recommendations.

Storage of pipes on site shall be on a raised floor with support frames so that the sockets do not touch the ground. Storage can be either head to tail storage or all pipes pointing in the same direction.

### Laying and Jointing

#### Re-rounding and Cutting of Pipes

Pipes that have been roughly handled can have an ovalisation at the spigot end that prevents a correct assembly of the pipeline. Such ovalisation may be corrected with special tensioning equipment to the approval of the Engineer.

Pipes shall be cut at right angles to the pipe axis. It is recommended to use wheel cutters for cutting the pipes. Care shall be taken to remove all burrs and to remake the chamfer to facilitate the fixing of the automatic joint and to avoid damaging the joint ring. The chamfer, made with a file for ND 300 and less or with a wheel cutter for the larger than ND 300, must be in strict accordance with the original chamfer made in the factory.

#### Excavation of Trenches

Trenches shall be excavated to the width and the depth and to the lines shown on the drawings and shall be carried out in accordance with Paragraph “Earthworks”.

#### Bedding of Pipes

The bedding to the pipes and fittings shall be carried out in accordance with Paragraph ”Earthworks”.

#### Laying and Jointing of Pipes

Before lowering the pipes into the trench, the Contractor shall carefully inspect and clean the pipe to ensure that it has been freed for all foreign matter.

The alignment of the pipe in the trench shall be controlled by level instrument or boning rods to ensure correct levels.

The Contractor shall keep the interior of pipes clean and free from water, dirt, stones and other foreign matter as laying proceeds, and at the end of the day's work or at other times when installation work is not proceeding, the open ends of the pipes shall be sealed off by a suitable stopper. The Contractor shall take such precautions as are necessary to prevent pipes from floating.

The pipes shall be laid in straight lines both in horizontal and vertical planes. Changes of direction of less than 11¼° shall be obtained by deviating the pipes after jointing at one or more joints. The angle of deviation at each joint depends on the ND and has the following maximum values:

ND 	 	Maximum deviation

- 100 to 300 	3.5°

- 350 to 600 	2.5°

- 700 to 2000 	1.5°

No deviation can be made at a locked joint.

The jointing of spigot and socket, and flanged pipes and fittings shall be carried out strictly in accordance with the manufacturer’s instructions or recommendations.

#### Thrust and Anchor Blocks

Thrust blocks, or other approved means of restraint, shall be provided at bends (both horizontal and vertical), branches and blank ends on flexibly jointed pressure pipelines.

Thrust blocks shall be of reinforced Concrete Class C25/30 or mass Concrete Class C16/20. Thrust blocks shall extend from the fitting to solid undisturbed earth, shall be suitably reinforced and shall be installed so that all joints are accessible for repair. The concrete backfill to the excavation shall be placed the same day as any additional excavation for the thrust block is carried out. No pressure shall be applied to thrust blocks until the concrete has matured as specified in the Paragraph “Loading of concrete Structures”.

In large radius curves obtained by deviations at the pipe joints, the thrusts are absorbed by the backfill. Anchor blocks shall be provided on steeply sloping pipelines, where the slope exceeds 25 % for a buried pipeline or 20 % for a pipeline laid in a shaft.

The pipeline shall be secured by stirrups fixed into the concrete block and placed immediately behind the sockets (the sockets normally pointing uphill).

The concrete shall be reinforced Concrete Class C25/30. The concrete shall not be subjected to any load until the concrete has matured as specified Paragraph “Loading of concrete Structures”.

#### Locking Joints

Locking joints or restrained flexible joints may be used, as an alternative to thrust blocks for:

- Areas where the underground space is crowded, large urban zones, industrial installations, etc.;

- Low strength grounds where massive concrete thrust blocks would otherwise be necessary;

- Under crossings of services, rivers, streams etc.;

- Shafts.

Locking joints shall be provided for sufficient lengths along either side of the joint requiring restraint, in order to generate sufficient frictional force from the pipeline to resist the thrust.

#### Surround to Pipes

##### Selected Fill Surround

The filling to the pipeline shall be carried out in accordance with Paragraph “Earthworks”.

##### Concrete Bed and Surround

Where concrete protection to pipelines is to be provided, the Engineer may direct that a blinding layer of Concrete Class C16/20 be laid over the full width of the bottom of the trench so as to satisfy the following requirements:

| Details of Concrete Blinding | Pipe Nominal Bore (mm) |  |  |
| --- | --- | --- | --- |
|  | 600 and less | 700 to 900 | 1000 to 2000 |
| Min. thickness of blinding | 75 | 75 | 75 |
| Min. extent of blinding each side of pipe barrel | 150 | 150 | 230 |
| Min. clearance between blinding and pipe barrel | 150 | 150 | 230 |
| Min. clearance between blinding and pipe barrel | 150 | 150 | 230 |
| Min. clearance between blinding and underside of pipe socket | 25 | 25 | 25 |

Any concrete blinding shall be allowed to set and be thoroughly washed down before pipe laying commences.

The length of pipelines laid in any one operation before concreting the pipeline shall be as directed by the Engineer so as to permit accurate laying of the pipeline and proper compaction of the fill.

Pipes up to and including 1200 mm nominal bore shall be firmly supported on precast concrete blocks and separated from them by a 25 mm thick saturated softwood packing.

After the pipeline has been tested by the Contractor and approved by the Engineer the concrete shall be thoroughly washed down and Concrete Class C20/25 shall be carefully placed and compacted thereon to avoid disturbing the pipes or joints until the appropriate profile for the type of protection required has been reached.

Concrete protection to the pipelines shall be either bed or surround of Concrete Class C20/25 along such lengths as ordered by the Engineer in writing.

The concrete protection shall be placed to the full width of the trench and never less than 150 mm wider on each side than the barrel of the pipe. When support of excavation is provided building paper shall be placed against that support before concreting to facilitate withdrawal of the support.

In the case of spigot and socket pipes with flexible joints the concrete protection at each joint shall be interrupted in a vertical plane at the edge of the socket by a strip of fibreboard or other material approved by the Engineer and of the following thickness:

| Pipe Nominal Bore (mm) | Fibreboard Thickness (mm) |
| --- | --- |
| 300 and less | 12 |
| 350 to 600 | 24 |
| 700 to 1200 | 36 |
| 1400 to 2000 | 48 |

Where two or more pipelines are laid in the same trench, the joints shall coincide at the points where the continuity of the concrete surround is broken at the joints in the pipeline with the longest pipes, and any intermediate joints in the other pipeline with shorter pipes shall be surrounded in concrete.

##### Pipe Supports

The Contractor shall take due care to support adequately the pipework during installation until permanent supports and anchorages as approved by the Engineer have been completed. The Contractor shall ensure that no excessive loads or stresses are imposed upon the fittings, pipework or structure during installation. Pipework systems shall be complete and checked for correct position and alignment before and after being embedded in concrete, where applicable.

##### Backfilling

The remainder of the trench above the pipe surround shall be backfilled with approved selected backfill material in accordance with the Specification.

### Accessories

#### Mechanical Couplings

Approved couplings or flange adaptors shall be used to joint respectively two plain ended pipes or a flanged fitting/valve to a plain ended pipe. They shall be installed and jointed strictly in accordance with the manufacturer’s instructions and protected as specified for bolted joints.

#### Dismantling Joints

Dismantling joints or adjustable and removable joints of an approved manufacture shall be installed at all valves exceeding 100 mm diameter to permit the removal of the valve.

#### Flanged Anchoring Sleeves

Flanged anchoring sleeves, complying with relevant standard, shall be used whenever a ductile iron pipe passes through a concrete wall or structure.

#### Surface Boxes

Surface boxes for buried valves, hydrants etc. shall be manufactured from cast iron, coated with a tarbased coating.

### Corrosion Protection

#### Sleeving of Pipelines

Polyethylene sleeving shall be installed to all buried spigot and socket pipelines. The sleeving shall be installed in accordance with the manufacturer’s instructions. The method of application shall include the independent protection of joints with protective wrapping tape and continuous sleeving over the joints.

#### Protection of Bolted Joints

Bolted joints at all buried flanged fittings, accessories and valves shall be protected by tape wrapping. A continuous coating of bitumen primer shall be applied over the whole area to be protected. Where bolt heads, nuts, flanges and other projections arise, a profiling mastic shall be used to give a smooth external profile. The joint or fitting shall be wrapped with a self-adhesive, cold applied, rubber bitumen tape with a PVC backing. The minimum application shall be a spiral wrap using 55% overlap. The tape shall extend along 150mm of the barrel of the pipe on each side of the joint or fitting.

### Testing of Pipelines

#### Testing of Pressure Pipelines

Pressure pipelines (together with all specials and valves incorporated) shall be tested with water in accordance with relevant standard. The trench must be filled on the pipe barrels, leaving the joints uncovered so as to prevent the pipeline from moving whilst leaving the joints accessible. Thrust blocks must also be constructed before testing. In heavily trafficked roads the backfilling at joints may take place before testing if the Engineer so allows in writing. At least two days’ notice must be given in writing to the Engineer before pressure testing of any section is commenced.

The test pressures, unless otherwise specified or ordered by the Engineer, shall be:

1.5 × the maximum working pressure or the maximum surge pressure, if applicable, whichever is the greater.

Pipes shall be filled and tested in sections of convenient lengths, which must not exceed 1000 metres. Where pipes are laid with steep gradients the length of pipes tested at any one time shall be as directed by the Engineer.

The ends of pipes under test shall be closed by means of caps or blank flanges with anchors all provided by the Contractor. Valves must not be used for this purpose. All scour valves and air valves shall be replaced by blank flanges before commencement of the test.

After laying, jointing and anchoring the pipe shall be slowly and carefully charged with water so as to avoid water hammer and all air shall be released through the upper pipe end or in case of an intermediate high point by installing a service connection with a tap. Pipes internally lined with mortar shall be allowed to stand full for at least 24 hours before testing.

The test pressure shall be applied by means of a manually or motor operated test pump connected to the pipe and to two parallel installed pressure gauges calibrated at an approved testing laboratory. The test pressure shall be maintained for at least 30 minutes without the pressure decreasing by more than 0.2 bar. During the test the pipe joints shall be inspected for leakages, but the duration of the test shall under no circumstances exceed 2 hours in which case a pressure drop of 0.3 bar shall be permissible.

Should leakage of water occur at the joints, the joint shall be reassembled to eliminate such leakage or, should this not prove possible, the Contractor shall supply and assemble new joints at his own expense. Should any pipe or joint burst or should water leak through the body of a pipe or joint the Contractor shall forthwith remove the faulty pipe or joint and replace them with new at his own expense. In all the above cases the length under test shall be re-tested as above described and the process repeated, if necessary, until the pipeline satisfactorily withstands the prescribed test.

A test report shall be prepared in respect of each and every test performed. The test report shall contain as a minimum the following data:

- Number and date of the test

- Description of the section tested with unambiguous indication of the extremities of the section

- Sketch showing in the order of laying, the number and the characteristics of the pipes, the fittings, the specials and other apparatus incorporated in the section

- Duration of the test, test pressure, results obtained

- Decisions relative to possible repair works and conclusions.

The test report shall be signed by the Contractor and the Engineer’s Representative.

The Contractor shall provide labour, install and work the test pump, pressure gauges and all other equipment required for the test and he shall fill the pipes with water and subsequently empty them after the test, all to the approval of the Engineer. The water used for testing shall be obtained from an approved source. Water drained from the pipes shall be discharged in a way that does not affect the stability of the Works or adjacent structures.

## Steel Pipes, Laying and Testing

### General

Steel pipes and fittings shall be factory made. Factory welding of longitudinal and spiral seams shall be by an automatic submerged arc welding process, except for smaller pipe diameters as detailed under “Manufacture” in this Paragraph. The ends of pipes, fittings and specials shall be fully prepared for jointing by the specified method, prior to delivery to site.

Internal and external corrosion protection systems shall normally be applied at the factory, and pipes and fittings shall be supplied to the site with adequate quantities of materials to permit the completion of the protection systems at welded joints on site.

Steel pipework shall comply with the relevant Standards and all assembling shall be made up from piping to this specification. The type of pipe shall be made of seamless steel below diameter 250 mm.

Steel pipework above 80 mm diameter shall be either coated externally and security wrapped where laid underground shall be painted externally when laid above ground or in ducts. In both cases they shall be internally lined at the manufacturer’s works with either an approved epoxy based or similar lining of not less than 250 microns in thickness or with concrete lining.  The internal lining shall be continuous across joints as far as this is practicable according to the size of pipe. Steel pipework below 80 mm bore, shall be galvanized.

Individual sectioning of pipework shall be cut to the correct length and joined with loose flanges. The flange connections shall have welded collars PN 10 with loose flanges, according to relevant standards and shall have material quality of 1.4301. Flexible joints shall be bolted gland or detachable flexible coupling as necessary.

### Materials

Steel pipes shall be manufactured and tested in accordance with relevant standards.

The steel quality shall be grade Fe 44 corresponding to DIN 1626 grade 44-2, having the following chemical composition:

- Carbon, max: 	0.21 %

- Phosphor, max: 0.04 %

- Sulphur, max: 0.04 %

### Manufacture

The manufacturing process shall be as follows:

- For pipes DN ≤ 300 mm seamless or HFI welded pipes are acceptable

- For pipes 300 mm ≤ DN ≤ 500 mm seamless, longitudinal or spiral welded pipes are acceptable  For pipes DN > 500 mm longitudinal or spiral welded pipes are acceptable.

Electric resistance and induction welding may be used for longitudinal seams in pipes manufactured from rolled steel strip having a thickness not exceeding 12.7 mm. Low frequency welding will not be accepted. Submerged arc welding, using an automatic process, may be used for longitudinal or spiral seam welds for pipes of nominal diameter exceeding 300 mm, using sheet steel having a thickness not exceeding 32 mm. There shall be at least two weld runs, one of which shall be on the inside of the pipe.

Heat treatment shall be applied to all cold finished pipes, and to the weld zones of electric resistance or induction welded pipes. Sheet and plate steel shall be shaped by rolling or pressing, width adjustment of sheet and plate shall be permitted.

Repairs by welding are not permitted in:

- Parent materials

- Seamless or HFI welded pipes

- Cracks in weld seams

Other defects in the weld seams shall be repaired in accordance with an approved weld repair procedure, and subsequently radiographed.

Jointers and girth welds shall not be permitted.

Pipe ends shall be bevelled or straight in accordance with relevant standards.

All units shall have a workmanlike finish, free from visual defects, and shall pass all specified tests. Butt welded, electric resistance and induction welded units shall not include welds used for joining lengths of strip steel. Skelp end welds if required on spiral pipe shall be as close to the middle of the pipe as possible and never closer to the pipe ends than 3 x nominal pipe diameter.

### Dimensions

#### Electric Resistance Welded Pipes

Electric resistance welded pipes shall be in conformity with the following table:

| Outside Diameter in mm | Minimum thickness in mm | Weight in kg/m | Hydrostatic test pressure in Bar |
| --- | --- | --- | --- |
| 60.3 | 2.8 | 3.97 | 70 |
| 73 | 3.2 | 5.51 | 70 |
| 88.9 | 3.2 | 6.76 | 70 |
| 114.3 | 3.6 | 9.83 | 70 |
| 141.3 | 3.6 | 12.22 | 60 |
| 168.3 | 3.6 | 14.62 | 60 |
| 219.1 | 4.0 | 21.22 | 51 |
| 273.1 | 4.0 | 26.54 | 41 |
| 323.9 | 4.0 | 31.54 | 35 |
| 355.6 | 4.4 | 38.11 | 35 |
| 406.4 | 4.4 | 43.62 | 31 |

Tolerances on the outside diameter shall be ± (0.5 % × OD + 1) mm. The wall thickness shall be within the limits: – 0.0 mm / + 10 % of the specified wall thickness.

#### Submerged Arc Welded Pipes

The outside diameter and wall thicknesses of spiral welded pipes shall be in conformity with the following table:

| Outside diameter wall thickness in mm | Standard in mm | Weight kg/m | Hydrostatic Test pressure in Bar |
| --- | --- | --- | --- |
| 219.1 | 4.5 | 23.8 | 50 |
| 273.0 | 5.0 | 33.0 | 40 |
| 323.9 | 5.6 | 44.0 | 34 |
| 355.6 | 5.6 | 48.3 | 34 |
| 406.4 | 6.3 | 62.2 | 29 |
| 457.2 | 6.3 | 70.0 | 28 |
| 508.0 | 6.3 | 77.9 | 26 |
| 558.8 | 6.3 | 85.9 | 26 |
| 609.6 | 6.3 | 93.8 | 24 |
| 660.4 | 7.1 | 114.0 | 26 |
| 711.2 | 7.1 | 123.0 | 24 |
| 762.0 | 8.0 | 149.0 | 22 |
| 812.8 | 8.0 | 159.0 | 21 |
| 914.4 | 10.0 | 223.0 | 23 |
| 1016.0 | 10.0 | 248.0 | 21 |
| 1120.0 | 10.0 | 273.0 | 22 |
| 1220.0 | 12.5 | 372.0 | 21 |
| 1320.0 | 12.5 | 403.0 | 241 |
| 1420.0 | 12.5 | 435.0 | 21 |
| 1520.0 | 14.2 | 529.0 | 21 |
| 1620.0 | 14.2 | 564.0 | 21 |
| 1720.0 | 14.2 | 600.0 | 20 |
| 1820.0 | 14.2 | 636.0 | 20 |
| 2020.0 | 16.0 | 795.0 | 17 |
| 2220.0 | 16.0 | 876.0 | 16 |
| 2540.0 | 17.5 | 1089.0 | 16 |

Tolerances on the outside diameter shall be:

- for pipes < 1000 mm: + (0.5 % × OD + 1) mm

- for pipes > 1000 mm: + 6 mm

Inside diameter tolerances at pipe ends shall be + 1.6 mm derived from circumferential measurement. Wall thickness (t) tolerances shall be:

- for t < 10 mm: – 0.35 mm/ + 10 % of the specified wall thickness

- for t > 10 mm: – 0.50 mm/ + 10 % of the specified wall thickness

The offset of the plate edges shall not exceed 10% of the wall thickness or 1.5 mm whichever is less. However, with a specified wall thickness less than 10 mm, the offset may reach a maximum of 1 mm over a length not exceeding the external diameter.

The centers of the inner and outer weld seams shall not be displaced by more than 3 mm from each other (4 mm for wall thicknesses over 16 mm).

The center of longitudinal and spiral weld seams shall not be displaced by more than 2 mm from the center of the weld groove. Complete weld penetration shall be ensured under any condition.

### Pipe lengths

Steel pipes shall be supplied in lengths as follows:

- Shortest pipe: 	 8.5 m

- Longest pipe: 	14.0 m

- Min. acceptable average length: 12.0 m

### Sampling, Inspections and Tests

For sampling purposes, the pipes shall be batched as follows:

- pipes < 500 mm: 	100 pipes or up to 100 pipes

- pipes > 500 mm: 	 50 pipes or up to 50 pipes

From each batch, one pipe shall be selected for destructive testing as enumerated below, before testing the samples shall undergo a heat treatment at 250 o C for 6 hours:

- Tensile tests to be performed on one sample cut from the parent material, and one sample cut perpendicular to the weld seam and containing the weld seam

- Bending tests to be performed on two samples cut perpendicular to the weld seam and containing the weld seam. The bending test shall be made by bending the sample through 180° around a mandrill having a diameter of three times the pipe wall thickness. After bending, the sample shall show no crack in the weld material, or between weld material and base metal, with a dimension exceeding 3 mm. alternatively, if cracking or fracture does occur, the sample shall be opened and the fracture surfaces examined. The sample will be regarded as having passed the test if the fracture surfaces show no gas pockets or slag inclusions having any dimension exceeding 2 mm.

- Flattening tests. Pipes of nominal diameter exceeding 50 mm and not exceeding 150 mm shall have test rings not less than 38 mm cut from them and flattened between parallel plates. Any weld in the sample shall be positioned at the point of maximum bending, and shall show no sign of fracturing until the distance between the plates is less than 75 % of the original outside pipe diameter. No sign of fracture in the base material shall occur until the distance between the plates is less than 60 % of the original outside diameter.

and nondestructive testing as follows:

- Impermeability tests of all pipes

- Surface inspection of all pipes

- Nondestructive inspection of all pipes

- Dimensional inspection of all pipes

The impermeability test shall take place at a testing laboratory to be approved by the Recipient. The test shall take place at room temperature with an applied water pressure of 50 bar for a minimum of 5 hours. The test shall take place before the pipe is isolated and the test reports shall be submitted to the Engineer for approval. The Contractor shall bear all costs of the impermeability testing.

### Internal Lining

#### Large Diameter Pipes

Pipes shall be internally coated with a cement mortar lining.

The cement mortar lining shall be made with sulphate-resisting cement and shall be applied by a centrifugal method.

#### Small Diameter Pipes

Pipes and fittings up to and including 150 mm nominal diameter shall be hot dip galvanized. Prior to galvanizing, units shall be thoroughly descaled and cleaned. Galvanizing shall be carried out by dipping in a bath containing not less than 98.5 % by weight of molten zinc. The whole surface of the unit coated with uniformly adherent zinc, capable of passing an approved copper sulphate solution immersion test. Galvanising shall be carried out prior to threading or jointing surfaces.

### External Coating

Pipes and fittings of nominal diameter greater than 150 mm shall be protected externally by reinforced bitumen enamel wrapping, or coal tar enamel wrapping.

Surfaces to be protected shall be thoroughly cleaned to remove all scale, rust, grease or other extraneous matter, by acid pickling, abrasive, mechanical or flame descaling. The surface shall be grid blasted to quality Sa 2½.

Reinforced bitumen or coal tar enamel wrapping shall comprise hot applied, mineral filled, bitumen, or coal tar, giving a minimum finished thickness of 3.5 mm. Reinforcement shall comprise an inner layer of 50 grams/square meter glass tissue, spirally wound with overlap, separated from the pipe surface by at least I mm thickness of enamel, and an outer sheathing of bitumen or coal tar impregnated, longitudinally reinforced, glass fabric spirally wound onto the pipe with overlap, and separated by at least I mm of enamel from the inner glass reinforcement.

Bituminous and coal tar coatings shall be tested for continuity of coverage by the use of holiday detectors. All pinholes or other discontinuities shall be made good. Adhesion of coatings shall be checked by cutting through the coating and peeling off a 50 mm wide strip. Inspection during and after peeling shall show adhesion between coating and pipe to have been obtained over the whole area.

### Marking, Tolerance Class and Certification

The following markings shall be made in white reflective weather resistant paint on one end of the pipe:

- Manufacturer’s mark

- Material grade

- Outside diameter and wall thickness

- Length of pipe in meters to two decimals

- Pipe number (individual and selected consecutively, no two pipes shall bear the same number). The pipe number shall ensure full traceability to test reports.

Tolerance symbols for pipes > 500 mm shall be marked as follows:

The inside diameter of the pipe ends shall be measured, derived from circumferential measurements, and assigned to the appropriate tolerance class. The respective symbol shall then be die stamped on each end.

| Tolerance Class (mm) | Symbol |
| --- | --- |
| – 1.6 to – 0.8 | - |
| – 0.8 to + 0.8 | 0 |
| + 0.8 to + 1.6 | + |

The pipe certification package shall comprise the Manufacturer’s Certified Test Reports and inspection certificate in accordance with relevant standard, including when required Independent Inspectors Reports and third party certificates, all marked with the supply contract number and containing:

- Heat and product analysis results. Mechanical test results.

- Nondestructive examination reports with a statement of method used.

- Statement of compliance with visual and dimensional checks. Statement of manufacturing process and type of heat treatment

- Statement of compliance with hydrostatic test requirements including test pressure.

- Inspection certificates and reports for surface treatments.

### Transport, Storage and Stringing of Pipes

All equipment necessary for the loading, transport to construction sites or storage sites and unloading shall be supplied by the Contractor.

Pipes shall be handled in such a way that damage is avoided as far as possible. They shall only be lifted with straps of a material and a form which protects the pipes and their coating from damage. The Contractor shall check the pipes for any visible defect or damage and notify the Engineer in case of any found. The Contractor shall be responsible for making good any damage or defect to the approval of the Engineer.

All pipes shall be protected against weather attack, including sunlight, and fouling during transport storage and stringing. If any pipe gets fouled, it shall be cleaned before installation.

The Contractor shall be responsible for obtaining all necessary permits for transporting the pipes. Wherever possible, the Contractor shall ensure that any weight restrictions on public roads are not exceeded. The Contractor shall be responsible for making good any damages caused to these roads. When pipes are collected from a storage site, the Contractor shall secure the remaining pipes against slippage. When a storage site is emptied of materials the Contractor shall clean the site and any access road and reinstate both to their original condition.

The pipes shall be strung consecutively along the working width on timbers or similar, with at least two per pipe, to avoid damaging or fouling the pipes. The pipes shall be strung in such a way that the normal use of the surrounding areas is disturbed as little as possible. Pipes shall be secured against rolling. When stringing pipes with diameter tolerance marks (+, 0, –), ends with the mark + shall never abut on ends with the mark.

### Bends

#### General

The pipeline shall be laid in such a way that it follows the outline of the terrain as closely as possible. The application of bends shall be limited to sudden changes of direction or gradient. Adjustment to the outline of the terrain shall, where possible, be made by suitable excavation of the trench, so that the pipe can follow the trench by elastic deformation only. If the Contractor so wishes and he has obtained the Engineer's approval, field bends may be applied. The Contractor shall only use factory made bends where stated on the drawings. Where technological reasons prevent him from using bends as specified, he is responsible for adapting these bends to his technology.

#### Elastic Bends

Changes of direction or gradient with elastic deformations - elastic bends - shall be made in circular arcs with minimum radius as defined in the following table:

STEEL PIPES: Elastic Bends, Minimum Radius in meters

| ND | OD | Wall | min, m, min , m, |  |
| --- | --- | --- | --- | --- |
|  |  |  | Design Factor Design Factor |  |
| [mm] | [mm] | [mm] | F = 1.0 | F = 0.9 |
| 200 | 219.1 | 4.5 | 335 | 372 |
| 250 | 273.0 | 5.0 | 417 | 463 |
| 300 | 323.9 | 5.6 | 495 | 550 |
| 350 | 355.6 | 5.6 | 543 | 603 |
| 400 | 406.4 | 6.3 | 621 | 690 |
| 450 | 457.2 | 6.3 | 698 | 776 |
| 500 | 508.0 | 6.3 | 776 | 862 |
| 550 | 558.8 | 6.3 | 853 | 948 |
| 600 | 609.6 | 6.3 | 931 | 1034 |
| 650 | 660.4 | 7.1 | 1009 | 1121 |
| 700 | 711.2 | 7.1 | 1086 | 1207 |
| 750 | 762.0 | 8.0 | 1164 | 1293 |
| 800 | 812.8 | 8.0 | 1241 | 1379 |
| 900 | 914.4 | 10.0 | 1397 | 1552 |
| 1000 | 1016.0 | 10.0 | 1552 | 1724 |
| 1100 | 1120.0 | 10.0 | 1711 | 1901 |
| 1200 | 1220.0 | 12.5 | 1863 | 2070 |
| 1300 | 1320.0 | 12.5 | 2016 | 2240 |
| 1400 | 1420.0 | 12.5 | 2169 | 2410 |
| 1500 | 1520.0 | 14.2 | 2321 | 2579 |
| 1600 | 1620.0 | 14.2 | 2474 | 2749 |
| 1700 | 1720.0 | 14.2 | 2627 | 2919 |
| 1800 | 1820.0 | 14.2 | 2780 | 3088 |
| 2000 | 2020.0 | 16.0 | 3202 | 3557 |
| 2200 | 2220.0 | 16.0 | 3518 | 3909 |
| 2500 | 2540.0 | 17.5 | 4026 | 4473 |

#### Field Bends

Changes of direction or gradient which cannot be made with elastic bends shall be made with field bends, produced by the Contractor.

Field bends shall be made in the field by bending straight pipe with a suitable bending machine. Over the whole bent section, these bends shall have a constant radius as prescribed on the applicable standard drawing. For the control of bending radius, the Contractor shall, for each diameter used, provide a 2.5 m long gauge constructed with the prescribed radius. Suitable and well supporting matrices shall be used when percolated pipes are bent. The bends shall be made in such a way that no measurable reduction of the wall thickness occurs during bending.

Bending operations may only take place when the coating over the last 12 hours has had a surface temperature not higher than 40°C measured on the sunlit side. The bending itself may only take place when the surface temperature of the coating is 30°C or less.

Measures to be taken during periods of time where the temperatures specified above cannot be ensured by usual procedures, may be:

- Whitewash with suitable paints

- Shielding against direct sunshine

- Water cooling

- Bending operations only to take place in the morning

Specific measures to be applied shall have the Engineer's approval.

The Contractor shall provide and use instruments capable of measuring the angle to an accuracy of 0.5°. The bending machine shall be operated by a skilled person with experience in the production of field bends.

No wrinkles shall occur in the wall, and the difference between the maximum and minimum diameters shall at no place exceed 3 % of nominal diameter D.

Bending in steps shall be made in accordance with the applicable standard drawing. Pipes must not be bent closer to the ends than two times the diameter and no cuts must be made closer than 2 m (1.5 m for pipes with nominal diameter D ≤ 300 mm) from the bent section.

When bending spiral welded pipes, only pipes not containing skelp ends may be used. When bending longitudinally welded pipes, the weld seam shall be placed in the tensile side 30° – 45° from the neutral axis if the weld seam is visible. However, in the case of crossings having a length that allows the use of only two pipes, each containing both an over bend and a sag bend, the longitudinal weld seam shall be along the neutral axis. Irrespective of longitudinally or spiral welded pipes being used at these crossings, the over bend and the sag bend shall be separated by at least 1.0 m of straight pipe in order to ensure the required roundness of the pipe.

The Contractor shall maintain a record of all bends constructed, including pipe number, pipe length, angle of bend and location in the pipeline.

Pipes that are rendered unusable through incorrect bending shall be replaced at the Contractors expense.

Pipe coating which is damaged during bending shall be repaired by the Contractor at his own expense. All bends constructed shall be legibly paint marked with angle and scope (over bend or sag bend, etc.).

#### Factory Made Bends

Changes of direction or gradient which cannot be made either with elastic bend or field bends shall be made with factory-made bends supplied by the Contractor.

Factory-made bends shall be made with R = 1.5 × D or 3 × D. When factory made bends which are cut in the field, the portion not immediately required shall be marked with its new angle.

#### Tees and Y’s

Tees, crosses, laterals, Y’s, headers, or other fittings that provide means of dividing or uniting flow in pipelines shall be either factory made or manufactured at site.

Tees and Y’s shall be reinforced by collars welded to the main pipes around all branches and tees. The width of the collars shall be 250 mm and the thickness shall be 10 mm for all dimensions of branches and tees.

### Welding of Pipelines

The Contractor shall provide all necessary personnel, equipment and materials. The equipment shall include, but not be limited to:

- Welding machines and generators suitable for pipeline welding.

- Preheating equipment which ensures uniform preheating around the whole circumference of welding ends.

- Post-weld heat treatment equipment.

- Internal and external line-up clamps (the external clamp shall be hydraulically operated).

- Protective canopies (or umbrellas and wind shield collars) so that welding can be carried out even in relatively bad weather.  Weather proof, insulating mats for the internal insulation of girth welds (at least 1.5 × D wide).

The Contractor shall supervise the site, the welders and their work during the entire working period. For this purpose the Contractor shall use a qualified welding engineer or alternatively, if accepted by the Engineer, an engineer with documented thorough theoretical knowledge and practical experience in the performance and evaluation of the welding work.

The welding shall be inspected by an independent inspection company engaged by the Contractor. It is the sole responsibility of the Contractor to document that welding and welding inspection fulfil all specified requirements.

#### Materials

The steel covered by this specification shall comply with the base metal specified in Paragraph “Steel Pipes, Laying and Testing”.

Attention shall be paid to obtaining a good working environment such as selection of low smoke developing consumables, etc.

The weld filler metal selected shall give a weld metal matching the base metal properties as closely as possible. The yield strength of consumables shall neither overmatch the base material yield strength by more than one level in accordance with relevant standard, nor shall under matching be allowed.

#### Welding Processes

Acceptable welding processes are:

- Shielded Metal Arc Welding (Stick) SMAW

- Gas Tungsten Arc Welding (TIG) GTAW

- Gas Metal Arc Welding (MIG/MAG) GMAW

- Flux Cored Arc Welding FCAW

The use of welding processes other than those listed above is permitted only with the prior approval of the Engineer. Processes may be used in combination if the same combination and sequence of processes have been qualified by the welding procedure qualification test.

#### Welding Procedure Qualification

The Contractor shall submit detailed welding procedure specifications complying with API 1104. All dimensions, all combinations of materials to be joined and all repairs welding shall be covered by the procedure specifications. The procedure specifications are subject to the approval by the Engineer.

The Engineer may approve, at his sole discretion, the use of already established, sufficiently tested and documented procedures not more than 2 years old. Transfer of welding procedure qualification records from one Contractor to another is not permitted.

For each procedure specification and prior to start of production welding the Contractor shall carry out welding of test joints under site conditions following all of the details of the approved procedure specifications.

The qualification test shall be carried out on steel with the highest specified minimum yield strength/maximum carbon equivalent which is expected to be covered by the Welding Procedure Specification. All the results from the procedure qualification records shall be submitted to the Engineer for approval of welding procedures.

#### Qualification of Welders and Welding Operations

Only skilled welders and welding operators who can document qualifications relevant for pipeline welding will be accepted by the Engineer. Prior to the performance of any production welding operators shall qualify for the relevant welding procedures according to relevant standards.

The qualification tests are acceptable if they meet the requirements for visual examination, destructive testing and for radiographic examination as specified in relevant standards. The testing shall be carried out by an approved laboratory at the Contractor’s expense. Welder and welding operator performance test certificates shall be issued and kept on site during the whole working period.

Welder and welding operator qualification tests may be performed together with welding procedure qualification tests.

These certificates are only valid for six months after the last welding.

#### Welding Preparation

Items material grades, wall thicknesses and pressure ratings shall conform to the requirements laid down in the applicable drawings and specifications.

Each pipe or component shall be visually inspected to ensure that it has not sustained any visually determinable damage. Disposition of damaged items shall be resolved in consultation with the Engineer. All requirements for welding preparation contained in the qualified welding procedure specification shall be strictly adhered to.

#### Welding

All welding shall be performed by qualified welders and strictly in accordance with qualified welding procedures.

Welding shall be suspended by the Contractor when prevailing weather conditions will impair the quality of the work, e.g. airborne moisture, blowing sand, high winds or thunderstorms.

Stray arching outside the weld groove is not permitted. Should stray arching outside this area occur, this shall be brought to the attention of the Engineer who may require any such damaged section to be repaired or cut out at the Contractor’s expense.

Earth connections for the welding shall always be positioned in the center of the joint during root and cap-bead laying. They shall be mechanically or magnetically connected to the pipe.

Each pass shall be completed around the whole circumference before the next pass is started.

The position of start/stop on subsequent passes shall not be identical.

Upon completion of the cap bead, the weld and the pipe surface shall be cleaned of weld spatter and other deposits, and shall then be wrapped with a dry waterproof insulating mat to ensure a slow cooling of the weld zone and to give protection against rain.

#### Cleaning after Welding

The surface shall be dry and free of oil, grease, soil and concrete residues. All loose rust and mill scale shall be removed by wire brushing immediately before welding inspection. On straight pipes brushing shall be done mechanically using sharp brushes to avoid polishing of the steel surface. Therefore a stock of readily accessible new brushes is required.

Welds fabricated with basic finer metals shall be washed with fresh water.

Cleaning by sandblasting to grade Sa 2 is allowed as an alternative.

#### Post Weld Heat Treatment

PWHT of weld seams shall only be carried out if specified in the approved welding procedure or where this is indicated in the project material. PWHT procedures shall be approved by the Engineer.

#### Identification of Weld Seams

Every girth weld shall be numbered by the Contractor in accordance with a system to be specified by the Engineer. This number shall be painted on the pipe coating on one side of the joint between 0.5 m and 1.0 m from the seam together with the pipe number and pipe length to facilitate completion of the pipe book. For each pipeline and each pressure test section, the Contractor shall fill out preprinted forms and enter these in a pipe log. As the work progresses, the Contractor’s shall present the pipe log forms to the Engineer. Before the start of a pressure test, the completed pipe log for the section in question shall be handed over to the Engineer.

#### Closing of Pipe Ends

During welding on a pipeline segment all open ends of that segment shall be kept closed with a plug or a cap.

At interruption in the pipeline construction, the Contractor shall close the ends of the pipe strings. The closure shall be tight enough to prevent any entry of foreign matter into the pipe.

Plugs or caps must not be fixed by welding or by any other method which damages the pipe. They shall be securely attached to the pipe and shall remain in place until the string is laid.

### Welding Inspection

#### General Requirements

Examination shall be performed according to this specification, previously stated standards and the following codes and standards:

- Ultrasonic examination according to ASME Boiler and Pressure Vessel Code, Section V, Nondestructive Examination, Article 5, Ultrasonic Examination Methods for Materials and Fabrication.

- Magnetic particle examination according to ASME Boiler and Pressure Vessel Code, Section V, Nondestructive Examination, Article 7, Magnetic Particle Examination.

- Visual examination according to ASME Boiler and Pressure Vessel Code, Section V, Non-destructive Examination, Article 9, Visual Examination.

- Hardness measurement according to ASTM E110, Standard Test Method for Indentation Hardness of Metallic Materials by Portable Hardness Testers.

The Contractor shall engage a qualified independent inspection company which shall perform, evaluate and document all welding inspection. The inspection company shall be approved by the Engineer.

All non-destructive examination shall be performed according to a written procedure. The procedure shall conform to the requirement of the adequate method standard and this specification. Procedures shall be submitted to the Engineer for approval and shall be qualified to the satisfaction of the Engineer.

#### Extent of Examination

All welds shall be 100 % visually examined.

Guarantee welds (welds which will not be pressure tested) and tie-in welds shall be 100 % examined by radiography as well as by ultra-sound.

All welds which have been repaired or replaced shall be 100 % re-examined by the same methods and with the same acceptance criteria as required for the original work.

Ultrasonic examination may substitute radiography where radiographic examination is impractical and may be used as general back-up for radiography in case of interpretation/verification problems.

Socket welds and branch connection welds which are not radiographed shall be examined by magnetic particle or penetrant methods to the extent stated for butt welds.

Where spot examination is required in subsequent sections, the welds shall be selected to ensure that the work of each welder and each welding procedure is included.

When required spot examination reveals defects, two additional welds, the preceding and the subsequent welds made by the same welder, shall be examined.

If one of these welds shows defects, three preceding and three subsequent welds shall be examined at the Contractor's expense.

If five or more subsequent welds of one welder show defects, all welds of this particular welder shall be additionally examined at the Contractor's expense.

All butt welds in piping systems with design pressure > 16 bar shall be examined by 100 % radiography. At least 10 % of other butt welds shall be examined by radiography along their entire circumference as described above. The Engineer may specify greater extent of examination.

In particular for treatment plants all welding’s in:

- Piping containing lethal substances

- Hydrogen service piping

- Underground process piping

- Jacketed (inner) pipes shall be examined 100 % by radiography.

#### Acceptance Criteria

Acceptance criteria shall be as stated in API 1104.

#### Production Testing

The Engineer shall be entitled to select a number of seams for destructive testing.

The Contractor shall be responsible for cutting out the seams, beveling the pipe ends and rewilding the joint. The destructive tests shall, unless otherwise agreed, be made in accordance with the requirements in the respective general welding specification covering qualification tests for welding procedures.

The Recipient will bear the cost of these tests, if the welds are proved to be acceptable. However, if it turns out that the seam does not comply with all the requirements, the Contractor himself shall bear the costs. In this case, the Engineer may insist on an additional seam being tested, and the costs of the testing and renewal of this seam shall be paid by the Contractor, irrespective of the results. If this seam does not comply with the requirements, the control may be further extended at the Contractor’s expense.

The extent of any such supplementary inspection work shall be decided by the Engineer with the aim of establishing in a satisfactory manner whether the welding work complies with the requirements or not. If any change of personnel takes place during the course of the welding work, this could influence the of weld seams and the Engineer may require a new seem to be destructively tested at the Contractor's expense.

##### Document Requirements

Before examination:

- Certificates for NDE personnel

- NDE procedures

- Report forms

- Request for deviations, if any, from specified requirements

During examination:

- Field reports

After examination:

- Authorized examination reports with enclosed field reports and films.

### Coating of Weld Seams

Upon successful completion of all inspection procedures, the weld seams and their surroundings shall be carefully cleaned and protected with an internal lining and external coating as specified in Paragraph “Cleaning and Welding” and “Post Weld Heat Treatment”.

### Pipe Lowering

Pipe lowering shall be carried out in a safe manner, in accordance with applicable safety regulations and normal practices.

Bitumen coated pipes shall be handled with suitable slings which do not damage neither pipe nor coating. A sufficient number of lifting machines (e.g. side booms) shall be used to ensure that the pipe is not subject to detrimental stresses. The radius of curvature of any elastic deformation during lowering-in shall not be less than indicated in the longitudinal sections.

The Contractor shall, before lowering the pipe, ensure that the bottom of the trench is even and free from stones and other deleterious matter which may damage the coating.

The lowering-in procedure shall ensure that the pipe is not subjected to shocks or unnecessary stresses. The pipe shall be laid in as straight a line as possible, keeping a distance from the walls of the trench of at least 0.20 m. It shall be supported along its whole length and it shall, as far as possible, lie free of stresses. If a section is damaged during lowering, it shall be taken up again, repaired and relowered. Any damage which may affect the structural quality of the pipeline shall be treated as directed by the Engineer. The Contractor shall bear all costs associated herewith.

In areas where the pipe may be buoyant, it shall be secured against up drift with reinforced concrete “riders” or with anchorage to the solid bottom, so that a safety factor of 1.2 against buoyancy is achieved. Modification of anchors or any other handling which damages the galvanization of the anchors is not allowed.

If conditions permit, temporary loading can, with the approval of the Engineer, be obtained by filling the pipe with clean water after lowering. The water shall fulfil the requirements set up for potable water. After the pipe has been lowered, and permanent weighting or anchorage has been applied, the pipe can be emptied for water.

Where possible the ends of all lowered pipeline sections shall be closed with watertight caps. The Contractor is responsible for keeping the pipeline internally clean and free from foreign matter.

Any additional excavation required after the pipe has been lowered shall only be carried out with the permission and in the presence of the Engineer's Representative.

### Other Jointing Methods

#### Threads

Steel pipes with nominal diameters up to and including 150 mm may be threaded at both ends and provided with a detachable screwed coupling attached to one end. Couplings shall have a minimum length of 44 % of the pipe diameter, plus 30 mm, and shall have parallel threads. Pipe ends shall be provided with taper threads. Couplings shall be made from similar material to that of the pipes.

#### Flanged Joints and Mechanical Couplings

Where flanges are required they shall be forgings or made from steel plate meeting the steel specification of the pipe material. Flanges shall be weld-on type and drilled to the application, NP 10 or NP 16.

Mechanical couplings shall be as specified for ductile iron pipes.

Bolts and gaskets, and corrosion protection shall be as specified for ductile iron pipes.

### Pipe Laying and Pressure Testing

#### Excavation of Trenches

Trenches shall be excavated to the width and the depth and to the lines shown on the drawings and shall be carried out in accordance with Paragraph “Earthworks”.

#### Bedding of Pipes

The bedding to the pipes and fittings shall be carried out in accordance with Paragraph “Earthworks”.

#### Thrust Blocks

Thrust blocks, as specified for ductile iron pipes, shall be provided where a flexible joint e.g. mechanical coupling, is installed in the pipeline adjacent to a bend, branch or blank end.

#### Surround to Pipes

##### Selected Fill Surround

The filling to the pipeline shall be carried out in accordance with Paragraph “Earthworks”.

##### Concrete Bed and Surround

Concrete bed and surround to the pipeline shall be provided, where required, as specified for ductile iron pipes.

###### Pipe Supports

Pipe supports shall be provided as specified for ductile iron pipes.

###### Backfilling

The remainder of the trench above the pipe surround shall be backfilled with approved selected backfill material in accordance with the Specification.

###### Testing of Pipelines

Testing of pressure pipelines shall be carried out as specified for ductile iron pipes.

### Cathodic Protection System

#### General

The work for the cathodic systems comprises measurements, analyses, design of project, supply and installation, control and tests of the installed system as well as an operation and maintenance manual.

#### Standards

The work for the cathodic protection system shall be designed, prepared and installed in accordance with the requirements of relevant standards and scientific sources.

#### Specification of the Works

The following specification gives the minimum requirement to the work to be carried out by the Contractor.

- Measurements to determine the specific resistivity of the soil along the pipe routes.

- Measuring of the pH-value along the pipe routes to determine the variation of soil characteristics.

- Analyses of the chloride and sulphate content along the pipe line to determine the positions of isolating flanges.

- Investigation of electrical continuity along the pipe line to determine the positions of isolating flanges.

- Select suitable places for anode beds.

- Decide on suitable points on the pipe line for current connections.

- Preparation of project including calculations and criteria for approval of the Engineer.

- The project shall be shown on the pipe line plans and include divisions of the pipes with isolating flanges, sites for transformer/rectifier units, anode beds, measuring posts and cable routes.

- Detail drawings of cabinets for transformer/rectifier units and for measuring posts. j) 	Electrical diagrams.

k) 	The anodes shall be designed to have a life time of minimum 15 years.

#### Material Specification

##### Ancillary Anodes

Iron silicon anodes shall be used on pipe line sections, which are protected by the external current cathodic system.

The dimensions of the anodes shall be:

| - Diameter of cap: | 100 mm |
| --- | --- |
| - Body diameter: | 75 mm |
| - Length: | 1500 mm |
| - Weight: | 45 kg |

The chemical composition of the anodes shall be:

- Silicon (Si): 	 	14-16 %

- Chromium (Cr): 		4-4.5 %

- Carbon (C): 	 	1 %

- Manganese (Mg): 	1 %

- Iron (Fe): 	approx. 78 %

The caps shall be protected by an insulating material and the cable connection shall also be insulated with hard material.

The cast anodes shall be without cracks and non-porous. A sample shall be taken from each anode for chemical analyses and for electro analyses.

##### Anodes for Ground Installation

Magnesium anodes shall be used on pipe line sections, which are protected by the galvanic system. The anodes shall have a weight of 7 to 15 kg.

The anodes shall be 99.9 % magnesium (Mg).

10 % of the anodes shall be tested for the following:

- Electrical potential: (ref Cu/CuSO, electrode) -1500 mV in seawater

- Theoretical current capacity: 	2200 Ah/kg

- Anode efficiency: 	 	50%

The anodes shall be free from dirt, rust, scale, paint and other foreign substances.

##### Anode Bed Material

The material to be used for iron silicon anode beds shall be coke dust with about 10 % unslaked lime mixed into the coke during application. The maximum size of the coke dust particles must be 10 mm and the passing ratio from sieve No 100 shall not exceed 5 %.

The electrical resistivity of the material should not be greater than 5 ohm. 200 kg of material shall be used for every anode.

The material to be used for magnesium anode beds shall be a mix of gypsum, bentonite and sodium sulphate to give an electrical resistivity of 25–100 ohm depending on the resistivity of the surrounding soil.

##### Transformer/Rectifier Unit

The unit shall be a silicon diode, oil cooled type with a capacity 2 times bigger than the required capacity. The unit shall be protected against over-voltage and be able to work continuously between – 15 and + 70 degrees C.

The volt meter in the unit shall have a range of 0–15 V and the ampere meter, also in the unit, a range of 0–50 A both with an accuracy of 1 %.

The cabinet, cables and other items shall be as specified in the Paragraph for electrical installations and the cabinets shall be mounted securely on reinforced concrete foundations. The unit shall be connected to the electrical supply network with an approved electricity meter.

##### Measuring Posts

The measuring posts shall be small cabinets with the necessary pole connections securely set into concrete in the ground. The Paragraph in the specification for electrical installations shall be adhered to. A double separate cable shall be connected to every anode from the measuring posts with a minimum 3 m long cable without any joints. The current conductor in the anode shall be steel.

Reference electrodes shall be Cu/CuSO4.

##### Installation

Installation of anodes shall be carried out in accordance with relevant practice. The anode bed material shall surround each anode with a minimum layer of 250 mm. Electrical connections shall be carried out as thermos-welds and joints shall be insulated with approved materials.

The resistivity of anode beds shall be controlled immediately after installation.

All cables in the ground shall be marked with the appropriate cable tape and be laid in accordance with the Paragraph in the electrical specification.

Excavation and backfilling shall be carried out in accordance with the relevant Paragraph in this specification.

##### Pre-Commissioning

After completion of the installation work of the systems the following measurements shall be carried out and recorded as documentation:

###### External current system

- Potential of pipe/ground

- Resistance of anode bed

- Output voltage of transformer/rectifier

- Current for anode bed

- At each point of the pipe line the potential shall not be less than – 850 mV measured against the reference Cu/CuSO4 electrode.

- The potential of pipe/ground shall not be less than – 2 volt at the point of current connection on the pipe

- The resistivity of the combined anode and bed shall not exceed 1 ohm

- The supplied current from the transformer/rectifier shall not be less than    80 % of the demand of the system.

###### Galvanic anode system

- Potential of pipe/ground

- Potential of anode/ground

- Potential of system/ground

- Anode current

- The potential of pipe/ground shall not be less than – 850 mV measured against the reference Cu/CuSO4 electrode at each point.

If the above measurements are not in accordance with the requirements, the Contractor shall at his own cost make the necessary corrections on the system until the measurements are in accordance with the specification.

##### Operation and Maintenance

The Contractor shall prepare an operation and maintenance manual including the final measurements to be submitted to the Engineer for his approval.

If the cathodic protection system is not handed over to the Employer immediately after the installation and a 12 months running-in period the required measurements and controls shall be performed by the Contractor and recorded in accordance with the manual.

If any faults occur in the systems during this period, they shall be rectified by the Contractor at no additional cost to the Employer.

### Isolating Flanges

Isolating flange to protect the steel pipes from stray currents shall be used at the following positions:

- At all connections between tees on steel pipes and ductile iron branches.

- At either side of all valves on steel pipes.

- At either side of overhead or underground high voltage lines (over 50 kV) at a distance of 75 meter from the high voltage lines.

- At selected positions as determined by the Contractor’s design of the cathodic protection system.

- At all other places where an isolating flange is deemed necessary.

The isolating flanges shall secure a complete electrical disconnection of the pipe sections or pipe and appurtenances.

The insulating gasket shall be 4 mm thick with minimum 1 mm thick vulcanized gasket material or similar on either side.

The isolating sleeves around the bolts shall be in one piece for each bolt and shall extend through the isolating and steel washers at either end. Wall thickness to be minimum 1.0 mm.

The isolating washers shall have a diameter of 15 mm larger than the diameter of the steel washers and a thickness of minimum 4 mm.

## Stainless Steel Pipework

Stainless steel (SST) pipes shall be of weldable quality according to relevant standard. Material shall be 1.4404 (AISI 316L) or 1.4301 (AISI 304).

The minimum wall thickness of SST-Pipes:

| Nominal Diameter | Wall Thickness |
| --- | --- |
| ND 25 - 32 | 2.0 mm |
| ND 40 - 200 | 2.0 mm |
| ND 250 - 350 | 2.5 mm |
| ND 400 - 600 | 3.0 mm |

## Mild Steel Pipework

Steel (ST) pipework below and equal 200 mm shall be of the hot finished seamless steel type according to relevant standards. All pipe assemblies shall be made up from piping to these requirements.

The overall dimensions and minimum wall thickness of ST-Pipes:

| Nominal Diameter | Outside Diameter |  | Wall Thickness |
| --- | --- | --- | --- |
| ND 25 | 33.7 mm | x | 2.6 mm |
| ND 32 | 42.4 mm | x | 2.6 mm |
| ND 40 | 48.3 mm | x | 2.6 mm |
| ND 50 | 60.3 mm | x | 2.9 mm |
| ND 65 | 76.1 mm | x | 2.9 mm |
| ND 80 | 88.9 mm | x | 3.2 mm |
| ND 100 | 114.3 mm | x | 3.6 mm |
| ND 150 | 168.3 mm | x | 4.0 mm |
| ND 200 | 219.1 mm | x | 6.3 mm |

Steel pipework above or equal 250 mm shall be of the welded steel tubing type and shall be according to relevant standards. All pipe assemblies shall be made up from piping to these requirements.

The overall dimensions and minimum wall thickness of ST-Pipes:

| Nominal Diameter | Outside Diameter |  | Wall Thickness |
| --- | --- | --- | --- |
| ND 250 | 273.0 mm | x | 5.0 mm |
| ND 300 | 323.9 mm | x | 5.6 mm |
| ND 400 | 406.4 mm | x | 6.3 mm |
| ND 500 | 508.0 mm | x | 6.3 mm |
| ND 600 | 609.6 mm | x | 7.1 mm |
| ND 700 | 711.2 mm | x | 7.1 mm |
| ND 800 | 812.8 mm | x | 8.0 mm |
| ND 900 | 914.4 mm | x | 10.0 mm |
| ND 1000 | 1016.0 mm | x | 10.0 mm |

The individual sections of pipework shall be pre-fabricated in required lengths. Connections shall be prewelded according relevant standards, min. PN 10-16, unless required with special connections.

Connections to be jointed at site shall be made by pre-welded flanges, unless otherwise required.

## Galvanized Steel Pipes

Galvanized steel pipes shall be hot galvanized according to the relevant standards.

Galvanized steel pipes and fittings shall be supplied with either flanged ends or with threaded ends.

## Copper Pipes and Fittings

Copper tubing and fittings for shall be light gauge copper tubing and shall conform to the relevant standards.

The fittings shall be compression type fittings approved by the Engineer.

Pipes shall be fixed clear of walls or soffits with cast brass brackets at no more than 1.5 m centers.

## Concrete Pipes, Laying and Testing

### General

Concrete sewerage pipes shall be tested according to the relevant standards.

All pipes and fittings shall be transported, stored, handled, laid and jointed strictly in accordance with the manufacturer’s instructions or recommendations.

### Pipe Laying and Testing

#### Excavation of Trenches

Trenches shall be excavated to the width and the depth and to the lines shown on the drawings and shall be carried out in accordance with Paragraph “Earthworks”

#### Bedding of Pipes

The bedding to the pipes and fittings shall be carried out in accordance Paragraph “Earthworks”

#### Surround to Pipes

Selected Fill Surround:

The filling to the pipeline shall be carried out in accordance Paragraph “Earthworks”

Concrete Bed and Surround:

Concrete bed and surround to the pipeline shall be provided, where required, as specified for ductile iron pipes.

#### Pipe Supports

Pipe supports shall be provided as specified for ductile iron pipes.

#### Backfilling

The remainder of the trench above the pipe surround shall be backfilled with approved selected backfill material in accordance with the Specification.

#### Testing

Sewer pipes shall be tested in the shade with air or water as specified below or as instructed by the Engineer when they have been bedded and jointed and before any concrete surround or backfill is placed. A further test shall be carried out when any concrete surround has been completed and when backfill has been placed and compacted to a depth of 300 mm above the crown of the pipeline.

Air Test: 	 Pipelines above DN 750 mm

Pipelines to be air tested shall have air pumped into the length under test until a pressure equivalent to 100 mm of water indicated on a graduated glass U tube gauge.

After a period of five minutes without any further pumping this pressure shall not have fallen below 75 mm water gauge. The method of pumping shall be approved by the Engineer and shall be such as to avoid significant changes in the temperature or humidity of the air pumped into the pipeline.

Water Test: Pipelines up to and including DN 750 mm:

Pipelines to be water tested shall be filled with water under a pressure head of not less than 1.2 m above the crown of the pipe at the high end and not more than 6 m above the pipe at the lower end. Steeply graded pipelines shall be tested in sections so that the above maximum pressure head shall not be exceeded.

Unless otherwise agreed by the Engineer the test shall commence one hour after filling the test section at which time the level of the water at the vertical feed pipe shall be made up to produce the required 1.2 m minimum test head. The loss of water over a 30 minute period shall be measured by adding water at regular 10 minute intervals to maintain the original water level and recording the amounts added. The section of the pipeline would have passed the test if the volume of water added does not exceed 0.12 liters per hour per 100 meters of pipeline per millimeter of nominal internal diameter of pipe.

With the approval of the Engineer non-pressure pipelines with a nominal bore greater than 1000 mm may alternatively be tested by a combination of visual inspection from the inside and the use of equipment designed to test the tightness of individual joints.

For non-pressure pipelines the total infiltration shall not exceed 6 liters per day per millimeter of nominal bore per kilometer of pipeline, and no pipe or joint shall show visible infiltration flow during an internal inspection. The infiltration shall be measured after backfilling has been completed and the groundwater has returned to its pre-construction level (a minimum of 7 days shall be left after backfilling) and after all pressure testing has been completed.

The Contractor shall provide labour, install and work the test pump, pressure gauges and all other equipment required for the test and he shall fill the pipes with water and subsequently empty them after test, all to the approval of the Engineer. The water used for testing shall be obtained from an approved source. Water drained from the pipes shall be discharged in a way that does not affect the stability of the Works or adjacent structures.

## Plastic Pipes, Laying and Testing

### Unplasticized Polyvinyl Chloride (PVC) Pipes

Unplasticised PVC pipe (uPVC) shall only be used for water and drainage purposes with the express approval of the Engineer and shall comply with the relevant standards and test methods.

The Contractor shall advise the manufacturer of the climatic and transporting conditions at the site of the Works and shall seek his advice on the storage of PVC materials on site. Subject to the Engineer’s approval this advice shall be followed at all times.

Gravity pipes shall have ring stiffness at least SN 8 kN/m2.

#### Jointing

Except in the case of flanged joints and where otherwise specified or approved by the Engineer pipe joints shall be flexible and sealed with a rubber ring or gasket to the approval of the Engineer and shall withstand the various tests specified in the applicable standards. For pipes with a nominal bore of 100-230 mm the joints shall be capable of withstanding a deflection of not less than 3.0 degrees in any direction and for pipes with a nominal bore of 250-330 mm a deflection of 2.0 degrees and from 350 to 600 mm 0.5 degrees in any direction. All pipes shall be capable of withstanding a "draw" of 13 mm over and above the initial jointing allowance. The initial jointing allowance is the gap measured parallel to the center line of the pipeline and shall not be less than 6 mm or more than 13 mm or as otherwise recommended by the pipe manufacturer and approved by the Engineer. Pipes and fittings shall be indelibly marked prior to laying to indicate the correct initial jointing allowance.

PVC pipes shall have mechanical joints of a type suitable for the liquid to be carried by the pipework.

Small-bore pipework shall be jointed with PVC “hand tight” screwed fittings of standard manufacture.  Adhesives for cold solvent welding of pipes and their elements for pipes shall comply with DIN 16970 or equivalent. PVC pipes shall be capable of withstanding ultraviolet degradation. A rodent inhibitor shall be incorporated in the material of the pipe.

Except in the case of flanged joints and where otherwise specified or approved by the Engineer pipe joints shall be flexible and sealed with a rubber ring or gasket to the approval of the Engineer and shall withstand the various tests specified in the applicable standards.

### HDPE Pipes

All HDPE pipes and fittings shall be manufactured by a quality assured manufacturer in accordance with the ISO 9000 system. PE pipes and fittings shall comply with the relevant provisions of CEN-standard for water and wastewater and for gas.

The pipes shall be manufactured from high-density polyethylene containing only those antioxidants, UV stabilizers and pigments necessary for the manufacture of potable water black pipes. The Contractor shall provide an approved third party certificate to verify the above.

HDPE pipes shall be manufactured from PE 100 material, as classified by the European Technical Committee Report CEN/TC 155. In accordance with relevant standard the PE 100 material shall have a minimum required strength (MRS) value of 10 MPa. The pipes and fittings shall be colored blue (potable water), yellow (gas) or black (wastewater) and be suitable for below-ground use.

Gravity pipes shall be engineered light weight pipes with (structured wall pipe type) with ring stiffness larger than SN 8 kN/m2.

Pressure pipes shall be of pressure class appropriate for fulfill the design purpose. The couplings and fittings shall be designed for a nominal working pressure (at least the same as for pipes) and a temperature of 40°C and shall fit the HDPE pipes.

Generally, all buried pipes shall be jointed using either butt or electro fusion welding techniques. Small diameter pipes (diameter<63 mm), pipes within structures and pipes connecting to metal fittings shall be jointed using mechanical jointing techniques, such as compression, flanged joints or push-fit joints. Jointing of large pipes of the light weight type shall be made by extruder welding.

All welding shall be performed by certified welders holding licences not older than 12 months, and issued by a recognised institution approved by the manufacturer and the Engineer.

For non-buried pipesm, mechanical couplings and fittings shall be used. The mechanical joints shall be push-on types. They shall be produced in acetal-homo-polymer or be combined with gunmetal adapters. The joints have to provide the system with strength in tension and water tightness. Push fit jointing type shall consist of a PVC grip ring and nitrite elastomers or equivalent O- ring.

The minimum diameter of the rollers for coiled pipe should be such that kinking of the pipe is prevented. The minimum internal diameter of the rollers shall not be less than 24 times the nominal outside diameter of the pipe. The ends of the pipe shall be plugged or covered.

### GRP Pipes

Glass reinforced plastic (GRP) pipes and fittings made of glass fiber reinforced polyester resin, centrifugally cast, aggregate filled shall comply with relevant standards.

GRP pipes shall be applied after formal Approval from the Engineer and the Employer, only.

The pipes shall be manufactured using a centrifugal molding technique, and all pipes shall have a resin rich inner layer of minimum 0.4 mm thickness.

Bends shall be fabricated in GRP to the same standard as the pipes.

All pipes and fittings shall have a minimum nominal stiffness of 10,000 N/ mm².

Pipes shall be joined by means of a push fit sleeve coupling comprising an EPDM rubber seal bonded inside a GRP casing. The rubber seal shall extend over the full length of the joint and shall have moulded central register with two pressure actuated lip seals either side.

Pipes shall be plain ended, shall have a smooth outer surface and shall have a constant outside diameter throughout their length thus allowing them to be cut and jointed at any position along their length without the need for any special preparation of the cut end, other that resealing the exposed fibres.

Longitudinal angular deflections at the joints shall not exceed 75 % of the maximum stated by the manufacturer.

Rocker pipes shall be incorporated adjacent to all thrust blocks.

The Contractor’s pipe laying labor will be required to demonstrate that they have attended the pipe manufacturers own training course for the installation of GRP pipes and fittings, before they are permitted to commence pipe laying activities.

### General Requirements

Pipes and fittings shall be stored, handed, laid and jointed strictly in accordance with the manufacturer’s instructions and recommendations.

Plastic pipes shall be capable of withstanding ultraviolet degradation.

The Contractor shall advise the manufacturer of the climatic and conditions at the site of the Works and shall seek his advice on the storage of plastic materials on site. Subject to the Engineer's approval this advice shall be followed at all times.

### Pipe Laying and Testing

#### Excavation of Trenches

Trenches shall be excavated to the width and depth and to the lines shown on the drawings and shall be carried out in accordance with Paragraph “Earthworks”.

#### Bedding of Pipes

The bedding of the pipes and fittings shall be carried out in accordance with Paragraph “”Earthworks”.

#### Thrust and Anchor Blocks, and Locking Joints

Thrust and anchor blocks, as specified for ductile iron pipes, shall be provided where the pipeline incorporates flexible joints or where a flexible joint e.g. mechanical coupling, is installed in a continuous, pressure pipeline adjacent to a bend, branch or blank end.

#### Surround and Protection to Pipes

##### Selected Fill Surround:

The filling to the pipeline shall be carried out in accordance with Paragraph “Earthworks”.

##### Concrete Slab Protection:

Plastic pipelines shall be protected from excessive deflections resulting from superimposed loadings, by the provision of a reinforced concrete slab, where the pipeline is laid under the following situations:

- Where the cover is less than 1 m, laid in un-paved areas not liable to live loading

- Where the cover is less than 1 m or 1 times DN, laid in or alongside roadways subject to light traffic loadings

- Where the pipeline is laid in or alongside roadways subject to heavy traffic loadings

- Where the cover is greater than 6 m, in poor ground conditions

The concrete slab shall be minimum 300 mm thick and shall bear a minimum 500 mm on the undisturbed surface at each side of the trench.

##### Concrete Bed and Surround:

Concrete bed and surround shall be provided, where required, as specified for ductile iron pipes.

##### Pipe Supports

Pipe supports shall be provided as specified for ductile iron pipes.

##### Backfilling

The remainder of the trench above the pipe surround shall be backfilled with approved selected backfill material in accordance with the Specification.

##### Testing of Non-Pressure Pipelines

Testing of non-pressure pipelines shall be carried out as specified for concrete pipes.

##### Testing of GRP Pressure Pipelines

Testing of GRP pressure pipelines shall be carried out as specified for ductile iron pipes.

##### Testing of Thermoplastic Pressure Pipelines

Testing of thermoplastic (PVC, polyethylene, etc.) pipelines shall be carried out generally as specified for ductile iron pipes, together with the procedure as detailed below to take into account of the viscoelastic (creep) response of the material. The procedure shall be as follows:

  - When the main is fully charged and all air vented the system should be allowed to stabilize before the test procedure begins

  - Pressure should be applied at a constant rate and the time tL taken from the start of pressurisation to attainment of test pressure must be recorded.

  - Readings of pressure decay at time intervals in minutes must be taken and recorded, and should be taken by the temporary installation of a pressure logging and recording device.

  - The first such reading P1 is taken at any decay time t1 equal to and greater than tL

  - The second reading P2 is taken at any decay time t2 equal to and greater than 5 × tL

  - Calculate N1 = (loge P1 - loge P2) / (loge t2 - loge t1) which should be between 0.04 and 0.12.

If N1 is greater than 0.25, then an unacceptable leak is indicated.

  - A third reading P3 is taken at any decay time t3 equal to and greater than 15 × tL

  - Calculate N2 = (loge P2 - loge P3) / (loge t3 - loge t2)

If N2 is greater than 0.25, then an unacceptable leak is indicated.

If the ratio N1 / N2 is less than 0.8, an unacceptable leak is indicated.

## Cable Conduits

The pipe material for Cable conduits shall be PVC, suitable for retraction of control cables. The work Cable conduits includes supply of pipe material diameter not less than 63 mm, pipe laying and laying of Inzlon plastic ropes 5 mm in the cable conduits, end caps and all additional work for connecting to cable shafts.

The quantity of pipes in place shall be measured as linear meters run along the centerline of the cable conduits between neighboring cable manholes without deduction for fittings. Every type of fittings shall be deemed to be included in the unit rates of the pipe laid.

Cable shaft shall be made of precast or in site concrete elements with entries for PVC pipes. Covers shall be suitable for single load of 10 tons.

## Flanges, Bolt, Nuts and Washers

The dimensions of bolts, nuts, and washers shall be in accordance with the flange dimensions.

Bolts, nuts and washers and other demountable fastenings of all galvanized parts and also aluminum alloy parts shall be in stainless steel to the appropriate standard. PTFE washers shall be fitted beneath bolt-head and washer when fastening galvanized and aluminum alloy parts.

Fastenings, except high tensile, of all ferrous parts shall be steel prepared and galvanized to or sherardized to the relevant standards, primed and painted in accordance with location.

All bolts, nuts and washers used in the jointing at flanged valves shall be of stainless steel grade 1.4571 and/or 1.4301, i.e. bold made of 1.4301 with washer and nut made of 1.4571.

Unless specifically approved and required for superior protection, electro-galvanizing, nickel, cadmium or any other plating process, except chromium plating, will not be acceptable, and shall not be offered.

## Joints

Pipe joints shall be completed in accordance to the pipe manufacturer’s recommendations after submittal of adequate Method Statements and approval of the Engineer, only.

All joints shall be accurately made and shall be capable of passing tests for individual joints and for the completed pipeline as may be specified hereafter.

### Bolted Gland Joints

Jointing of spun (asbestos cement) and cast iron spigot and socket pipe with bolted gland flexible joints shall be completed in accordance to the pipe manufacturer’s recommendations. In particular the Contractor shall ensure that after spigot has been centered in the socket the lead-tipped rubber ring is pressed into its seating between the socket and spigot and evenly tapped home with a wide faced caulking before the gland is drawn up into position. All nuts shall first be tightened by hand and nuts on opposite sides of the joint circumference shall then be alternately and progressively tightened with a spanner so as to ensure even pressure all-round the joint.

### “Push-In-Type” Joints

Jointing of cast iron spigot and socket pipes with “push-in-type” flexible joints shall be completed in accordance to the pipe manufacturers’ recommendations. In particular, the Contractor shall ensure that the spigot end of the pipe to be jointed is smooth and has been properly chamfered, that the rubber ring is correctly positioned in the socket and that the two pipes are accurately in line, before the joint is made. After the joint has been made the Contractor shall ensure by the use of a suitable feeler gauge that the rubber ring is evenly seated in its correct final position. The rubber rings and any recommended lubricant should be obtained only through the pipe suppliers.

### Flanged Joints

Jointing of spun and cast iron pipes and specials, for steel pipes, and for valves by flanges shall be completed with rubber joint rings and steel bolts and nuts, which include two washers per bolt, unless, specified otherwise.

Joint rings shall be made from 3 m thick rubber reinforced with fabric and of such width as to cover the machined face of the joint inside the bolt holes. They shall be of such physical properties as to be capable of forming permanent watertight joints against pressures up to the maximum test pressure. The use of jointing paste or grease will not be permitted. The ring may be fastened to the bolts with cotton thread. The bores of abutting pipes or fittings shall be concentric and no jointing material is to be left protruding into the bore.

All nuts shall first be tightened by hand and nuts on opposite sides of the joint circumference shall then be alternately and progressively tightened with a spanner so as to ensure even pressure all-round the joint.

### Welded Joints

Welded joints in steel pipes shall be butt-welded, carried out manually by the metal-arc process.

Only welders approved by the Engineer shall carry out welding. All bends, tees and other specials shall be prefabricated by the pipe supplier.

All parts to be welded shall have loose scale; paint and other foreign matter removed by means of a wire brush and shall be left clean and dry. All scale and slag shall be removed from each weld run when it is completed. Pipes manufactured with longitudinal or spiral welds shall be lined up before jointing so that these welds are at least 15° apart around the joint circumference.

## Fittings and Accessories – General

The nominal working pressure of valves, fittings and accessories shall be 1.0 or 1.6 bar (MPa). All valves, dismantling pieces, flexible couplings connections to pipes shall be flanged supplied with bolts, gaskets, etc.

Surface boxes, covers and other accessories shall be supplied for all valves and fittings for which manholes with access opening are not foreseen. Access openings shall be positioned directly above the valves, fittings or accessories to allow dismantling with lifting facilities.

### Tees and Wyes

Tees, crosses, couplings, Y-bends or other fittings that provide means of dividing or uniting flow in pipelines shall be factory made and shall comply with the respective standards. These fittings may be connected to pipes by welding.

For connection of all kind of valves welding neck flanges shall be applied if the nominal diameter of the pipe is greater or equal 150 mm.

Tees and wyes shall be reinforced by wrappers or collars. The design shall in all cases be submitted to the Engineer for approval.

### Bends

The pipeline shall be laid in such a way that it follows the outline of the terrain as closely as possible except where otherwise indicated on the drawings.

Changes of direction or gradient shall be made with bends, produced by the Contractor in accordance with the drawings, plans and the longitudinal sections.

Bends shall be made with R= 1.5 D.

### Dismantling Joints

All valves, fittings and accessories etc. shall be easily accessible for disassembly and reassembly. Valves, fittings and accessories etc. shall be mounted with dismantling joints or adjustable and removable joints (dismantling pieces) of an approved manufacture to permit the dismantling of the valve, fittings and accessories.

### Flexible Couplings

Jointing of plain-ended cast iron or steel pipes with flexible detachable couplings shall be completed in accordance to the coupling manufacturer’s recommendations. In particular the Contractor shall render the end of each pipe smooth so as to allow the joint sleeve to slide freely and where necessary shall re-coat the pipe ends with two coats of quick drying bituminous solution.

### Anchoring Sleeves

Anchoring sleeves shall be used whenever a ductile cast iron; steel or plastic pipe shall pass through a concrete wall of water or sludge retaining tanks.

Sleeves shall be of stainless steel grade 1.4301.

Sleeves shall be sealed on one or two sides with permanently elastic EPDM gasket elements. Seals between pipes and conduits shall be made of seal belts expanded when wrenched tightened to fill the gap and create the seal. The seal belt shall consist of EPDM reinforced with stainless steel bolts to be tightened with stainless steel nuts.

## Valves, Penstocks and Actuators

This section of the specification sets out the general requirements for standard valves, penstocks, hand-stops, headstocks, and actuators etc., required for the works.

### Valves and Penstocks - General

All valves and penstocks shall be best water works quality and suitable for use in wastewater works (as appropriate) at all temperatures up to 45 °C.

All valves shall be flanged if not specified otherwise. All flanges of the valve shall be according to relevant standards and in accordance with the required test pressure and shall satisfy the requirements stated in the standards.

The face-to-face dimensions of all flanged valves shall comply with the relevant standards.

Valve bodies shall give the information about manufacturer’s name; hydraulic test pressure; size of valve; direction of flow ‘arrow’ and applied standard (according to relevant standard).

Unless specified otherwise; all standard valves shall have flanged joints of pressure rating PN10 and shall be to a class in excess of the maximum pressure they will attain in service including any surge pressures, but all valves shall be tested to stand a working pressure of 1.5 working pressure of pipeline or 6 bars, which is greater.

Valves shall be capable of withstanding the same test pressures as the pipe on which they operate. All nuts and studs subject to vibration shall be fitted with spring washers of locking taps.

All materials shall comply with the appropriate EN-ISO Standards and shall be subject to the Engineer’s approval. All castings shall be free of blowholes and other defects.

Gate valves shall be provided with renewable seats and it shall be possible to remove the gates without removing the valve body from the pipework. Penstock gates shall be provided with renewable sealing faces. Sluice valves and butterfly valves shall be suitable for flow in either direction. Gate face rings shall be screwed into the gate or alternatively securely pegged over the full circumference.

Butterfly valves shall be installed in the pipework in such a manner that they can easily be removed from the line for dismantling and replacement of the seats, designed to give minimum leakage, unless otherwise specified.

Non-return valves shall possess high speed closing characteristics, with minimum shock on closing.  Packed glands shall be arranged for easy replacement of the packing, which shall be accessible without removal of the valve from the pipe.  Precautions shall be taken to prevent corrosion of the valve spindles in contact with the gland packing.

Each valve or penstock gate or its operating equipment shall bear an approved brass nameplate stating its function in English and in Serbian.

Valves, cocks and operating spindles that are applied for submerged operation, shall be independent of external lubrication.

Extended spindles and headstocks shall be provided where necessary and shall be provided in stainless steel.

### Spindle Operation

Unless otherwise specified, all valves shall be located and orientated in readily accessible positions with hand wheels conveniently arranged for ease of operation.

Manual operation of valves shall be clockwise. The operating gear of valves and penstock gates shall consider a maximum torque of 13 Nm and a maximum force of 25 N.

Where this requirement is impracticable or would lead to under complications, operating spindles shall be taken vertically to headstocks for manual operation.

Chain operated wheels shall not be incorporated in the arrangements. Knuckling of spindle extensions and remote operation through miter-geared linkages shall be avoided.

Tee-key operation of valves and penstocks shall only be adopted in unavoidable situations or for secondary and only occasionally used purposes such as underground main valve bypasses, air valve isolation, and minor drainage valves. Where so provided, the spindles shall be fitted with a cast iron detachable cap manufactured to and of identical shape to the valve spindle caps.

Operating and extension spindles shall be provided with suitable bearings that are rigidly held on brackets or stays. Bearings and spindles shall be suitably protected against corrosion, spindles shall be provided in stainless steel.

Where specified valves and penstocks shall be power operated by electric or pneumatic actuators, each actuator shall have local manual ‘override’ facilities. No alternative systems shall be subsequently offered.

Penstock gates and valves of 50 mm nominal bore and over shall be fitted with mechanical position indicators to show the amount that the valve or penstock gate is open or closed in relation to its full travel.

### Hand wheels

Operating hand wheels for gate valves and penstocks shall be cast iron to EN, ISO Standards pattern, materials specification and finishes set out.

All hand wheels on valves over 50 mm diameter shall be fitted with a circular inscribed brass disc with an arrow indicating English and Serbian. Plates on hand wheels for valves over 150 mm diameter shall in addition, have a simple bilingual inscription denoting the function e.g., “Inlet”.

External hand wheels shall be fitted with proprietary integral locking device to prevent operation by unauthorized persons. A padlock and chain will not be acceptable.

### Sluice Gates

All sluice gates shall be of stainless steel type Material 1.4301 to DIN 17007 or equivalent harmonized European Standards. The frame of the support of the drive mechanism shall be provided also in stainless steel.

Stainless steel sluice gates shall be provided with rubber sealing faces of high synthetic rubber. Spindles, spindle extensions and hand wheels shall be the same as for penstocks.

All anchor bolts, assembly bolts and nuts shall be of ample section to safely withstand the forces created by operation of the gate. Quantity and size of the anchor bolts shall be of stainless steel type 1.4301 in accordance with relevant standards.

### Sluice Valves

Sluice gate valves shall be of the double-flanged ductile iron wedge-gate type unless otherwise specified.

Valve spindles shall be generally of the internal non-rising type. Valve stems shall be of forged aluminum bronze, machined all over with a machine cut robust trapezoidal or square form thread, operating in a gunmetal nut.

They shall have renewable non-ferrous faces on body and wedge and a bolt-on bonnet to facilitate gate removal. Stem seals shall be of the stuffing box and gland form arranged for easy replacement of packing and shall be accessible for maintenance without removal of the valve from service.

Extension spindles, headstocks and foot brackets shall be provided where necessary.  Extended spindle installations shall include all necessary brackets, intermediate supports etc. Headstocks for non-rising spindle installations shall incorporate a valve position indicator.

All handwheels, headstocks, foot brackets and guide brackets shall be of cast iron. Fixing nuts and bolts supplied by the manufacturer shall comply with the appropriate specifications and standards. Those subject to vibration shall be fitted with spring washers or locking tabs.

All valves shall be works tested hydraulically to pressures of 25 bar, and be suitable for working at pressures of 16 bar. All valves shall be prepared and painted in accordance with the General Specification, Painting and Protective Coatings.

All sluice valves shall be subjected to works test and the manufacturer shall issue test certificates to this effect.

### Gate Valves

Gate valves provided for the works shall be of the flat-bodied type, double flanged, with cast iron bodies, and shall comply with the requirements of relevant standards. They shall be of the inside screw non-rising stem type. The direction of closing shall be clockwise.

Valve stems shall be forged aluminum bronze machined all over and have a strong trapezoidal or square formed thread, operating in a gunmetal nut. Stems in chromium steel (material no. 1.4021) will also be permitted.

Stems shall be sealed with two O-rings, arranged for easy replacement of the packing and shall be accessible for maintenance without removal of the valve from the pipeline.

All valves shall be supplied with either hand wheels or extension spindle sockets. Extension spindle sockets shall be drilled and each provided with a nut and bolt for sealing of the stem, which shall also be drilled.

Extended spindle installation shall include all necessary brackets; intermediate supports etc. and provisions shall be made for adequate lubrication.

Hand wheels shall have smooth rims and have a diameter to enable two men to operate the valve. The direction of opening and closing shall be clearly marked on the hand wheel.

### Reflux Valves

Reflux valves shall be double flanged cast iron unless otherwise specified. They shall be of the quick acting non-slam single or multi door type designed to minimize slam on closure by means of heavy gunmetal faced doors weighted as necessary and with stainless steel hinge pins. The valves shall be fitted with renewable door sealing faces that shall be positively fixed.

The flaps and external weight shall be positively and securely fixed (grub screws, pins or clamps are not acceptable). All internal fixing devices shall be of stainless steel.

All reflux valves shall be suitable for operating in the horizontal plane unless otherwise specified.

The design of the valve body shall be such that there is adequate clearance around and at the back of the door the minimize jamming by rags etc. Stops shall be provided to limit the back lift of the door and in such a position to prevent fouling by rags.

Covers shall be provided to allow ample access for cleaning and service and shall be supplied complete with tapped bosses fitted with Air release cocks.

Valves shall carry identification marks and/or plates in accordance with the relevant EN-ISO Standards.  All nuts and studs subject to vibration shall be fitted with spring washers or locking tabs.

All valves shall be prepared and painted in accordance with the general Specification, Painting and Protective Coating.

### Penstocks

Penstocks shall be manufactured of stainless steel grade 1.4301 (AISI 304) or 1.4404 (AISI 316L), as per specification, with the guides doweled and bolted to the frame.

Frames shall incorporate a rectangular or circular opening with integral spigot on the back.

The gate shall be of one piece made of stainless steel with vertical and horizontal ribs, a reinforced pocket to receive a gunmetal thrust nut, pads to receive wedges and reinforced periphery around the backside machined for non-ferrous seating faces.

Guide rails shall be of such length as to retain at least one half of the vertical heights of the slide when in the fully open position.

The manufacture and assembly shall be such as to ensure accuracy in mating the frame and door faces and tight closure while maintaining freedom of gate movement during operation and minimizing sliding wear of the sealing faces.

Unless otherwise stated each penstock shall be provided with a suitable hand-wheel of adequate diameter for the duty required, or gearing shall be supplied where necessary to ensure that the required operating force applied by hand to the rim of the wheel or geared handle does not exceed 25 kg.

Gearboxes of hand-wheels shall have cast on them the direction of closing which shall be clockwise and vandal and weatherproof clear polycarbonate tube covers shall be securely fitted to protect the threads of rising spindles. Each tube shall be clearly and permanently engraved to indicate the position of the penstock to which it is fitted.

Spindles shall have machine cut robust trapezoidal or square form threads. They shall be of bronze, running in gunmetal nuts. Extension spindle coupling shall be of the muff type and they shall be drilled and provided with a nut and bolt for securing the spindle to the penstock spindle-head, which shall likewise be drilled to receive the bolt.

Where penstocks are specifically required to be operated by tee-keys, spindle caps of the specified type shall be fitted. The caps shall be drilled and each provided with nut and bolt for securing to the spindle, which shall also be drilled.

All hand-wheels, headstocks, foot brackets and guide brackets shall be of stainless steel at least grade 1.4301. Guide brackets shall be adjustable. Fixing nuts and bolts shall be specified in the appropriate clauses herein.

Penstocks shall be structurally designed for on-seating or off-seating pressures of 5 times the maximum possible hydraulic loading, which they could be subjected to on site. Those with on-seat pressures may have side wedges only. Those with on-seat pressures may have side wedges only. Those with off-seat pressures shall incorporate top, side and bottom wedges.

Weir penstocks, where specifically required, shall be designed for on-seat pressure application and shall incorporate a removable sharp edges overflow.

### Air and Gas Relief Valves

Air and gas relief valves shall be of the double orifice pattern with grey or ductile cast iron bodies. The inlet flange shall be faced and drilled.

The valves shall be adequately sized for the release of gas from the pipeline without restriction of rate of filling or flow due to backpressure and also to allow admission of air during pipeline emptying at a rate sufficient to prevent excessive depression of pressure in the pipe.

Valves shall be designed to prevent the operating elements being in contact with the pipeline liquid by approved means such as the provision of an auxiliary float and chamber sufficiently large to isolate the orifice valves and seats throughout the rated operational range.

Air valves shall be fitted with an isolating sluice gate valve and gearing shall be provided where necessary to facilitate operation.

In applications where the pipeline characteristics may lead to liquid column separation with consequent possibility of surge, a vented non-return valve shall be provided which allows air to enter freely on separation but controls expulsion of air/gas as the liquid column re-joins.

All air and gas relief valves and associated isolating valves shall be works tested hydraulically and capable of withstanding test pressure of 25 bar and working pressures of 16 bars.

All valves and operating linkages shall be prepared and painted in accordance with the General Specification for Painting and Protective Coating.

All materials used in the manufacture of the valves shall conform to the following minimum standards:

- Float Chamber Grey Cast Iron

- Flange and Cover Grade 220 or Spheroidal Graphic Iron

- Liquid Float Copper, Polycarbonate or approved equivalent

- Air Valve Float and Guide Polycarbonate or approved equivalent

- Orifices, Guides and Mechanisms Stainless Steel

- Sealing Rings 	Molded Rubber or suitably approved equivalent.

### Butterfly Valves

Butterfly valves shall conform to relevant standards for NP 10 (i.e. 10 bar) pressure rating.

Except where otherwise specified, all butterfly valves shall be resilient seated and shall give tight closure against unbalanced water pressure in either direction. The unbalanced water pressure shall be the design pressure rating of the valve.

The valve seat shall be replaceable but may be vulcanized and be formed of rubber or other approved resilient and durable material. The valve seat shall be securely clamped into a machined groove in the valve body or to the edge of the disc by seat retention members, or other equivalent retention device, in such a manner as to prevent leakage of water under the seats and to hold the seat securely in position during opening and closing of the valve disc.

The seat retention members shall be of stainless steel shall be securely fastened to the body or disc with stainless steel fasteners.

Disc edges shall be machined with rounded corners and shall be polished to a smooth finish. The valve disc shall rotate through an angle of 90 degrees from the fully opened to the fully closed position and the seat shall be of such design as to allow the valve disc to seat at an angle normal to the axis of the pipe when the disc is in the fully closed position. The valve disc shall be made of stainless steel.

Adjustable mechanical stop shall be provided in the valve body to present over-travel of the valve disc in both the open and closed positions.

Butterfly valve spindles shall be horizontal when mounted.

The valve shaft shall be fabricated of stainless steel and may be in one piece or attached as two stub ends on opposite sides of the disc. The means of the attachment of the shaft to the disc shall be using fixings in a homogenous corrosion-resistant material of a pattern which precludes the assembly becoming loose in operational service. Grub screws, pins (parallel or taper) or clamps will not be acceptable. The shaft and disc fixing shall be capable of absorbing the full operating torque with a minimum design safety factor of five. Shaft seals, when used, shall be rubber 0-ring type. Packing shall be either rubber 0-ring or self-adjusting chevron type.

When all the seat retention members are in place, the finished edges shall fit closely and the surface shall be smooth with all fastenings set flush in the water passage so as to offer the least resistance possible to the flow of water through the valve.

Valve seats which extend over the face of the flanges to secure the seat in place, or which require surface grinding and/or hand fitting of the disc; or designs which require the adjoining pipe flange to retain the seat in place and resist line pressure, will not be acceptable.

Operating gear for butterfly valves shall be of the fully enclosed type. Valves shall be suitable for operation by one man at all pressure conditions that can apply. A valve position indicator shall be provided. Where a hand-wheel is used for operating the valve, the indicator shall be clearly visible from the hand-wheel operating position.

All butterfly valves shall be tested at the manufacturer’s works under ‘open end’ conditions. The seat test shall be for tight closure under maximum unbalanced water test pressure in either direction. Test certificate shall be provided.

The Contractor shall provide details of the materials of manufacture and design of butterfly valves (certificates), and shall provide evidence to show that the proposed seating materials and seating designs have given satisfactory performance in similar conditions to those applying under the Contract.

Valves shall carry identification marks and/or plates and those for use on process works shall carry an additional brass plate carrying valve identification and a brief description of its function.

Valves shall have 10 bar flanges and be drilled to EN, ISO Standards and shall be capable of withstanding the same pressure as the pipeline on which they operate. All nuts and studs subject to vibration shall be fitted with spring washers or locking tabs.

All materials used in manufacture of butterfly valves shall conform to the following minimum standards:

- Body and Disc - Cast Iron to Grade 220 or Spheroidal Graphite Iron.

- Shaft - Stainless Steel

- Sealing Ring & Seat – Gunmetal

- Disk valve - Stainless Steel.

All valves and shall be prepared and painted in accordance with the General Specification for Painting and Protective Coating.

### Pressure Control Valves

Pressure and flow control valves for 80 mm diameter and above used for pressure reduction, pressure sustaining or pressure relief shall be of the double flanged type and of grey or ductile cast iron and shall operate by use of an integral auxiliary actuating mechanism suitable for the application. For diameters less than 80 mm a direct spring controlled valve may be used.

The valves shall be adequately sized to control the flow and pressure differential required for the application with an accuracy of ±2.5 % of the set valve. They shall be capable of operating at a sustained pressure 20 % in excess of the nominal declared working pressure.

Valves shall be sized to ensure that their full capacity will be more than adequate to accept the desired maximum flow at the minimum required differential pressure. Flanges shall be of 10 bar design.

Where specified, an externally projecting indicator rod shall be fitted to the top of the piston to indicate the position of the main valve disc.

The main pressure control valve operation shall be actuated by a hydraulic differential pressure system in balance with a spring loaded bellows type diaphragm, the reference pressures being bled from the inlet and outlet of the main valve application.

The control circuit bleeds shall be controlled by isolating cocks to enable the system connections to be removed without disturbing the main valve.

The detail connections and application of reference pressure shall be arranged to suit the requirement, whether for pressure reduction, pressure relief to sustain a constant pressure, or regulate flows.

Monitoring orifices shall be protected by suitably fine mesh strainers on the pipeline side, the elements, strainers, pipework and fittings being in suitable corrosion-resistant materials.

A pressure gauge shall be fitted to indicate the regulated pressure. Where required a needle valve shall be incorporated in the connection from the relay valve to the main valve piston cylinder to adjust the rate of pressure.

All valves and operating gear shall be prepared and painted in accordance with the General Specification for Painting and Protective Coating.

All materials used in the manufacture of the valves shall conform with the following standards:

| - Body, Cover and disc | Cast Iron to Grade 220 or Spheroidal graphite iron. |
| --- | --- |
| - Valve guide, rings, etc. | Gunmetal |
| - Liner | Bronze |
| - Seating Face | Gunmetal, synthetic or other approved material as appropriate |
| - Indicator rod | Stainless steel |
| - Actuating valve body etc. | Bronze |
| - Spindle | Stainless steel |
| - Valve face | Nylon |
| - Diaphragm and bellows | Reinforced synthetic rubber or approved equivalent |
| - Orifice body and plate | Bronze |
| - Strainer | Copper wire cloth |
| - Spring | Spring steel. |

All detain parts not listed shall be in homogeneous corrosion-resistant material.

### Flap Valves

Flap valves shall be round or rectangular, single door bitumen coated, cast iron double hung tidal type flap valves, with the clear opening dimensions designed to pass the required discharge. Flap valves shall be fitted with phosphate or bronze or stainless steel or similar approved corrosion resistant metal faces and hinge pins and shall have a galvanized mild steel lifting eye.

Flap valves shall be designed to withstand a working pressure equivalent to 8.0 m of water.

Flanges shall be of 10 bar design.

## Manholes and Chambers

### General

Manholes and chambers shall be constructed on sewer and drain pipelines and shall be positioned at all changes in alignment and levels, and connection with existing sewers.

Generally, all manholes and chambers shall be constructed in either pre-cast or cast in situ concrete made with sulphate resistant cement, and shall be watertight.

Manholes and chambers should satisfy the relevant standard.

### Construction details

Bases for manholes and chambers shall be constructed in reinforced at least Concrete Class C20/25. Access shafts, walls, and cover slabs shall be constructed in cast-in-situ at least Concrete Class C20/25 reinforced or in precast construction using units made of Concrete Class C30/37.

Benching to manholes and chambers shall be in Concrete Class C20/25 and carefully formed to shapes and forms. The benching shall be sloped towards the channel at a gradient of 1 in 20.

Valves and other accessories shall be seated, embedded and anchored to concrete plinths cast in Concrete Class C20/25 to shapes and forms as necessary.

All pipes entering and leaving manholes and chambers shall be laid soffit to soffit unless otherwise specified.

### Manhole Accessories

Manholes and chambers shall be provided with heavy duty manhole covers having clear openings of 750 mm by 750 mm for pipes 1200 mm internal diameter and above and clear opening of 600 mm diameter for pipes of internal diameter below 1200 mm unless specified otherwise.

Manhole covers and frames shall be constructed flush with the final ground level on roads and pavements, but they shall be 75 mm above final ground level elsewhere.

## Bricks

Bricks for manhole chambers and brickwork below ground level shall be according to the relevant standards for massive clay bricks and radial clay bricks. Sample of all bricks intended for use in the Works shall be submitted to the Engineer for approval. Bricks incorporated in the Works shall be at least equal in quality to the approved samples.