LOT 2

VOLUME 3

SECTION 2C

GENERAL TECHNICAL SPECIFICATIONS FOR ELECTRICAL WORKS

LOT 2: GENERAL TECHNICAL SPECIFICATIONS

FOR ELECTRICAL WORKS

1	GENERAL DATA	9

1.1	Introduction	9

1.2	Objective of the Works	9

2	GENERAL TECHNICAL REQUIREMENTS	10

2.1	Regulations and Standards	10

2.1.1	Conditions for Electricity Equipment	10

2.1.2	Quality Assurance / Quality Control	10

2.2	Design and Construction	11

2.3	Equipment selection	11

2.3.1	Interchangeability	11

2.4	Conservation	12

2.4.1	Painting	12

2.4.2	Use of Metals	12

2.4.3	Use of Wood	12

3	GENERAL ELECTRICAL REQUIREMENTS	13

3.1	General	13

3.2	Polarity	13

3.3	Voltages and Frequencies	13

3.4	Wiring	13

3.5	Electrical Safety	14

3.6	Design and Construction of switchgear panels	14

3.7	Panels	14

3.8	Electrical Motors	14

3.9	Switchboard Construction	16

3.9.1	Safety	16

3.9.2	General Construction	16

3.9.3	Section Labels	17

3.9.4	Earthing	17

3.9.5	Earthing of MV Circuit	17

3.9.6	Outdoor locations	17

3.9.7	Switchboard Wiring	18

3.9.8	Switchboard Busbars and Primary Connections	18

3.10	Switchboard Components	19

3.10.1	Indicating Instruments and Meters	19

3.10.1.1	Digital Indicators	19

3.10.1.2	Meter Relays	19

3.10.2	Indicator Lamps	19

3.10.3	Labels	19

3.10.4	Push Buttons	20

3.10.5	Terminal Blocks	20

3.10.6	Test Terminal Blocks	20

3.10.7	Time Relays	20

3.10.8	Fused-switches and Disconnecter Combination Devices	20

3.10.9	Fuses and Links	21

3.10.10	Control, Auxiliary, and Selector Switches	21

3.10.10.1	Discrepancy Switches	21

3.10.11	Switchboard Ancillary Equipment	21

3.10.12	Voltage Transformers	21

3.10.13	Current Transformers	22

3.10.14	Control Transformers	22

3.10.15	Circuit Breakers	22

3.10.16	Low Voltage Auxiliaries for power switch board	23

3.10.17	Relays	23

3.10.18	Control and Interposing Relays	23

3.10.19	Anti-Condensation Heaters	23

3.11	Protective Relays	24

3.11.1	Overcurrent and Earth Fault Protection	24

3.11.2	Under and Over-voltage Relays	24

3.11.3	DC Trip Relays	24

3.11.4	Motor Thermal Relays	24

3.12	Motor Starters	24

3.12.1	Individual Starters	25

3.12.2	DOL Motor Starters	25

3.12.3	Current Reducing Motor Starters	26

3.12.4	VSD Starters	26

3.12.5	Frequency converters	26

3.12.6	Motor Starters – High Voltage	27

3.12.7	Actuator Starters	27

3.13	Circuit Breakers	28

3.13.1	High Voltage Circuit Breakers	28

3.13.2	Low Voltage Circuit Breakers	29

3.13.3	Moulded Case Circuit Breakers	29

3.13.4	Miniature Circuit Breakers	30

3.13.5	Residual Current Circuit Breakers	30

3.14	Control Distribution	30

3.14.1	Local Control Stations and Control Boxes	30

3.14.2	Marshalling Boxes	31

3.15	Power Transformers	31

3.15.1	Insulators and Bushings	31

3.15.2	Insulating Oil	32

3.15.3	Transformer Tanks Enclosures	32

3.15.3.1	Oil Filled Transformers	32

3.15.4	Main Terminal Connections	32

3.16	Earthing	32

3.16.1	Submissions by the Contractor	32

3.16.2	Installation	33

3.16.3	Conductors	33

3.16.4	Earth Electrodes	34

3.16.5	Main Earth Bar	34

3.16.6	Tests at Site	34

3.17	Lightning Protection	34

3.17.1	Conductors	34

3.17.2	Lightning Protection Devices for Plants	35

3.17.3	Lightning Protection for Control and Instrumentation	35

3.18	Cables and Wires	36

3.18.1	Cable Types	36

3.18.1.1	High Voltage Power Cables	36

3.18.1.2	Medium/Low Voltage Power Cables	36

3.18.1.3	Submersible Borehole Pump Cables (Low voltage)	37

3.18.1.4	Flexible Cables and Cords	37

3.18.1.5	Instrumentation and Control Cables	37

3.18.1.6	Fiber optic cables	38

3.18.2	Cable Labeling	38

3.19	Cable Installation	38

3.19.1	Submissions by the Contractor	39

3.19.2	Installation Direct in the Ground	39

3.19.3	Installation in Underground Ducts	40

3.19.4	Sealing Cable Entries into Buildings	40

3.19.5	Marking of Underground Cables	40

3.19.6	Installation in Cable (Bus) Trunking	41

3.19.7	Installation in Troughs and Trenches	41

3.19.8	Cable Trays and Ladders	41

3.19.9	Installation in Buildings	42

3.20	Cable Installation in Conduits	42

3.20.1	Surface Installation	42

3.20.2	Concealed Installation	43

3.20.3	Flexible Conduits	43

3.20.4	PVC Conduits	43

3.21	Cable Terminations and Joints	44

3.21.1	Power Cable Terminations	44

3.21.2	Multicore or Control Cable Terminations	44

3.21.3	Fiber Optic Cable Termination Boxes	45

3.21.4	Joints	45

3.22	Small Power and Lighting Installations	45

3.22.1	Distribution Boards	45

3.22.2	Bulk Switching Contactors	46

3.22.3	Socket Outlets	46

3.22.4	Lighting Switches	46

3.22.5	Internal Lighting	46

3.23	Types of Luminaries	46

3.23.1	LED	46

3.23.2	External Luminaries	47

3.23.3	Emergency Lighting	47

3.24	Lamps	47

3.24.1	LED Lamps	47

3.24.2	Low and Extra Low Voltage Supply Transformers	47

3.24.3	Electric Hand-lamps	47

3.25	Batteries and Chargers	47

3.25.1	Batteries	47

3.25.2	Battery Charger	48

3.26	Generator Sets	48

3.26.1	Engine Control	48

3.26.2	Emergency Power Generation	50

3.26.3	Preliminary Check, Service and Test Running	51

3.26.4	Stripping Down Checking and Scheduling of Overhaul Works	51

3.26.5	Reconditioning/Overhaul	52

3.27	Power Factor Correction Capacitors	52

3.28	Cathodic Protection	52

3.28.1	General	52

3.28.2	Installation of Control-measuring Outputs	52

3.28.3	Cathodic Protection Station	53

3.28.4	Anode Bearing	53

3.29	Video Surveillance	54

3.29.1	General	54

3.29.2	Technical Specification	54

3.30	Fire Alarm System (FAS)	55

3.30.1	General	55

3.30.2	Technical specification for Installations	56

3.31	Access Control System with Time Attendance System	56

3.32	Public Address System	57

3.33	Intercom System	57

3.34	Gas Detection System	58

3.34.1	General	58

3.34.2	Technical specification for Installations	58

3.35	Structured Cable Network System	59

3.35.1	General	59

3.35.2	Technical Specification for distribution cabinet	59

4	GENERAL INSTRUMENTATION REQUIREMENTS	60

4.1	Design	60

4.1.1	Central Control System	60

4.1.2	Panel Mounted Instruments	60

4.1.3	Local Instruments and Controllers	60

4.1.4	Pressure and Differential Pressure Transmitters	60

4.1.5	Instrument Connections	61

4.1.6	Instrument Protection	61

4.1.7	Safety Design	61

4.1.8	Marking / Labeling	61

4.1.9	Water Meters	61

4.2	Flow Instruments	61

4.2.1	Electromagnetic Flowmeters	61

4.2.2	Ultra-Sonic Clamp-On Flowmeter	62

4.2.3	Flow Switches	63

4.3	Level Instruments	63

4.3.1	Type of Level Control	63

4.3.2	Pressure Transducer Level Measuring Equipment	63

4.3.3	Pressure Transducer Installation	64

4.3.4	Ultrasonic Level Measuring Equipment	64

4.3.5	Installation of Ultra–Sonic Level Equipment	65

4.3.6	Electrode Level Control Equipment	65

4.3.7	Float Switches	66

4.4	Pressure Instruments	66

4.4.1	Pressure and Compound Gauges	66

4.4.2	Pressure Switches	67

4.5	Temperature Instruments	67

4.5.1	Thermowells	67

4.5.2	Thermocouples	67

4.5.3	Temperature Transmitter and Controller	67

4.6	Process Analytic Instruments	67

4.6.1	Field mounted instruments	67

4.6.2	Samplers	68

4.7	Control Valves	68

4.7.1	Sizing Base	68

4.7.2	Body Material	68

4.7.3	Valve Types	69

4.7.4	Valve Trim	69

4.7.5	Packing Gland	69

4.7.6	Valve Actuators	69

4.7.7	Handwheel	69

4.7.8	Valve Positioner	69

4.7.9	Safety and Relief Valves	69

4.8	Instrumentation Air Supply Piping and Tubes	69

4.8.1	Air Supply	69

4.8.2	Signal Tubing	70

5	GENERAL SCADA REQUIREMENTS	71

5.1	Functional Design Specification	71

5.2	System Overview	71

5.3	Dispatcher System Hardware	72

5.4	System Availability	72

5.4.1	Uninterruptible Power Supply (UPS)	72

5.4.2	Maintenance	73

5.5	Communications Equipment	73

5.6	Data Storage	73

5.7	Workstations	73

5.8	Printing Devices	73

5.8.1	Colour Printer	73

5.9	Remote Data Transfer	74

5.10	System Features	74

5.10.1	System Access	74

5.11	Colour Graphics Displays	74

5.11.1	Mimic Displays	74

5.11.2	Display of Variables	75

5.11.3	Display Attributes	75

5.11.4	Picture Creation	76

5.11.5	Help Pages	76

5.11.6	Graphs	76

5.11.7	Bar Charts	76

5.11.8	Alarm and Event Log Listings	76

5.11.9	System Set-up and Maintenance Displays	77

5.11.10	Logging On/Off	77

5.12	Alarm Facilities	77

5.12.1	Alarm Priorities	77

5.12.2	Alarm Annunciation	77

5.12.3	Alarms Filtering	78

5.12.4	Derived Alarms	78

5.13	Historic Information	78

5.13.1	PLCs	78

5.13.2	Master station	78

5.14	Controls	78

5.14.1	Manual Control	78

5.14.2	Automatic Controls	78

5.14.3	Terminal Time-out	79

5.15	System Record	79

5.16	Report Generation	79

5.17	System Time	79

5.18	System Database Configuration	80

5.19	PLC Equipment	80

5.19.1	Power Supply Requirements	81

5.19.2	Input/Output Requirements	81

5.19.2.1	Digital Input Requirements	81

5.19.2.2	Digital Output Requirements	81

5.19.2.3	Analogue Input Requirements	82

5.19.2.4	Analogue Output Requirements	82

5.19.3	Communication Ports	82

5.19.4	Protocols	82

5.19.5	High Speed Pulse Counter	82

5.20	Communications	82

5.20.1	Scan Times	82

5.20.2	Transmission and Protocol	82

5.20.3	Electronic Equipment	83

5.21	Testing	83

5.21.1	Factory Acceptance Test	83

5.21.1.1	SCADA Database Configuration	83

5.21.1.2	Picture Configuration	84

5.21.1.3	Data Collection	84

5.21.1.4	Supervisory Control	84

5.21.1.5	Alarm/Event Handling	84

5.21.1.6	Data Logging	85

5.21.1.7	PLC Programming	85

5.21.1.8	Management Information System Development	85

5.21.1.9	Factory Acceptance Test - Witnessing	85

5.21.1.10	Factory Acceptance Test Procedures	85

5.21.1.11	Factory Acceptance Test – Records	86

5.21.1.12	Failure and Re-test	86

5.21.2	Site Acceptance Tests	86

5.21.3	Systems Acceptance Tests	86

5.22	Training	87

5.22.1.1	System Operators	87

5.22.2	Systems Administrators /Programmers/Engineers	87

5.22.3	Site Training	88

5.23	Operations & Maintenance Documentation	88

5.23.1	Full System Operating Procedures (six Copies)	88

5.23.2	Full Software Documentation (six Copies)	89

5.23.3	PLC Programming Documentation (one Copy)	89

5.24	System Recovery	89

5.25	Consumables	89

5.26	Spares and Test Equipment	89

6	GENERAL TESTING REQUIREMENTS	90

6.1	Testing and Inspection	90

6.2	Electrical design meetings	90

6.3	Tests Generally	90

6.4	Testing for the equipment and materials	90

6.4.1	Electrical Switchgear and M.C.C.’s	91

6.4.2	Inspection on Delivery and During Installation	91

6.5	Tests on Completion	91

6.5.1	Damages for Failure to pass Tests on Completion	92

6.6	Test Instruments	92

6.7	Control/Switchgear Panels	92

6.7.1	Low Voltage Devices	92

6.7.2	High Voltage Devices, if needed	92

6.7.3	Switchboards and Motor Control Centers	93

6.7.4	Instrument and metering equipment	93

6.8	Transformers	94

6.9	Cable Tests during Installation	94

6.9.1	High voltage cables if needed	94

6.9.2	LV cables 600/1000 V	94

6.10	Electrical Measuring Instruments and Meters	95

6.11	Programmable Logical Controller (PLC)	95

6.12	Test Period	95

- GENERAL DATA

  - Introduction

These Specifications are to be read in conjunction with the rest of Volume 3 and in particular with the Employer’s Requirements.

  - Objective of the Works

The main objective of this Contract is design and construction of the Transfer Station Vrbas and of the Transfer Station Bačka Palanka, including Civic Amenity Site (CAS) and sorting line, at both locations, in order to contibute to establishing a long-term sustainable regional waste management system.

# GENERAL TECHNICAL REQUIREMENTS

## Regulations and Standards

The installation shall comply with all relevant statutory regulations and standards (with up to date amendments) current for design, fabrication, inspection and testing at the date of tender, unless otherwise indicated within this Specification. In general, the following shall be applied:

- Project country standards (SRPS)

- EU regulation and standards (EN)

- International Electrotechnical Commission (IEC) recommendation

If no standard is specified, the relevant International standard or, in the absence of such standard, the DIN, VDE or British Standard shall be applied.

Regarding safety measures the Project country standards and regulations shall be applied, if they are not harmonized with above listed standards.

Contractor shall supply the Engineer with one set in English of latest version of all standards, norms and recommendations relevant to the equipment and works subject of this Tender.

### Conditions for Electricity Equipment

The designed electrical equipment shall be in harmony with European norms; such as all new electrical installations shall be designed according to relevant European publications, especially:

- EN 61439-1 for design of Switchboards (maximum 1 kV)

- EN 61439-3 for design of Switchboards (maximum 1 kV)

- EN 60204-1 Electrical Equipment of machines (maximum 1 kV)

- IEC 60364 series for building installation or according to local laws, regulation and norms.

- European norm EN 60292 Safety of machinery-Principles for risk assessment.

- CE marking of all electrical equipment.

- Project Country Electrical Standards

Any particular requirements of the Project country standards shall take precedence to any other standards.

### Quality Assurance / Quality Control

The Contractor shall carry out control procedures according to the Quality Assurance Specifications and General Testing, Inspection and Pre-Commissioning Requirements

The Contractor shall furthermore perform tests for all switch and control boards. The tests shall include but not necessarily be limited to Test according to EN 61439-1, EN 61439-3 and EN604-1:

- Test of outputs

- Test of inputs

- Test of operator keys and functional switch - Test of displays/lamps/instruments/push-buttons

- Test of insensitiveness to voltage variations

- Functional test of complete control monitoring

- Lifetime-test (supply voltage, 400/220 V at 24 hours at maximal ambient temperature, 40oC) - Visual control.

## Design and Construction

The Works shall be designed in all respects to conform to the latest current engineering practice.

The philosophy of the design shall be simplicity and reliability such that the equipment will give long trouble–free service with low maintenance costs. Particular attention should be paid to ease of access to facilitate inspection, cleaning, maintenance and repair.

All equipment supplied shall be designed to meet the needs for satisfactory operation under all variations of operating loads, pressures and temperatures including variation in the ambient temperature.

All materials shall be new and of the best quality and shall be selected to withstand the stresses imposed by the working and the ambient conditions without distortion or deterioration affecting the efficiency and reliability of the plant.

It shall be the responsibility of the Contractor to ensure that the electrical equipment is completely satisfactory for use with the mechanical equipment offered.

Each component or assembly shall have been proven in service in a similar application and under conditions no less arduous than those specified herein.  The Engineer shall have the right to request the Contractor to justify his selection of equipment.  Where it is shown that material or plant are of a standard lower than that necessary to comply with the Specification, the Contractor shall modify or replace the equipment concerned at no extra cost.

The choice of materials and finishes shall take into account the atmospheric conditions at the Site.  Equipment shall be protected against the entry of vermin, insects or small animals.

Outdoor equipment shall be weatherproof and designed to prevent the collection of water at any point.

Mechanisms shall be constructed of materials, which will not jam due to rust, corrosion, brine or dust.  Bearings of exposed operating shafts shall be designed to prevent moisture seeping along the shaft into the interior of the equipment.

Equipment and instruments shall not be located in positions where they are vulnerable to falling objects or water drips. Weather shields shall be provided where necessary to protect equipment, instruments and cabling against weather conditions and direct sunlight. Outdoor located electrical box/cubicle or instrument shall not be facet to the South.

## Equipment selection

The equipment is to be selected taking into account the application field, its reliability and viability and the environment where it is to be installed. The equipment shall be designed and installed as such that failure of a component should not cause damage or the occurrence of dangerous situations.

### Interchangeability

All equipment performing similar duties shall be of a single type and make and fully interchangeable in order to limit the stock of spare parts required.  This is to apply particularly to such items as motors, switchgear, instruments, controls, valves and relays.

## Conservation

### Painting

All non-RVS metal parts shall be suitably protected against corrosion. Protective coatings shall be applied at the place of manufacture and before installation of internal fittings. A final coat of heavy duty finishing paint shall cover the whole of the external part of the equipment.

Materials and painting process shall be specified in consideration of the circumstances. The painting color shall be as manufacturer's standard.

### Use of Metals

Iron and steel members shall be painted or galvanized. Small iron and steel parts (other than stainless steel) the cores of electromagnets and the metal parts of relays and mechanisms are to be treated in an approved manner to prevent rusting. Cores, etc., which are built up of laminations or cannot for any other reason be antitrust treated are to have all exposed parts cleaned and heavily enameled or lacquered. The use of iron and steel shall be avoided in instruments and electrical relays wherever possible.

When it is necessary to use dissimilar metals in contact, these should be selected so that the electrochemical potential difference is not greater than 250 mV. Where practicable the two metals are to be insulated from each other by an approved insulating material or by a coating of an approved varnish compound.

Steel screws when used are to be hot-dip galvanized. Sanitary fixtures are to be chromium plated. Springs are to be of brass, bronze or non–rusting material (under conditions of atmosphere on the place of apply). Pivots for which non–ferrous material is unsuitable shall be of approved corrosion resisting steel.

### Use of Wood

The use of wood is to be avoided as far as possible. When used it shall be of approved type to resist termite attack and fungal decay.

# GENERAL ELECTRICAL REQUIREMENTS

## General

The electrical works provided comprises of the supply of electric equipment and necessary instruments and electro-mechanical devices to operate the pumps, screens, etc. at the RWMC. All mechanical and electrical equipment installed shall be equipped with own monitoring and control equipment, MCC’s, switch panels, etc.

The equipment shall be connected with a PLC which will be connected to the SCADA system provided. The control systems shall provide for local manual and automatic loop control operation, where it is applicable, and operation through the SCADA system.

Direct connections to the power supply network shall be provided by the Contractor with a maximum of two connections.

## Polarity

The polarity of all electrical apparatus used for the Works specified shall be arranged as follows:

for two pole apparatus the phase of 'live' pole at the left hand side and the neutral on right hand side and 'earthed' pole at the bottom and top, for three or four pole apparatus the phases in order L1, L2, L3 and neutral reading from the left to right in the case of horizontal lay outs respectively and as viewed from the front.

Phase colors and sequence shall be to project country regulations. All cable cores shall be identified with phase references.

All cables shall be connected between main switchboards, distribution boards, plant and accessories so that the correct sequence or phase colors is preserved throughout the system. All non flexible cable cores shall be identified with phase colors for three and four wire circuits.

## Voltages and Frequencies

Unless otherwise indicated, all apparatus and wiring shall be suitable for use with a 3 phase, 4(5) wire, 400/230 Vac, 50 Hz, earth and neutral supply.

Supplies for control, tripping, alarm and indication circuits shall be 24 Vdc. Circuit breaker spring charging motors can operate on 230 Vac, with spring capacity for ultimate disconnecting operation.

Tap changer motors and electrical panel heating and lighting shall operate at 230V, single phase.

All references to voltages shall relate to the nominal or rated value of the supply.

## Wiring

Small wiring shall have a cross section of not less than:

2.5 mm² for CT secondary circuits, socket outlet circuits and circuit connected to current transformers,

1.5 mm² for control, indication, lighting, fixed apparatus and other circuits.

Wiring shall be self-extinguishable, minimal 1000V grade, according to EN 60695 2-11. Wiring shall be suitably labeled at each end so that any checks made on wiring can be carried out easily.

Internal wiring shall be carried installed in surface run conduit or trunking and shall be fixed to walls, ceilings or structured steelwork.

No conduit serving a single phase socket outlet, lighting point or switch shall contain more than one supply phase.

## Electrical Safety

The Contractor shall be responsible for the electrical safety of all equipment supplied and installed. Whilst any equipment is being installed or tested, the Contractor shall ensure that all necessary precautions are taken to safeguard personnel working on site. If necessary, this shall include erecting warning notices and fencing off areas which are considered to pose a risk. The Contractor shall be responsible for ensuring that the electrical installation is carried out by competent personnel and that the work is carried out in accordance with standard procedures and test requirements. Before any piece of apparatus is energized it shall be thoroughly examined for the presence of dirt, water or other foreign bodies.

All devices shall be controlled and operated from the local control panels or boxes for the maintenance duty only, with lockable local/remote selector switch. Emergency stop push buttons shall be provided for all motors as specified in SRPS EN 418:1997 and SRPS EN 1050:2005.

Where 230Vac lighting and heating is used within a panel which otherwise contains equipment with a nominal operating voltage of 24Vdc, the 230Vac equipment shall be insulated, sheathed and protected in accordance with standard practice for installing such equipment in buildings. No live terminals shall be accessible without the use of tools, no single-insulated wires shall be used, and no 230Vac cables shall share cable trays or other routes with 24Vdc circuits.

## Design and Construction of switchgear panels

The switchgear shall be of the indoor and outdoor type, how it is applicable. The panel shall be metal enclosed according to IEC 60298. The functions for circuit-breaker, current transformer and LV cable connection, busbar, shall be arranged inside different compartments segregated by metallic or insulating partitions.

The modular design shall enable any alteration or extension of the switchboard on either side.

## Panels

The switchgear shall consist of separate panels holding a fixed circuit breaker, load break and fuse combination and shall form an extensible metal enclosed switchboard. The panels shall be suitable for floor mounting.

The switchboard shall comply with safety of operation ensured by a combination of electrical and mechanical interlocks.

The panels shall be designed in such a way as to prevent access to any live part during service, as well as during maintenance operation. The panels which form part of the switchboard shall be mounted on a simple concrete floor with or without covered trenches according to the cable cross-section and type.

Any material which constitutes the enclosures which departs from the IEC standards shall be rejected. The command of all necessary devices for usual operation has to be from the front of the panel.

Distribution cabinets shall be equipped with a multifunctional network analyzer (measurement of voltage, current, frequency, distortion, etc.) mounted in the upper part of the front panel.

## Electrical Motors

Motors shall be three phase squirrel cage induction type. They shall be capable of withstanding without damage an overload equivalent to 150% of full load torque for 15 seconds. The motor rating shall be not less than 105% of the maximum power demand of the driven machine when operating in its normal range. For motors above 15kW, the cosfi power factor shall not be below 0.85. According to the energy conservation law, motors shall be of IE3 class or at least IE2, but controlled via frequency converters.

Care must be taken in selecting the type of motor starters in relation to the starting characteristics of the driven load. Although a DOL starter may be suitable in respect of starting current limitations, the starting torque may be insufficient and a variable speed motor drive could be required. The some is applicable for the other process required duty.

Conversely, where a mechanical overload device is applied, it may be necessary to limit the starting torque of the motor thus ensuring the overload device can be set to give maximum protection to the machine.

All motors shall be suitable for operation at 400 Vac, 3 phases, 50 Hz supply and shall comply with EN or IEC Standards.

Motors for indoor use shall conform to a degree of enclosure protection not less than IP54, for outdoor use not less than IP55, and motors for submersible pumps shall conform to a degree of protection not less than IP68.

All motors, exclusive submersible pumps, shall be suitable for operation in the site climatic conditions and at ambient temperature up to 40°C without reducing of performances.

Bearings shall have a minimum rated life of 6 years (50,000 hours) and have provisions for adequate lubrication. The bearing caps on the non–drive end covers of the motors shall be arranged so as to allow a speed check to be taken.

The motor terminal box shall allow adequate clearance for an air termination of the specified cable, cable lugs and glands.

A motor rating plate shall be fitted to every motor giving the following information:

- manufacturer's name

- motor type and serial number

- power rating at ambient temperature 40°C and declared starting mode

- current, voltage and winding connection

- supply frequency

- duty power factor

- duty speed

- class of insulation

- IP rating

- maximum number of starts per hour / motor duty

Motors shall be S4 duty type and capable of a minimum number of 15 starts per hour unless specifically detailed elsewhere in the appropriate section of the Specification.

Motor insulation shall be rated to thermal class F, but temperature rise shall not exceed the limits of class B.

The motors shall be commercially silent in operation and run free from vibration. The rotors shall be balanced both statically and dynamically and shall be tested and adjusted for dynamic balance both in an approved manner.

All motors shall be provided with a frame earth terminal of sufficient size to take full fault current.

All motors rated at 15 kW or greater shall incorporate winding temperature protection embedded in the stator windings. The temperature detectors shall be wired to a connection box mounted on the motor frame. The box shall incorporate over-voltage protection devices.

The same is applicable for all motors with VSD Starters and submersible pumps, but starting from 5 kW motor rated power.

All motor rotating parts together with their couplings shall either be enclosed within the motor frame or be fitted with guards, removable only by the use of tools, to prevent accidental contact.

## Switchboard Construction

This section shall apply to the construction of all panels housing electrical apparatus, including but not limited to: switchboards; motor control centres; circuit breakers; control panels; monitoring or supervising panels; distribution boards - control panels; marshalling panels; interface panels; local control panels.

LV switchboards and Motor Control Centres shall as far as possible be control centres manufactured by a single approved supplier and the construction of each individual panel shall be such that all components shall be selected in accordance with the applicable standard.

### Safety

Access to any enclosure or compartment shall be possible only:

- when the circuit switch-disconnecter is open and connections within the compartment are isolated or;

- when connections within the compartment including any on the door or access cover, are fully shrouded to prevent accidental contact or

- when connections within the compartment operate at a save voltage not greater than 55 volts.

Where a test facility is provided for use with the door or cover open the provisions of (2) shall apply.  Connections which may be live with the door or cover open shall be suitably labeled.

Bolted covers on compartments incorporating live connections shall bear a suitable warning label.

Labeled isolators, fuses or links shall be provided so that relays, controls and instruments may be isolated but keep other essential circuits energized.

### General Construction

Switchboards for electrical equipment shall be constructed in sheet steel not less than 2.0 mm thick and suitably braced to form a rigid structure. Exterior edges and corners shall be rounded and the use of externally visible assembly bolts or similar shall be avoided. The design shall provide protection against dust, damp and entry of vermin. Gaskets shall be fitted to doors and removable panels. Ventilation and cooling shall be by forced air circulation.

Unless specified otherwise switchboards shall be floor-standing with lockable hinged front doors and bolted removable rear panels for access to live equipment such as busbars and terminals.

Each section shall be separately accessible without disturbance to other sections for maintenance and inspection. Live parts with voltages greater than 55V to earth within the section shall be fitted with insulating barriers to prevent accidental contact by personnel. Parts still live when the unit is isolated shall be labeled "Danger Live". Where integral fuse or MCB distribution boards are incorporated, access to fuse carriers and MCB's shall be possible without isolating the fuse or MCB distribution board. With the operator's door open and with fuses and MCB's in place, the degree of protection of such distribution boards shall be not less than IP 20.

Lifting eyeholes shall be provided at each top corner of each section of the switchboard and shall be removed and replaced with blanking bolts after installation.

A clear access of not less than 1.00m shall be given at both ends of the panel.

Enclosures shall be constructed with protection ratings of at least IP65 for outdoor installation and IP 54 for indoor installation.

Switchboard construction shall be capable of withstanding without damage the fault current of the system.

Switchboards shall additionally have 2 No. 16 A, 230 V ac RCCB protected sockets.

Switchboards shall not rely on any removable portion for their rigidity.

### Section Labels

Each section or cubicle of the board shall be clearly labeled with a label of a suitable size (minimum letter size 8mm) which shall clearly indicate the circuit name and number, the reference number and the function of the section.

### Earthing

Cubicles and enclosures shall be earthed. Where a number of cubicles are bolted together, earthing shall be provided via a continuous high conductivity copper bar running the length of the switchboard. The cross section of this copper bus shall be designed to withstand the rated short circuit current of the switchgear for one second, in compliance with IEC 62271.

Terminals shall be provided for the connection of earthing from the metal cladding or armouring of incoming and outgoing cables. At each end of the bar there shall be a facility for connections to the main station earth and to future extension. The bar shall be fault rated at not less than that of the associated equipment. Warning labels and instructions for earthing and isolating shall be fitted in each switch compartment.

Front access doors shall open not less than 90 and shall be fitted with a locking handle and non-ferrous lift-off hinges which shall be captive when the door is closed. Locking combinations requiring different keys shall be approved before manufacture. The door shall be secured by captive screws or locking handles of sufficient number to ensure firm pressure on the door seal around the whole periphery. The door shall be mechanically prevented from opening before isolation of the live parts within. All doors shall be separately earthed to the main frame. Earthing via the door hinge will not be accepted.

### Earthing of MV Circuit

Provision shall be made for the earthing of cables, preferably by means of an integral earthing switch of the quick make type, able to earth the cables when the circuit is in the disconnected position. In order to shorten maintenance periods, it shall be possible to earth simultaneously the different feeders.

The earthing switch shall be operated from the front of the switchboard and be independent of the action of the operator. Padlocking facilities shall be fitted to enable the earthing switch to be locked in both positions. The position of the integral earthing shall be clearly visible from the front of the switchboard. Mechanical interlocks shall be provided to avoid any malicious operation such as:

- Closing of earthing switch if the circuit is in the service position;

- Inserting or closing of the circuit if the earthing switch is in closed position.

A capacity divider shall be fitted near the earthing switch. It shall be connected to a neon bulb indicator of the potential tester located in the front of the panel.

### Outdoor locations

Cubicles and enclosures for outdoor locations shall be fitted with lockable doors and a housing so designed that all controls, instruments and such like are front mounted and the whole assembly is weatherproof and vandal proof. The doors shall be fitted with stays to prevent overstraining of the hinge fixing, and allow fixing of the doors in the open position.

### Switchboard Wiring

The conductors shall be stranded or flexible (where applicable): solid cores will not be accepted.

Wiring within the switchboard shall be marked at each end for identification. The letters and numbers used shall correspond with the switchboard wiring diagram.

The wiring shall be contained within purpose designed plastic trunking and arranged so that access to equipment is not impeded. The ratio of effective cross-sectional area of the cables in the trunking shall be not greater than 40% of the trunking area. Where wiring passes through metalwork the access hole shall be fitted with a suitable grommet.

Wiring between panel sections shall be terminated on terminal blocks at each end. Wiring onto hinged doors or plates which are subject to movement shall be run in flexible circular section trunking and shall be supported securely at both ends of the moving section.

Crimped flat blades shall be applied to all wire ends to ensure sound connection to terminal blocks and all circuit components.

Wiring used for control, extra low voltage and instrument signals which are likely to be affected by interference shall be screened and/or spaced from each other and power cables to ensure no distortion or malicious operation.

### Switchboard Busbars and Primary Connections

All busbars and primary connections shall be of high conductivity copper and comply with the latest Standards. The mechanical and dielectric strengths of busbars and connection supports shall be able to withstand without damage the worst conditions of electrical surge which can occur on the installation. The busbars shall be capable of carrying full rated current continuously without exceeding temperature rise limits to the latest Standards.

The busbars, assemblies and connections of equipment shall be of a type which does not rely solely on air for insulation purposes. The covering material shall be non-deteriorating at the rated short-time maximum temperature of the busbars and shall have such thickness as is required to withstand rated line to line voltage between busbar and a conducting object on the exterior of the covering material for a period of not less than 60 seconds.

Where independent certification of busbar withstands and continuous rating is not available the Contractor shall include tests to demonstrate the suitability of the equipment.

Busbars and primary connections shall be housed in an air insulated enclosure segregated by barriers. Direct access to live bars shall not be possible. Access to busbars and connections shall be only by removal of bolted covers. Suitable warning labels shall be provided externally on covers and internally on shutters. Busbars shall be identified by colored banks opened at not more than 1000mm and in each compartment.

Baffles shall be provided to prevent the accidental entry of tools, etc. whilst maintenance work is being carried out in the vicinity of the chambers.

Busbar systems shall have a short time rating not less than that of the associated switchgear. Busbars shall be extensible at both ends.

The conductors shall be separated and supported with the appropriate clearances in air or shall be otherwise adequately insulated or encapsulated. According to the required insulation level, either heat shrinkable insulating tubing or insulated busbar are acceptable provided that they comply with the relevant IEC requirements regarding heating effects of the busbars.

Provision shall be made to allow for thermal expansion of the conductors due to the normal load and short circuit currents.

## Switchboard Components

This section shall apply to components used in all panels housing electrical apparatus, including but not limited to: switchboards; motor control centres; circuit breakers; control panels; monitoring or supervisory panels; distribution boards; marshalling panels; interface panels; local control panels.

Flash mounted components shall be front side protection not less than IP54, for outdoor use not less than IP55.

### Indicating Instruments and Meters

All instruments and meters shall be flush mounted and of the same pattern and appearance throughout. They shall be back connected and be similarly protected to maintain the environmental protection standard of the equipment enclosure on which they are mounted. Those which perform similar duties shall be of uniform type and manufacture.

Indicating instruments shall have black marking on a white background and be fitted with an externally accessible zero adjuster. They shall have no parallax error and their normal maximum reading shall be approximately 60 % full scale deflection.

Amp-meters in motor starter circuits shall be capable of withstanding the starting current and shall have a compressed overload scale. The scale shall be clearly marked with a red line indicating normal full load current.

Indicating instruments shall comply with EN 600 51 and shall be of industrial grade accuracy, (±5%) unless otherwise specified.

Kilowatt-hour meters shall be in form of power monitors, with communication port, comply with the latest Standards and have an accuracy of 1% unless otherwise specified.

#### Digital Indicators

The digital indicators shall have at least a 4-digit display with floating decimal point and shall display positive and negative readings; display digits approximately 14 mm high, and sampling rate not less than 10 per second, include a remotely initiated display hold facility, be powered from the 24 Vdc.

#### Meter Relays

Meter relays shall comply with the requirements as detailed in the Particular Technical Requirements, but shall additionally incorporate one or two adjustable set point contacts for alarm or control.

The set point shall be visible and adjustable from the front and the signal output shall be via volt–free change–over contacts of suitable material and rating for the application.

### Indicator Lamps

Indicator lamps shall be of LED diode type, uniform type as far as possible.

Indicator lamps shall be not less than 18mm diameter and shall be of the projecting type so they can be seen from the front and side of the switchboard. They shall be visible under bright sunlight conditions.  Colors of indicator lamps shall generally comply with the latest Standards.

A test buttons shall be provided for testing of indicator lamps.

### Labels

All components, internal wiring, doors and removable covers shall be labeled. Fuse carriers shall also have labels which state the fuse rating to be fitted.

All designating labels shall be of traffolyte or similar finished white (black) with engraved letters and numbers black (white) and fixed by non-rusting screws. Danger and warning labels shall be of similar material finished in yellow with red letters and numbers. Edges of labels shall be bevelled and lettering shall be at least 4mm high.

### Push Buttons

Colors of push buttons shall generally comply with the latest Standards and in particular shall be as follows:

- Red 	- stop, off or emergency buttons

- Green 	- start or on buttons

Emergency stop push buttons shall have enforced contact separation. They shall be direct acting on the control circuit, so they trip the circuit under all conditions, i.e. no intermediate devices shall be utilized. They shall have mushroom-heads of the stay-put pattern.

### Terminal Blocks

Terminal blocks shall be of non brittle material, screw-clamp or stud type barrier pattern. Pinch screw type blocks shall not be used. At least 20% spare terminals shall be provided at all blocks.

Every terminal block shall have a clear plastic clip-on cover running the full length of the block to prevent accidental contact with live terminals.

Removable DIN rail terminals shall be provided for all wiring, mounted at an angle to provide ease of access, positioned not less than 150mm from gland plates, doors or covers.

Power, control, earth and end stop terminals shall be provided and terminals shall be grouped, separated by barriers and labeled according to their voltage level and function.

No more than two conductors may be connected to one side of a terminal. Outgoing cables shall be wired so that outgoing wiring is connected to one side only.

### Test Terminal Blocks

Test terminal blocks shall be provided for secondary injection and testing of relays.

A metering block shall be provided for the connection of portable sub-standard instruments for plant testing.

Test terminal blocks shall be provided with shorting links or be of a type suitable for use with portable test plug-in equipment.

### Time Relays

Time relays shall be of an electronic uniform type for all applications, adjustable for different time ratio and delay duty.

### Fused-switches and Disconnecter Combination Devices

Fused switch disconnecters, switch disconnecters and disconnecters, shall be rated at 500V and shall be to the latest Standards. Fuse switch disconnecters shall be of the air break triple pole or single pole and neutral type. They shall have not more than one fuse in any one pole. The neutral shall be either switched or taken through a removable link. If a switched neutral is required, the neutral shall be arranged to make first and break. A separate brass earth terminal shall be provided.

Operating mechanisms shall be of the independent spring type and fitted with mechanical ON and OFF indicators. Operating handles shall be of semi-flush or telescopic pattern to reduce front projection to a minimum.

Facilities for locking the operating handles by padlock shall be provided.

All switch disconnecters shall be rated to make the full short circuit current of the system. Units used on distribution circuits shall be rated to break full load current and units used in motor starters shall be rated to break stalled motor current.

### Fuses and Links

Fuses shall comply with the latest Standards as appropriate. Fuses and links shall be provided to enable any circuit to be isolated as necessary for maintenance and test purposes without isolating the whole panel. All fuses over the 25A shall be of the cartridge type. Fuse carriers and solid link carriers and bases shall be made of plastic moulded insulating materials; ceramic materials will not be accepted. Accessible live connections shall be effectively shrouded and it shall be possible to change fuses and remove links with the circuit alive without danger of contact with live metal. The fuses shall be rated to give maximum protection to the apparatus in circuit and the rating shall be inscribed on the fuse label.

Earthing and neutral links in main supply circuits shall be solid copper bolted pattern.

Fuses and links functionally associated with the same circuit shall be mounted side by side.

### Control, Auxiliary, and Selector Switches

Control and Selector Switches shall conform to the latest Standard. Control Switches shall be of the three-position type with a spring return action to a central neutral position.

Electrically operated circuit-breakers shall be fitted with a control switch labeled Open/N/Close. These shall be of the pistol grip type with a spring return to the neutral position. The switch shall be lockable in the neutral position.

Selector switches shall make before break and shall remain in the position selected and be lockable in that position. They shall have spade shaped handles and each position shall be labeled.

Double pole moulded case or miniature circuit breakers shall be provided as required.

#### Discrepancy Switches

Where illuminated control switches are used to provide discrepancy indication, the circuits shall be arranged such that the lamp is energized via a flasher unit. This flashing discrepancy indication shall operate if the switch is not fully activated or if the controlled item is not in the position shown by the switch blade. The switches shall be of the type having a rotary action to select the operation and a push button action to initiate the operation.

### Switchboard Ancillary Equipment

The following ancillary articles shall be supplied with each switchboard:

- Two pairs rubber gloves to the latest Standard according to rated voltage of switchboard; - 1 No. "treatment for electric shock" metal enamel instruction plate suitable for screen attachment; - Operating handles, tools, spares and lubricants as manufacturer's standard.

### Voltage Transformers

Voltage transformers shall comply with the latest Standards. The accuracy class and VA rating shall match the requirements of all connected instruments and relays.

The primary circuit shall be protected by fuses having a short-circuit rating of not less than that of the switchgear. The connections between the fuses and the switchgear primary conductors shall be of sufficient cross section and be supported to withstand the short-circuit rating of the switchgear.

The secondary circuit shall be protected by fuses mounted as close as possible to the secondary terminals. Fuses shall be accessible without the need for isolating the switchgear.

### Current Transformers

Current transformers shall comply with the latest Standards and shall be of the wound- or bar-primary type according to ratio required. All current transformers shall have a short-time current rating of not less than that of the switch panel in which they are incorporated. For bar-primary current transformers this rating shall be for a period of 3 seconds. For wound-primary patterns the rating shall preferably be for a period of 3 seconds but may be reduced to not less than 0.5 second subject to the Engineer's written approval.

Identification labels shall be fitted giving type, ratio, rating, output and serial numbers.

Current transformers shall be of Class 1 accuracy for use with measuring instruments and Class 10P for use with protective relays. Class 5P shall be used for combined overcurrent and earth fault protection of the inverse time overcurrent type.

The secondary windings of each set of star-connected three phase current transformers shall be earthed at one point only, via a bolted link. Shorting links shall be provided at test blocks.

Separate sets of Current Transformers shall be used for metering and protection.

### Control Transformers

Unless otherwise specified all contactor control circuit supplies shall be obtained from the 230 V secondary winding of a single phase integral control transformer.

Transformers shall be of the double wound pattern in accordance with the latest Standards and shall have an earth screen between primary and secondary windings. One leg of the secondary winding shall be earthed. The primary winding shall be protected by cartridge fuses, and the secondary winding shall be protected by a fuse and link.

A spare control transformer shall be provided with each new switchboard.

### Circuit Breakers

The circuit breaker shall ensure isolation between bus bars and circuits when disconnected. Any access to the live fixed contacts shall be prevented.

Circuit breakers shall not involve any special maintenance, and shall have a high electrical endurance. All circuit breakers of the same type and rating shall be interchangeable. Circuit breakers shall be of the fixed type.

The circuit breakers shall be covered by a test certificate issued by a testing authority, recognized by International Agencies. Circuit breakers shall be equipped with manual operating mechanism or an electrical spring stored energy operating mechanism, including at least:

- 1 electrical motor, recharging the mechanism as soon as the breaker is closed or opened;

- 1 anti-pumping relay to prevent the closing coil being fed continuously.

On the front plate of the circuit breaker indication and control devices shall be provided as follows:

- mechanical indication of the position of the circuit breaker, positively driven in both open and closed positions;

- mechanical indication of the state of the motor charged spring; this shall clearly show whether the spring is charged or not;

- local manual spring release;

- emergency hand operated local spring charging device.

Provision shall be made for local manual tripping and closing of the breaker and at the front of the panel section a legend plate shall bear all the indicating and control devices necessary to carry out normal service operations.

The circuit breaker shall be equipped with a suitable number of auxiliary contacts. They shall be positively driven in both positions and be mounted in such a way as to facilitate maintenance and inspection. The equipment which constitutes the contact surfaces shall be treated against corrosion.

### Low Voltage Auxiliaries for power switch board

Each panel section shall be fitted with a low voltage compartment containing the whole low voltage equipment. All protective relays, instruments, meters, live parts of indication and control devices shall be located in this compartment and when necessary, indication shall be visible from the front. The low voltage compartment shall be located at such a height so that all indications can be clearly seen by the operating staff, normally standing.

### Relays

Relays shall comply with IEC 60255 standards. Relays shall be of the draw out type, flush mounted and of the static type. Instruments and meters shall be flush mounted.

### Control and Interposing Relays

All control and interposing relays, shall operate on a 24Vdc, or 230 Vac (nominal) to earth and shall: operate reliably over the range +10% to  20% of the nominal supply voltage, be of the plug in type complete with plastic cover and retaining clip, have vacuum impregnated coils and be suitably treated for operation under the specified environmental conditions, have contact material suitable for each application, have relay bases of the front connected, screw clamp type, incorporate indication of energisation / de-energisation.

All relays shall have a surge suppression either varistor or diode, what is applicable, connected directly across the coil.

All relays and the associated wiring shall be protected by suitably rated fuses or MCB.

A permanent means of identification shall be fixed to each relay base and this identification shall be in accordance with the circuit diagram reference.

Where voltages from a remote source (i.e. voltages which cannot be readily isolated from within the cubicle), are connected to a relay or associated terminals, fuses etc., the Contractor shall ensure that all such live parts are fully shrouded and that appropriate warning notices are fitted.

The Contractor shall be responsible for ensuring that a.c. relays cannot be held in due to capacitance effects on long switching lines. Where such a possibility exists, a d.c. supply shall be provided.

### Anti-Condensation Heaters

Anti-condensation / anti-humidity heaters shall be fitted to wall mounted enclosures; individual floor mounted enclosures; each vertical section of single tier switchgear or control gear; each tier of multi-tier enclosures. The rule is not applicable for the equipment located in the temperature conditioned rooms. Each heater shall be controlled by its own thermostat, ON/OFF switch and fuses or MCB. Heaters in exposed positions shall be fitted with a safety guard.

## Protective Relays

Protective relays shall be mounted on the front of the switch unit or relay panel in such a position that operation and maintenance can be conveniently carried out. Auxiliary relays may be mounted inside a cubicle provided that they are readily accessible. Each relay shall be contained in a dust proof case with a clear front cover. All metal bases and frames shall be earthed except where there are technical reasons where this is impracticable.

All relay contacts shall be capable of making the maximum current which can occur in the circuit without causing damage to the contacts. Relays shall have provision for testing the operation and calibration without disconnecting the permanent wiring.

Flush, draw out type relays are preferred. Each relay shall have an indicator device to show when the relay has operated and if necessary, which phase element. Each indicator shall be hand resettable. Resetting devices shall not require the removal or opening of the relay. It shall not be possible to operate the relay without opening the case.

Where solid state relays are specified, these shall be of the module type comprising a number of plug in elements allowing interchange of functions. Each of the protection elements shall have adjustable controls for current and time settings as required. Solid state relays of a particular type shall have interchangeable protective elements with other similar relays supplied under this Contract.

All relays shall be provided with a name plate giving manufacturer, type, serial number, year of manufacture, ratings and connection diagram.

All relays using a dc auxiliary supply shall operate down to 60% of the nominal voltage and up to boost charge voltage of the battery.

Protection relays shall comply with the latest Standards

### Overcurrent and Earth Fault Protection

Relays shall be of the attracted armature or rotating disc type having instantaneous, inverse or very inverse definite minimum time, directional or non-directional characteristics as specified.

### Under and Over-voltage Relays

Variable settings shall be provided as required together with a 0 to 5 second time delay.

### DC Trip Relays

Relays shall be suitable for operating with the voltage reduced to 60 % of normal.

### Motor Thermal Relays

Relays for motor protection shall give protection against overload, stalling, current unbalance, and single phasing. The relay shall have variable current settings and overload tripping time.

## Motor Starters

The starter cubicles are required to form part of a motor control centre and as such circuit connections, protection devices etc., shall comply with the relevant clauses of EN 60439-1 for form 3b switchboards. The cubicles shall be easily accessible for maintenance purposes and shall be damp and dustproof to IP54. Each motor starter shall be of a rating to carry the full load current of its rated duty at its most severe load conditions.

Motor starters shall be combination type as defined in and complying with IEC 60947-4-1, for type 2 short-circuit coordination, and shall be of the electromagnetic non-latching type. The circuit breaker fuse, contactor and overload relay combination shall have undergone and passed all the tests specified for full Type 2 co-ordination.

Utilisation Category shall be selected to suit the application of the motor starter, but shall be not less than

AC-3 and mechanical endurance of 3 million operation, at least. Unless otherwise specified, motor starters shall be suitable for uninterrupted duty.

Motor starters which are to be PLC controlled shall be adapted for such control.

Where two or more contactors are installed within a starter they shall be electrically interlocked to ensure that the correct starting sequence is maintained.

### Individual Starters

Each individual starter listed below, shall be housed in a separate totally segregated compartment fixed or withdrawable type and shall contain the following:

One Three Pole (& N) fault rated, door interlocked, fused switch or MCCB with mechanical operating handle, ON/OFF indication and padlockable OFF facility. The fused switch or MCCB shall be fitted with not less than one "make" and one "break" spare auxiliary contacts in addition to those used within the starter circuitry

Combination of triple pole magnetically operated contactors with magnetic blow–outs or arc chutes and no–volt release.

Thermal overload device with inherent temperature compensation and three phasing protection, time lagging to cover the starting period, and overload setting adjustment.

Control voltage MCB

Set of Control relays as required

Indicator lamps for Running status (Red) and Motor tripped alarm (Amber)

Ammeter and single CT for 3 phase motors of 5kW and above. Where power factor correction capacitors are fitted, the ammeter shall read uncorrected current

Hours run counter, if a function of operating time counting is not completed by SCADA

Winding temperature detector relay, if it is applicable

Power factor correction capacitors shall be supplied when necessary, to correct the power factor of the motor to a minimum of cosfi 0.85. Where the motor rating is 30kW or greater, the capacitors shall be separately switched and fitted with discharge devices. The capacitors shall comply with the latest Standards.

All necessary links, wiring, terminals, terminations, and insulated barriers

### DOL Motor Starters

For Direct on Line Starters MCCB and Thermal overload device could be combined as one device, if conditions of type 2 coordination can be achieved.

Current capacity of contactor applied shall be at least 50% higher then the motor rated current.

This type of engine start should be avoided as much as possible.

### Current Reducing Motor Starters

Motor starters shall be of either Star-Delta or Soft Starter type as specified. The starters shall comply with the latest Standards. The starter shall incorporate the following features:

- Motor circuit HRC fuses or motor circuit protector MCCB type, in coordination with Supplier recommendation.

- For Star-Delta starting, one set of magnetically operated, electrically or mechanically interlocked, star and delta contactors operating under electrical or pneumatic automatic timing devices with adjustable operating periods.

- For Soft Starting, one set of magnetically operated, electrically interlocked, main and by-pass contactors. The Soft Starters shall comply with the latest Standards and shall incorporate the following features:

- Temperature protection for Motor winding PTC/NTC input

- Starting current adjusting (2 – 6) motor rating current

- Motor current display and analog 4-20 mA output

### VSD Starters

The starters shall comply with the latest Standards. The starter shall incorporate the following features:

Motor circuit HRC fuses or motor circuit protector MCCB type, in coordination with Supplier recommendation.

The inverter shall be connected to the 400V supply by a triple pole contactor.

A facility to temporarily wire the motor as a DOL starter in the event of inverter failure, without inverter dismantling, shall be provided.

### Frequency converters

The frequency converter shall be delivered with the newest technology including digitalized control system, menu programming, diagnostic display for reading of faults and operation conditions and provides a variable voltage/frequency supply to the motor drive over the duty range. The following protection features shall be included:

- Instantaneous clearance of over-current, over-voltage, inverse time overload and earth leakage protection for the inverter/motor;

- Phase sequence indication, phase of fuse failure, and under voltage protection; - Thermal protection of power circuits from excess temperatures; - Built-in adjustable over speed or over frequency protection.

The program system for the frequency converter shall be simple so that input of all data can take place without other equipment than the operation unit in frequency converter. It shall be possible to read all alarms in a display or with lamps. Regardless of the type of fault that may arise, it shall be possible to transmit this alarm via a communication to the SCADA system. In the event of critical faults in frequency converter, motor or pump etc., the frequency converter must cut out.

The frequency converter shall be protected against surge voltage, excess current, excess temperature as well as be secured against short circuit and earthing and shall be delivered with a EMC filter fulfilling class B according to EN55011.

The frequency converter itself shall be built into an enclosure that meets IP2X with the main control panel doors open. The diagnostic display shall be readable with the compartment door closed and the isolator in the on position.

It shall be capable of operating within the specified panel without exceeding any maximum temperatures dictated by the equipment manufacturer with ambient temperatures up to 45oC. Adequate precautions shall be taken to prevent the protective fuse devices blowing due to incoming mains supply transients. The Contractor shall obtain from the Electricity Company the necessary written approval for the use of the equipment to be supplied and shall furnish the Engineer with copies of the data given to the Electricity Company and of the written approval received. In the event of problems in service, apparently attributable to the effects of the equipment, either on the plant or on the external electricity network, the Contractor shall provide and operate an automatic harmonic analyser to establish whether or not the equipment complies with the terms of the Electricity Supplier’s approval. The Contractor shall be responsible for rectifying any shortfalls identified.

It shall be a six pulse solid state electronic pulse width modulated variable frequency supply system, adequately rated to have 10% reserve capacity when continuously driving the pump motor at the highest load.

All the components of the frequency inverter shall be easily accessible for both test and maintenance purposes and there shall be built into the various components and circuits test facilities which either automatically indicate a failure or indicate a failure to a diagnostic test facility.

The amount of variation of the output wave from a pure sinusoidal wave shall be such as to enable any motor driven by the inverter to be continuously operated to at least 90% of its rated output on a normal 400V 3ph supply.

The ramp type acceleration/deceleration facility shall have a range to cover accelerating from zero to full speed variable from 0-10 sec’s to 0-120 sec’s with a similar facility on the deceleration range.

When fan cooled units are used, the fan should run whenever the drive is in operation.  This shall be achieved by interlocking the line contactor with the fan supply.

### Motor Starters – High Voltage

High voltage motor starters at 3.3, 6.6 or 11 kV shall comply with the latest Standards and incorporate features specified under LV motor starters except as modified below.

Contactors shall be vacuum or air as specified. Operation of vacuum contactors shall be such that current is broken at, or very near to zero current to minimise current chopping. Contactors shall comply with the latest Standards and shall have utilization category AC-3 and duty of Class 0.03 unless otherwise specified. Each starter shall have low voltage and high voltage apparatus segregated with access to the low voltage control compartment by a separate door.

All HV starters shall be equipped with motor protection relays which provide thermal imaging type overload detection, earth leakage protection, instantaneous overcurrent protection, and phase current unbalance protection.

### Actuator Starters

When motorised valves are specified, the actuator starters shall be integrally housed within the actuator in a robustly constructed, totally enclosed weatherproof housing to enclosure protection standard IP65. The motor starter shall be capable of starting the actuator motor under the most severe load conditions.

The starter housing shall be fitted with contacts and cable terminations for power supply, remote PLC control and positional indication circuits.

Each actuator starter shall be equipped as follows:

- Magnetically operated line reversing contactors with arc chutes, no-volt releases and electrical and mechanical interlocks;

- thermal overload device;

- set of “Open”, “Close” and “Stop” pushbuttons;

- set of “Torque”, “Open” and “Close” position limit switches;

- “Local-Off-Auto” Switch with padlocking Works. The “Auto” position will permit control to be initiated by a signal from automatic equipment as detailed in the relevant section of the Specification.

## Circuit Breakers

### High Voltage Circuit Breakers

Circuit breakers shall be vacuum or SF6 type as specified. The equipment shall comply with the latest Standards as appropriate and be fully rated for the ambient conditions specified. Circuit breakers shall be capable of clearing any fault condition which may occur on the system without damage to equipment or personnel. Circuit breakers of the same pattern and rating shall be interchangeable.

Vacuum circuit breakers shall comprise separate vacuum interrupters designed to prevent welding of contacts and sharp current chopping during fault interruption or switching or motor loads.

All circuit breakers shall be provided with operating mechanisms as detailed in the specification, the selection being from the following types:

- independent manual spring;

- hand charged spring with electrical or manual release;

- motor charged spring with electrical release;

- dc solenoid.

All operating mechanisms shall have mechanical 'ON' and 'OFF' indicators and a manual trip device fitted with means for locking. Hand charged and motor charged spring mechanisms shall have mechanical indicators to show 'SPRINGS CHARGED' and 'SPRINGS DISCHARGED'. The operating mechanisms of hand charged and motor charged spring types shall be arranged so that release of the springs to close the circuit breaker can only be achieved by a deliberate action. It shall not be possible for vibration or mechanical shocks to release the charged springs. Motor charged spring mechanisms shall be arranged so that charging is initiated automatically following a discharge. The necessary limit stops and switches for the automatic control of the charging shall form an integral part of the mechanism. The facility shall be provided to hand charge a motor charged spring mechanism.

Spring operated mechanisms shall be provided with volt-free contacts to give indication that the springs are charged.

Solenoid closing mechanisms shall be suitable for operation down to 80 % of the nominal control voltage. They shall not maloperate or cause excessive vibration when energized either from the voltage of the closing battery with the charging rate set at maximum, or from the voltage of a full wave rectified source designed for multiple simultaneous operation. Unless otherwise specified, this higher voltage shall be not less than 120 % of the nominal control voltage.

To facilitate maintenance and the adjustment of contacts, it shall be possible to 'slow-close' the circuit breaker but this operation shall only be possible in the fully withdrawn position. Any operating handle or lever necessary shall be supplied.

All circuit breakers shall be provided with interlocks to ensure that:

- the circuit breaker cannot be racked into or out of the service or earth position whilst it is closed. Attempts to rack out a closed circuit breaker shall not cause it to trip;

- the circuit breaker can only be closed when fully engaged in the service, earth, or fully isolated positions;

- the circuit breaker cannot be closed in the service position without completing the auxiliary circuits between the fixed and moving portions;

- the circuit breaker cannot be 'slow-closed' except in the fully isolated position;

- with hand charged or motor charged spring mechanisms, the springs cannot be discharged until they have been fully charged or until the means for charging has been fully removed and disconnected;

- when the circuit breaker is closed in the earth position, tripping can be effected only by the manual device on the operating mechanism;

- Where mechanical key interlocking is employed, tripping of a closed circuit breaker shall not occur if any attempt is made to remove the trapped key from the mechanism.

Circuit and/or busbar earthing shall be by the transfer circuit-breaker method without the requirements of any loose attachments. The earthing operation shall be completed by the closing of the circuit breaker by its normal operating means using local control. Selection of either circuit or busbar earthing shall be possible only after the circuit breaker has been fully isolated. Mechanical key interlocks shall remain operative when the circuit breaker is in either earthing position.

Facilities shall be provided on all incoming and feeder circuit breakers for earthing the circuit side. On at least one circuit breaker panel in any section of busbars, facilities shall be provided for busbar earthing. A set of safety shutters shall be provided to cover each three phase group of stationary isolating contacts. The shutters shall be opened automatically by a positive drive from the circuit breaker moving portion and when closed shall prevent access to the stationary isolating contacts. When the circuit breaker is withdrawn each set shall be capable of being individually operated and of being padlocked in the closed position.

To facilitate high voltage and current injection testing via the isolating contacts, a device shall be provided for fixing (not locking) the shutters in the open position and for releasing them into the closed position. The device shall be arranged to be cancelled by the moving portion to ensure the restoration of the automatic feature of the shutters.

Busbar shutters shall be coloured red, and labeled 'BUSBARS' in large white letters. Circuit shutters shall be coloured yellow. Shutters in bus-section units shall be coloured red and shall be labeled with a large white arrow pointing in the direction of the section of busbars to which the contacts are connected.

Circuit breaker moving portions shall be fitted with positive guides to ensure correct alignment of the isolating contacts in both the service and the earth positions.

### Low Voltage Circuit Breakers

All 400V circuit breakers for incoming circuits and bus section circuits on 400V switchboards and interconnector circuits shall be of the air break metal clad type complying with the requirements of the latest Standards.

Circuit breakers shall switch three phase poles. The neutral pole shall either be switched or established through a bolted link. Access to the link shall not be possible when the equipment is in the "Service Position".

Provision shall be made for easy access to the circuit breaker contacts for maintenance purposes.

Arc chutes shall be so arranged that the emission of hot gasses shall not damage any part of the equipment.

### Moulded Case Circuit Breakers

Moulded case circuit breakers (MCCBs) shall be manufactured to the latest Standards. MCCBs shall have thermal overload and adjustable magnetic short circuit tripping devices with a trip-free mechanism to ensure that the contacts cannot be held closed against a fault. Contacts shall be silver tungsten tipped and shall operate with a wiping, arc resisting material and incorporate arc chutes based on the deionising principle.

MCCBs shall have a factory calibrated and sealed trip unit, interchangeable with similar units for varying the rating of the circuit breaker.

Where dust and damp proof enclosures are to be used, then the circuit breakers shall be fully enclosed in a case with a gasketted door. Circuit breakers mounted in a composite control panel shall be segregated from other equipment and have a matching purpose-made cover plate. Where possible, circuit breakers shall be mounted vertically and be arranged so that one breaker can be removed without interfering with other circuit breakers. The switch dolly and protruding face shall be engraved with the circuit rating and the ON and OFF positions.

Tripping due to overload or short-circuit shall be clearly indicated by the handle automatically assuming a position midway between the manual ON and OFF positions. To reset from the 'tripped' position, the dolly shall first pass through the OFF position. All phase poles shall operate simultaneously.

MCCB's shall be ambient temperature compensated. Compensation shall allow the breaker to carry rated current between 25 oC and 50 oC with tripping characteristics that are approximately the same throughout this temperature range.

### Miniature Circuit Breakers

Miniature circuit breakers (MCBs) shall be manufactured and tested to the latest Standards. MCBs shall have a short circuit rating of at least M4 or less according to selectivity and shall be Type C unless otherwise specified. The fault capacity of the MCB shall be not less than that of the switchboard. If this is not the case, back up HRC fuses shall be fitted.

### Residual Current Circuit Breakers

Residual current circuit breakers (RCCBs) shall be of the current operated type complete with current balance transformer, test push button, trip coil and thermal overloads. They shall be double pole for single phase and four poles for three phase and neutral circuits. ELCBs shall comply with the requirements of the latest Standards.

The out of balance current shall not exceed 30mA for circuit breakers up to 63 amp rating and 500mA for above this rating.

## Control Distribution

### Local Control Stations and Control Boxes

Local control stations shall be of heavy duty construction and where appropriate, constructed in accordance with electrical safety and general construction equipment. Local control stations and Control Boxes shall be mounted directly onto the plant to be controlled, or be provided with a floor mounting tubular pedestal with provisions to accommodate the incoming cables.

Small covers shall be secured by screws or bolts and be totally removable. In larger sizes and where instruments are to be fitted, the covers shall be provided with heavy duty hinges.

The bottom face shall be arranged to accept, with adequate space for the use of spanners, gland terminations for the number of cables required.

Terminals shall be provided for interconnections arranged vertically at the side for easy access, and marked with identification numbers/letters corresponding with the associated diagrams.

Local Control Stations shall be provided with the following:

- gland plate arranged for bottom entry;

- anti-condensation heater with thermostat and fuse;

- padlocking facility and padlock;

- earthing bar with terminal holes;

- labels for front door, fuses, terminal blocks, and terminals;

- control and signaling elements as it is specified by station duty

Pendant type local control stations for cranes, hoists, etc. shall be of moulded neoprene or equivalent heavy, flexible, high impact strength materials. The station shall be connected by a long moulded-in cable strengthening sleeve, to minimise the possibility of cable fracture at the bending point. The enclosure shall be self coloured in safety yellow.

### Marshalling Boxes

Marshalling boxes shall be constructed of sheet steel or moulded neoprene with ample space for routing and terminating cables and cores. Every marshalling box shall be provided with the following:

- undrilled gland plate arranged for bottom entry;

- padlocking facility and padlock;

- labels for front door, terminal blocks, and terminals;

## Power Transformers

Power transformers 25kVA and above shall be of the outdoor, oil immersed, naturally cooled type. They shall be manufactured and tested to the latest Standard.

Transformers shall be sized for continuous operation at the maximum rating at the ambient conditions specified. Unless otherwise specified the rating shall allow for unshaded conditions.

The transformer load factor shall be taken as 70% for normal operation, but not smaller then ten time of maximum drive rating with DOL starter and five time of maximum drive rating with Current Reducing Motor starter.

The windings shall be double wound with preferable connection Dy11, and above 100kVA connection Dyn5.

Transformers shall be supplied complete with standard equipment for the rating applied.

Transformers rated above 250kVA shall be provided with offload tap changers manually operated by a lockable wheel or handle. The tappings shall be provided on the HV windings at ±2½ % and 5% of the no load primary voltage.

Cable boxes with wiping or screwed glands shall be provided for the cables specified. A non-magnetic gland plate shall be fitted for single core cables and insulated glands provided for 400mm² cables and above. It shall be possible to remove the cable boxes without breaking the cable seal or draining the oil. Disconnecting link boxes shall be fitted on the high and low voltage sides of the transformer for cable pressure testing.

### Insulators and Bushings

Porcelain epoxy or silicon rubber insulators and bushings shall comply with the requirements of the latest Standard as appropriate.

Each insulator shall bear the manufacturer's mark and batch identification, which shall be applied before firing. The clamping surfaces of all porcelain insulators shall be accurately ground and shall be free of glaze.

### Insulating Oil

Insulating oil shall comply with the requirements of the latest Standards. Insulating oil shall be provided by the Contractor for all oil-filled apparatus and 10% excess shall be provided for topping up purposes in sealed drums. If equipment is to be filled with oil at Site, the Contractor shall provide for filtration equipment of suitable capacity.

The Contractor shall supply a schedule of insulating oils and greases which the Contractor recommends for use with his equipment.

### Transformer Tanks Enclosures

#### Oil Filled Transformers

Transformer tanks shall be shot blasted internally and externally to remove mill and welding scale.  Immediately after shot blasting, a primer coat of paint shall be applied to external surfaces.

Tanks shall be oil pressure tested to at least 34 kN/m² plus the dead weight of oil contained under the operating conditions.

Tanks shall be provided with a suitably sized earthing connection.

### Main Terminal Connections

Unless specified otherwise, HT cable connections shall be designed for dry type terminations, and shall have adequate space to permit cores of cables to cross over if required.

It shall be possible to remove the cables without breaking the cable seals or oil seals.

The primary and secondary terminal connections shall be provided with gland plates, to suit the M.V. and L.V. cables. Non-magnetic gland plates shall be provided where single core cables are specified

## Earthing

The RWMC shall be completed with earthing and lightning protection system according to DIN V ENV 61024–1, DIN V VDE V 0185 and the relevant standards and technical regulations of the Country of Project. At the beginning of the work, an Earth specific resistance shall be determined, in order to chose the required measures of earthing and lightning protection.

The metalwork of all items of electrical plant, electrical system neutral points, power and control cable armouring and screens, and extraneous metalwork including structural steelwork, pipework, fences and gates, shall be connected to the earthing installation.

Earth continuity in non-electrical plant shall normally be achieved via metal to metal faces, pipe flanges, metal hinges, and metal fixings. Earth straps to bond pipework sections shall be supplied where earth resistance is high or there is risk of corrosion or similar which could in the future increase resistance and affect earth continuity.

Perimeter fences shall be either bonded to the site earthing system or to an independent earthing system. Metal gates shall be bonded to the fence using flexible connections.

When the installation is complete, soil resistivity or other tests shall be performed and witnessed by the Engineer, to ensure that the required earth loop impedance is less than it is require by the local technical regulation.

### Submissions by the Contractor

The Contractor shall make submissions in relation to earthing installations including, where relevant, the following:

- Diagrams detailing the complete earthing installation, including connections to all items of electrical plant and extraneous metalwork.

- Earthing conductor route and lay out giving location of all test links and location of all earth electrodes and connecting chambers.

- Manufacturers catalogues, data sheets and specifications for all fittings and materials.

- Calculations for Earth resistance, Potential rise, and Step and Touch potentials.

- Test Certificates for tests carried out at site including: Earth electrode resistance; Continuity of protective and equipotential bonding conductors; Earth loop impedance.

### Installation

The earthing installation shall comprise an earth terminal, earth busbars, circuit earthing conductors, equipotential bonding conductors, main earthing conductor and earth conductors and electrodes (where is applicable). The circuit earthing and equipotential bonding conductors shall be of the radial, grid or ring form as dictated by the plant lay out. The earthing installation shall be protected from mechanical damage and corrosion.

Joints in tape conductors shall be bolted or welded. Clamped and bolted type joints shall be hot deep galvanized.

The interconnection of conductors made using X cross pieces below ground shall be corrosion protected. Compression type lugs shall be provided for the termination of cables.

Earthing conductors shall be buried directly in the ground or secured to building structures, cable racks and trays using propriety fixings.

Foundation earth conductor shall be embedded into concrete foundation of buildings, clarifiers, reservoirs, pump stations etc. For foundation earth conductors as well as for up-leads, the hot dip galvanized tape 25 x 4 mm shall be used.

Connection of foundation earth conductor to steel reinforcement shall be done at maximum 6 m intervals. For every room enough numbers of up-leads carried out up to (1-2) m above floor level, shall be obtained. An equipotential bond shall be provided to all buried metal pipework at the point of entry into a building or chamber where electrical apparatus is installed. Electrical continuity across all pipe joints within the structure shall be ensured. Normally the connection of the pipe flanges will suffice, but where pipework incorporates a compression coupling, a bond shall be provided to any otherwise isolated section.

Power Cable armouring and screens shall be bonded to earth at both ends unless otherwise specified. Cable armour shall not be used as the sole earth protective conductor.

### Conductors

Normally circuit and main earthing and equipotential bonding conductors shall be made of hot dip galvanized tape.

Where a copper as material is applied, the high conductivity copper tape or 1000V grade PVC insulated multi-stranded cable shall be used. PVC cable insulation shall be striped green/yellow. Cable lengths shall be continuous and intermediate jointing is not permitted.

The main bonding conductor shall be not less than 16mm² and supplementary bonding of non-electrical plant not less than 6mm². All connections shall be made using compression type cable lugs, taped on completion to completely seal the lug and any bare copper from the atmosphere.

It is suggested to avoid the use of copper in aggressive to copper atmosphere. Otherwise, it shall be deep tinned, or stainless steel materials resistive to aggressivity of the atmosphere shall be used.

The surface to which earthing bonds are fixed shall be cleaned free from paint and other non-conducting material and coated with petroleum jelly.

### Earth Electrodes

As an additional measure of the improving of the earthing system, the earth rod electrode shall be used around the building. Earth electrodes shall be 65 or 24 mm diameter steel dip galvanized steel pipe 3m long. Earth connectors shall be fixed to rod electrodes by rod to tape clamp.

Earth rods shall have hardened tips and caps and be extendable.

Each earth rod shall be provided with a clamp fabricated from non-ferrous metal for the connection of the earthing conductor. The connection shall be made in a concrete inspection chamber set flush with the finished ground level. The inspection chamber shall be permanently marked "ELECTRICAL EARTH".

Marker posts and plates shall be provided to mark the position of the electrodes and buried connections. The markers shall be similar to those provided for cable routes.

### Main Earth Bar

Where specified, a main earth bar shall be installed in a convenient location. This shall comprise a high conductivity copper bar of sectional area at least that of the main earthing conductor. The earth bar shall be wall mounted, supported on insulators. The earth bar shall be complete with disconnecting links for test purposes, and connection points for the outgoing and incoming earth cables and tapes.

Earth studs shall have a minimum size of M8.

### Tests at Site

On completion of the earthing installation the Contractor shall measure the resistance of each electrode installation and of each complete earthing system to the general body of the ground. All other tests stipulated in the Reference Standards, shall also be carried out.

The resistance to earth of each complete earthing network shall not exceed one ohm.

## Lightning Protection

All structures and buildings shall be provided with lightning protection in accordance with relevant

EN/IEC and the Project Country Standards (SRPS EN 62305-1:2013, Protection against lightning, General Principles)

Where buildings or sections of the plant are to be protected against lightning or static charges, an earthing system shall be provided. The installations shall be carried out in accordance with the latest version of DIN V ENV 61024-1, DIN V VDE V 0185 and the relevant standards and technical regulations of the Country of Project. The Buildings shall be classified to lightning protection of grade 1.

### Conductors

Lightning and down conductors shall be routed as directly as possible avoiding acute bends. The installation shall generally comply with the requirements for earthing conductor installation.

The lightning conductors and down connectors shall be of hot dip galvanized tape 25 x 3 mm or AL fi 10mm rod. The tape shall be fixed to the outside of the structure by means of stand off saddles. Where indicated, connections shall be made to the concrete reinforcing. The route of the tapes and the fixings shall be approved by the Engineer before installation. Where the conductors are specified they shall be PVC insulated to prevent corrosion and to blend with the building fabric.

It is suggested to avoid the use of copper in aggressive to copper atmosphere. Otherwise, it shall be deep tinned, or stainless steel materials resistive to aggressivity of the atmosphere shall be used.

A test link shall be installed in each down conductor adjacent to the earth rod at a height of 1700mm above ground level. The overall resistance of the earth termination system to earth shall not exceed 1 ohm. If this requirement is not met the number of earth electrodes shall be increased or they shall be interconnected until a value of 1 ohm is attained. After this resistance value is obtained, the lightning protection system shall be bonded to the main earthing system.

### Lightning Protection Devices for Plants

The Contractor shall provide lightning and surge protection devices at each area of plant. This shall ensure isolation and automatic resetting of the parts of the system being subjected to high surge currents. Devices shall be unfused if it is not strictly requested by the Manufacturer.

Lightning protection shall be selected to provide the highest degree of protection possible.

The type and manufacturer of the Lightning Protection Unit (LPU) shall be subject to the approval of the Engineer.

Each lightning protection unit shall be earthed as directly as possible, without inductive loops and equipotential bonding to the nearest earth reference bar. A single unjointed earth cable shall be utilized. Individual lightning protection units shall bolt directly onto a lightning earth bus bar. Cables and cores containing the circuits to be protected shall not be looped or grouped together until the circuits subject to induced lightning energy have passed through the protection units.

Where two or more lightning protection units are mounted on the same DIN rail mounted earth bar, the earth cable shall be sized as follows:

- Cable length less than 6 meters - 10 mm2

- Cable length greater than 6 meters - 16 mm2

The whole assembly shall be mounted inside an insulated box, if not already mounted separately from other equipment, close to the chosen earth termination in order to achieve a short, straight connection.  Lightning protection units which are mounted in an enclosure supplied with an alternative current electrical power supply which utilize DIN rail mounted earth bars shall have the earth bars insulated by means of a proprietary stand off, or the DIN rail insulated in an approved manner from the electrical power earth or any earthed conducting surface.

The route for the earth conductor system shall be as far away as possible from the vicinity of signal and instrument cables. The cable run shall be straight, but any bends that are necessary shall have a long radius.

The earth termination and the method of connection shall be subject to the approval of the Engineer.

### Lightning Protection for Control and Instrumentation

The Contractor shall provide lightening and surge protection devices at each PLC on each communications circuit, base station and at all other parts of the radio network to ensure isolation and automatic resetting of the system being subject to high surge currents.

Lightning protection shall be selected to provide the highest degree of protection possible.

LPUs shall be earthed to the nearest earth reference bar, as direct as possible without inductive loops by a single unjointed cable.

The earth conductor shall be copper it’s route shall be as short and direct as possible and, in any case, no longer than 10 meters.

## Cables and Wires

Cables and wires shall be supplied by an approved manufacturer and where possible the same manufacturer shall be used for all cables and wires. Each drum or coil of cable shall be accompanied by a certificate stating the manufacturer's name, rating of cable, result and date of tests.

All cables shall be delivered with cable ends effectively sealed. When a cable is cut from a drum both ends shall be immediately sealed to prevent ingress of moisture. Cables shall not be transported to site in loose coils, but a number of short lengths of cable may be transported either on the same drum or pallet, effectively fixed and mechanically protected. The Contractor shall be wholly responsible for the purchase and/or hire costs of all cable drums.

The Contractor shall submit cable schedules for approval, detailing ratings, sizes, lengths, method of installation, and function of all individual cables. Cables manufactured more than 12 months before delivery will not be accepted.

Cables and wires shall be adequately rated for current carrying capacity under normal and short time fault conditions at the specified voltage, type of the signal and other relevant conditions. When assessing the rating and cross section of any cable or wire, the following factors shall be taken into account:

- Maximum voltage drop permissible;

- Type and magnitude of load;

- Fault level and duration related to circuit protection relays and fuses;

- Overcurrent setting of relays;

- Route length and disposition of cables;

- Ambient temperature;

- Method of laying;

- Mode of usage (power supply, instrument, signal, etc.)

### Cable Types

Cables complying with SRPS EN, IEC, or approved equivalent standards will be accepted provided that all cables which are supplied for a specific operating voltage are to the same national standard. Each cable shall be in accordance with a standard which relates to its application. Standards specified in the following clauses indicate the type of cables which may be used in the design.

If the Contractor wishes to use cables to an alternative standard then specified, details of current carrying capacity, derating factors, etc, shall be submitted to the Engineer for approval.

The following cables are acceptable:

#### High Voltage Power Cables

XLPE/SWA/PVC - semi-conducting conductor screen, cross linked polyethylene insulation, stranded copper conductors, core screen of semi-conducting compound, semi-conducting tape, and metallic layer, extruded PVC bedding, galvanised steel wire armoured, flame retardant red PVC sheathed overall, suitable for use on an earthed system of the voltage specified. Cables shall comply with the latest Standards.

#### Medium/Low Voltage Power Cables

- XLPE/SWA/PVC - cross linked low density, polyethylene insulated, stranded copper conductors, extruded PVC bedding, galvanised steel wire armoured, flame retardant black PVC sheathed overall, suitable for use on an earthed system at a rated voltage of 0.6/1kV or 1.9/3.3kV as specified.

- Conductor temperature shall not exceed 90oC for continuous operation and 250oC for short circuit. Cables shall comply with the latest Standards.

- PVC/SWA/PVC - PVC insulated, extruded PVC bedding, galvanised steel wire armoured, flame retardant black PVC sheathed overall, stranded copper conductors suitable for operation on a system at a rated voltage of 0.6/1kV. Conductor temperature shall not exceed 70oC for continuous operation. Cables shall comply with the latest Standards.

- XLPE/PVC - cross linked low density, polyethylene insulated, extruded PVC bedding, flame retardant PVC sheathed overall, stranded copper conductors suitable for operation on a system at a rated voltage of 0.6/1kV. Maximum conductor temperature shall not exceed 90oC. Cables shall comply with the latest Standards stranded copper conductors,

- PVC/PVC - PVC insulated, extruded PVC bedding, flame retardant PVC sheathed overall, stranded copper conductors suitable for operation on a system at a rated voltage of 0.6/1kV. Maximum conductor temperature shall not exceed 70oC. Cables shall comply with the latest Standards.

- PVC - PVC insulated, single core copper conductor rated at 450/750 V. Insulation shall be phase coloured. Conductor temperature shall not exceed 70oC for continuous operation. Cables shall comply with the latest Standards.

#### Submersible Borehole Pump Cables (Low voltage)

PVC/PVC - PVC insulated, PVC sheathed overall, stranded copper conductors suitable for operation on a system at a rated voltage of 0.6/1kV. The cables shall be four core, 3 phase and earth without any armouring wires or screen. The cable format shall be either circular or flat.

#### Flexible Cables and Cords

General purpose-PVC insulated stranded copper conductors white PVC sheathed overall, rated at 300/500V in accordance with the latest Standards.

#### Instrumentation and Control Cables

Analogue signal cables shall be PVC or polyethylene insulated, twisted pair laid with individual or collective screen, tape bound with extruded PVC bedding, galvanised steel wire armouring (if method of lying requires) and overall PVC sheath. Conductors shall be multistrand copper, 24/0.2mm (0.75 mm²) or as specified. Solid cores could be permitted on non moving (vibrating) places. The cables shall be rated at 300/500V and shall comply with the latest Standards.

Multi-conductor cable shall be used for the following signals between field-mounted junction boxes and the control panels. Different electronic signals shall not run in the same multi-conductor cable, except the cables for alarms and interlocking signals:

- 20mA DC;

- EMF of thermocouples and thermoresistors; On-off contacts;

- Solenoid valves.

Cables with a collective screen are permitted for use where the signal is a high level carrier (eg. 4-20mA dc) and the route length is not greater than 60 m.

It is also acceptable to use polyethylene insulated and sheathed telephone subscriber cable, aluminum tape screened, with solid copper conductors 0.8 mm dia (4 insulated conductors twisted to star quad), applied in local network lines for subscriber and junction circuits, for under ground installation. The cable shall be of reinforced construction of a laminated AL sheaths.

Permissible temperature range in operational conditions shall be - 30 up to + 50° C. The highest effective voltage shall be at least 150 V a.c. and 210 Vd.c.

Digital signal and control cables, where the signal is based on a supply not greater than 24V dc and the maximum ON-state loop current does not exceed 20mA, then analogue type cables can be used. Where the voltage and/or current exceeds these limits the signal cables shall comply with the specification for Low Voltage Cables.

Following cables shall be connected directly from field instruments to the control panels without junction box:

- Power supply;

- Pulse signal.

#### Fiber optic cables

The ring and dedicated lines shall be made by optic cable delivered on site and stored in the Employer’s warehouse. All bulk materials and tools necessary for cable laying (as for example plastic tube), connection, fixing shall supply the Contractor.

Fiber optic cables shall be laid and installed in accordance with the Manual for Fiber Optic Cable Laying and Installation, published in the PTT, Serbia, Edition No. 4/89 and 33/91.

### Cable Labeling

At each end of each cable, in a uniform and visible position a label shall be fixed on the cable to indicate the cable reference. The reference, in form of cable list, have to indicate the site cable number and route, and the number and size of conductors. Labels shall be made of brass, aluminum, lead or some artificial, long durance and atmosphere and sunlight resistance material, engraved and retained by suitable nonrusting or non-corroding binding strip passing through two fixing holes, one at either end of the label. If the cable gland is not visible, then the label shall be fixed inside the panel.

Power cable cores shall be identified by the latest Standard colours and codes. Control cable cores, shall be identified either by numbers or colours, what is applicable for the cable applied.

On rotating consumers, where, to achieve the required direction of rotation it is not possible to connect the phase cores to the appropriately identified terminals, additional core ferrules shall be fitted to identify each core with the terminal to which it is finally connected.

Control cables shall have individual cores identified by means of suitable permanent ferrules bearing the same number as terminal connected.

Core identification shall occur at every point of termination using an approved system of ferrule markers. The size of the ferrule markers shall be such as to match the overall diameter of conductor plus insulation. Numbering shall read from the termination outwards on all cores.

Terminals shall bear permanent identification as follows:

- Power terminations 	- colour, number or letter

- Control terminations - letter or number or both

## Cable Installation

Non-sheathed single insulated wire shall only be installed in galvanised steel conduit or trunking. Cables with sheaths but without any form of armouring shall only be installed in protected indoor locations such as floor ducts, conduits, or covered cables trays and ladders.

Cables with underground quality PVC sheaths or steel wire armouring may be installed in all locations including being direct buried in the ground, pulled into underground ducts or clipped direct to a surface or uncovered cable tray.

Single core cables shall not be used unless absolutely necessary (eg. feeder cables from transformers to switchboards). Where the installation method requires armouring this shall be of the non-magnetic type formed from hard drawn aluminium strip or wire. No single core cables shall be direct buried in the ground.

Where cables are run together in the same tray, trench or conduit they shall be suitably derated or spaced to maintain current rating. Crossovers shall be avoided where possible. Large power cables (eg. those carrying in excess of 50A), and signal cables shall be run separately to minimise interference.

Where a number of cables are terminated in equipment, they shall finally approach the equipment from a common direction. Top and bottom entry methods shall not be mixed in the same panel.

Cables shall be complete with all saddles, cleats, hangers, brackets, trays, ladders, ties, nuts, bolts, screws, washers, packing, ducts, sand, concrete covers, marker tape and route marker posts as may be necessary to complete the installation.

Marker tape shall be placed in the ground above cables laid underground either direct buried or in ducts. The tape shall be shall be in accordance to the Regulations of the Project Country.

All cables of less than a complete drum length shall be installed without joints, except where approved by the Engineer.

Unless unavoidable, cables shall not be installed in areas of direct sunlight. Where it is necessary, sunshields constructed to the approval of the Engineer shall be supplied and installed, or covered cable trays are to be applied.

### Submissions by the Contractor

The Contractor shall make submissions in relation to the cable installation including, where relevant, the following:

Block diagrams to show control cabling systems with each cable and terminal equipment being identified as in the cable schedules.

Cable route and layout drawings. For those items which are underground these drawings shall include the following:

- Route plans for all cables, cable ducts, and cable trenches;

- Sectional views of all cable ducts, trenches etc. for each different section throughout the route;

- The position of all marker posts, joints, drawpits etc

Route plans and section views for all cable trays and cable runs.

Cable schedules, which shall detail the cable number, type, voltage, size, route, length, and number of cores. Control cable schedules shall detail the connected and spare core numbers, diagram numbers of connected equipment, core ferrule and terminal reference numbers.

A manufacturer catalogues and data sheets for all cables and fittings.

Cable sizing calculations

Test certificates for all witnessed and routine tests carried out at the manufacturer's works and at site.

### Installation Direct in the Ground

Power cables of rated voltage up to 1000V shall be buried in accordance to the Regulations of the Project Country.

The bottom of excavated trenches shall be free of sharp stones and other obstacles and shall be covered with sand or fine sifted soil compacted to a depth of 70mm.

Cables shall be unrolled from the drums in such a manner as to avoid loops and kinks, and care shall be taken when laying or pulling into ducts to avoid damage to the outer sheath by drawing over sharp obstacles, edges, or stones. Cables pulled in either by machine or by hand shall be pulled in using rollers to prevent contact between the cable and the ground. Cables shall be snaked into the trenches to avoid tension in the cables during backfilling or from subsequent settlement. After laying, cables shall be covered to a minimum depth of 100mm of compacted sand or sifted soil

Where cables of different voltages are laid together at the same depth, vertical cable tiles, or bricks shall be used to segregate the cables.

Control, instrumentation and communication cables shall be laid not closer than 1000mm to high voltage cables.

### Installation in Underground Ducts

Underground ducts shall be performed in accordance to the Regulations of the Project Country, and shall be constructed of impact resistant uPVC ducts. At road crossings, uPVC ducts of minimum diameter 100mm shall be laid at a minimum depth of 1000mm (to the duct centre). The duct shall be surrounded by not less than 100mm of concrete on all sides and adapted to road load capacity

When installing cables in ducts the following measures shall be observed:

- cables shall be pulled in a straight line;

- rollers shall be positioned at the ends of the ducts both at the drawing in and drawing out points over which the cables are to be drawn;

- uPVC ducts and cables sheaths shall be coated with an approved lubricant;

- the maximum distance between draw-pits shall be the guaranteed minimum length of cable on each drum, making allowance for jointing;

- adequate space shall be allowed in each draw-pit for the installation and jointing of cables;

- the pulling rope shall be guided by rollers;

- only one large cable shall be drawn into each duct;

- where more than one small cable is to be pulled into the duct, all cables shall be pulled in simultaneously.

Whenever a duct is laid in the ground, a draw wire or man-made fibre rope shall be pulled in with at least 1000mm excess length left at each end.

### Sealing Cable Entries into Buildings

Where cables pass in or out of duct entries into or within buildings, these entries together with any spare ducts shall be effectively sealed against the ingress of moisture. The sealing material shall have a fire resistance of not less than 30 minutes.

### Marking of Underground Cables

The location of all underground cables shall be identified by:

- engraved plates fixed to the exterior surface of the walls of buildings 300mm above ground level, directly above the point where cables pass through the wall;

- marker posts on road verges, etc. at intervals of not more than 100m and at all junctions and changes of direction along the route;

- marker posts at 10m intervals within an enclosed site and at all junctions and changes of direction along the route.

Marker posts shall be of concrete, not less than 200mm high and shall have an enamelled metal plate affixed giving the details of the cable below including the depth and voltage rating. A drawing or sample of a typical marker post shall be submitted to the Engineer for approval.

### Installation in Cable (Bus) Trunking

Cable trunking shall be manufactured from hot dip galvanised mild steel of thickness not less than 1.25 mm. The trunking shall have two return flanges for rigidity. Where is necessary, an additional strengthening straps shall be fitted internally. The cover shall overlap the trunking and be made of the same gauge steel. All bends, tees and intersections shall be of the gusset type and shall, wherever possible, be purpose made by the manufacturer and of a matching design to the main trunking. Retaining straps shall be fitted to hold cables within the trunking when the cover is removed. Barriers formed from continuous sheet steel with the bottom edge welded to the trunking shall be installed where it is necessary to segregate cables.

The size of the trunking shall be adequate for the number of cables to be installed together with 50% spare capacity. Trunking shall have minimum dimensions of 50mm x 50mm.

Internal connecting sleeves shall be fitted across joints in the trunking and earth continuity ensured by bonding each section of trunking to a continuous earth wire.

Non-flammable fire barriers shall be inserted where the trunking passes through walls or floors.

Conduit connections to trunking shall be made by flanged couplers and internal brass bushes.

Trunking shall be supported at intervals not greater than 2m horizontally or 2.5m vertically.

Crossings over expansion joints shall be made in flexible conduit.

Whenever trunking is cut or drilled bare sections shall immediately be given a coat of zinc rich cold galvanising paint.

Cable and trunking runs shall be determined by the Contractor and agreed with the Engineer before any work is started. A clearance of not less than 150mm shall be maintained between the trunking and plumbing or mechanical services.

Trunking systems erected outside a building shall be weatherproof.

### Installation in Troughs and Trenches

Where the building structure incorporates purpose built covered trench systems, power distribution cables may be laid on the floor of the trench. Control and instrumentation cables shall be segregated and installed on cable trays or ladders fixed to the walls of the trench.

Where the building structure incorporates general service trenches containing pipework, chemical lines and other services, all cabling shall be segregated from other services and run on cable tray or ladder fixed to the trench walls. Crossovers shall be kept to a minimum and cabling shall be taken above wet service pipework.

### Cable Trays and Ladders

Cable trays and ladders shall be of hot dip galvanised perforated steel of thickness not less than 1mm for trays up to 100mm width, not less than 1.25mm for trays from 100mm to 150mm width, and not less than 1.5mm for trays from 150mm to 300mm width. Cable trays and supports shall be manufactured in accordance with the latest Standards.

Cable tray and ladder supports shall be of ample strength to maintain rigid support to the fully laden cable tray along its entire length. All brackets and traywork shall be suitable for withstanding the normal weight of the cables fixed to it plus a temporary weight of 125kg.

Wherever possible, cable trays shall be installed in full lengths without cutting. Where tray is cut or drilled the bared sections shall be dressed and immediately given a coat of zinc-rich cold galvanising paint. Similarly for PVC coated trays, the bared sections shall be immediately sprayed using a PVC aerosol.

### Installation in Buildings

Cables to be run on walls, ceilings, or other structures shall be supported on trays or ladder racks, or enclosed in conduit or trunking. All cables shall be neatly run vertically or horizontally parallel to adjacent walls, beams or other structural members.

Cable hangers, cleats, saddles, brackets and similar supporting devices shall be of an approved type and of adequate strength for the cables they are supporting. They shall be treated to withstand site conditions without corroding. Self locking plastic buckle clips and strapping shall not be used.

When installing fiber optic cable in buildings, spare lengths are necessary either in the shaft or in sections designated for spare lengths or in the room with telecommunication equipment.

## Cable Installation in Conduits

Conduits shall be either galvanised heavy gauge steel screwed type or light-gauge steel non-screwed type, steel or PVC. Accessories shall either be malleable cast iron or pressed steel.

A space factor of 40% shall not be exceeded, and conduit of less than 20mm diameter shall not be used. Tubing is to be perfectly smooth inside and out and free from imperfections. Both ends of every length of tubing shall be reamed and all sharp edges removed before erection.

Where conduits converge, adaptor boxes shall be used. Conduits shall be connected by means of male brass bushes and couplings. Where conduits are greater than 25mm, straight through joint boxes shall be of the trough type. Where conduit or fittings are attached to equipment casings, the material of the casing shall be tapped for a depth of not less than 10mm or male bushes and flanged couplings may be used.

Hexagonal lock nuts shall be used at running joints and shall seat firmly and evenly onto mating faces. Lock nuts shall not be used at non-running joints.

All junction boxes, draw-in boxes, and inspection fittings shall be placed so that the cables can be inspected, withdrawn and re-wired during the life of the installation.

Generally, not more than two bends or offsets or one coupling will be permitted without a suitable inspection accessory. Fish wires shall not be left in conduits during erection. The whole of the installation shall be arranged for a loop-in type of system with joints being carried out at switches, isolators or appliance fittings.

Ends of conduits which are liable to be left open for any length of time during building operations shall be plugged to prevent the ingress of dirt and covers shall be fitted on all boxes.

Generally, conduits shall not cross expansion joints of buildings. Where they cannot be installed in any other manner, a galvanised flexible conduit shall be used across the expansion joint. A total of 150mm movement shall be allowed.

### Surface Installation

Surface conduits shall be secured and fixed by means of distance spacing saddles or clips which allow the conduits to be taken directly into accessories without sets or bends. Conduits shall be run in a square and symmetrical manner. Runs shall be properly ventilated and allow for drainage of condensation. All surface conduit runs shall be marked out for approval by the Engineer before the installation is carried out. Where large multiple parallel conduit runs occur, galvanised trunking may be used instead.

Conduits installed on structural steelwork shall be secured by girder clips, drilled and tapped to the metalwork. Power driven fixings shall be used only with the approval of the Engineer. Any drilling or access which is required through any structural member of the building shall be agreed with the Engineer before carrying out the work.

Exposed threads and plates where galvanising has been damaged shall be cleaned and then painted with two coats of an approved metallic zinc based paint. This treatment shall be applied as the work proceeds.

### Concealed Installation

Concealed conduits shall be securely fixed to prevent movement before laying of screed, floating of plaster, casting of columns or other building operations necessary after the conduit installation. Crampets or similar fixings shall be used for attaching the conduit to blockwork, etc. Building nails will not be accepted.

At least 15mm shall be allowed for finishes over the conduit. Where this cover cannot be maintained then expanded metal shall be fitted over the conduit. Conduit cast into reinforced concrete floors shall be fixed to the steel reinforcing. Concrete shall be prevented from entering conduit boxes when being poured. Where possible, the conduit boxes shall be fixed to shuttering to give a flush finish.

Conduit installed in voids, false ceilings, and other concealed routes shall be installed as specified for surface conduits. Draw-in wires shall not be pulled into the conduits during erection. Wiring shall be carried out after the false ceiling or permanent ducts have been completed. Conduit installed in floors shall be sealed against ingress of moisture.

The conduit installation shall be inspected by the Engineer before the building operation conceals the work.

### Flexible Conduits

Flexible conduit shall be of the waterproof galvanised type of PVC wire-wound type with cadmium plated mild steel couplings. Lengths of flexible conduit shall be sufficient to permit withdrawal, adjustment or movement of the equipment to which it is attached and shall have a minimum length of

300mm. Flexible conduit shall not be used as a means of providing earth continuity. A single earth conductor of adequate size shall be installed external to the conduit complete with earth terminations. Where conversion from rigid conduit to flexible metallic conduit is to be made, the rigid conduit shall terminate in a trough type box. The flexible conduit shall extend from this box to the equipment; the earth continuity cable shall be secured to the box and to the piece of equipment. The use of lid facing screws, etc. will not be permitted. Adaptors shall incorporate a grub screw or a gland to prevent the flexible conduit becoming loose.

### PVC Conduits

Where galvanised conduit is liable to corrosion, PVC conduit shall be installed. PVC conduit shall be of the round high impact non-flame propagating type as specified and self extinguishing. Surface and concealed installations shall be generally as described for steel conduit. PVC conduit fittings shall all be white unless specified otherwise.

Jointing shall be carried out using PVC socketed accessories. Expansion couplers shall be fitted in straight surface runs every 12m. The free end shall be sealed with non-setting mastic to form a waterproof seal.

Purpose made bends may be used providing that the cable bending radius is maintained. Cracked or crinkled conduit will be rejected.

The conduit shall be suitable for use in ambient temperatures of between -5oC and 60oC and shall not be installed in areas that receive direct sunlight. A separate protective conductor (earth continuity conductor) shall be installed.

Adaptable boxes and accessories shall be made from heat resistant insulating material. The minimum wall thickness of boxes having a nominal internal depth of 16mm or less shall be 1.5mm. For deeper boxes the minimum wall thickness shall be 1.5mm. For deeper boxes the minimum wall thickness shall be 2mm. All boxes which are intended to support luminaries or other heat sources shall have either external fixing lugs riveted to the metal fixing inserts or utilise steel insert clips.

Poly-ethylene conduits of 40 mm diameter shall be used for the fiber optic cables. Conduit shall be laid in area in new or existing building and infrastructure. The underground gallery and concrete channel should be used. In passable underground gallery the cable could be installed on new cable trays used only for fiber optic cables

## Cable Terminations and Joints

### Power Cable Terminations

Power cables shall be terminated in suitable boxes arranged for bolting to switchgear, motor starters and motors. Each cable entry into a terminal box shall be made through a suitable gland.

Boxes shall be of adequate proportions to accommodate all cable fittings including stress cones or other means of insulation grading. Boxes shall be openable for inspection without disturbing the gland plate, cable or termination.

Where air insulated terminations are used, the cable crutch shall be protected by a heat-shrink trifurcating sleeve.

Cores shall have either crimped lugs or sleeves to match either post terminals or bolted clamp terminals. Glands for armoured cables shall provide a positive armour clamp to the box or switchgear coating. This clamp shall completely support the cable weight so that no tension is applied to the termination. The clamp shall also provide earth continuity and be of adequate size to withstand the full fault current of the system for one second.

Where single core glands are required, these shall be non-magnetic. The gland plate shall also be of a non-magnetic material. Removable connections for bonding across the gland insulation shall be provided. The gland insulation shall withstand a test of 2 kVac for one minute.

Glands shall seal the inner and outer cable sheaths against ingress or dirt and moisture and provide mechanical support.

Where cable glands are exposed to the weather these shall be protected by heat shrink or purpose moulded sleeves covering the gland continuously from the cable sheath to the gland neck.

Where the apparatus enclosure classification requires sealed cable gland entries, sealing shall be achieved by using threaded cable gland holes and polytetrafluoroethylene (PTFE) tape.

### Multicore or Control Cable Terminations

A sufficient number of terminals shall be provided to terminate all cable cores. For control and auxiliary wiring an additional 20% of this number shall be provided as spares.

Terminal blocks for terminating up to and including 35mm² cables shall securely clamp the conductor, without damage, between two plates by means of a captive screw; pinch screw type terminal blocks shall not be used.

For cables above 35mm², stud or bolted terminals shall be used, each cable core being fitted with a suitable lug.

Not more than one core of internal or external wiring shall be connected on any one terminal. Where duplication of terminal blocks is necessary, purpose made solid links shall be incorporated in the design of the terminal blocks.

Terminals which remain energized when the main equipment is isolated shall be suitably screened and labeled.

Terminal blocks for different voltages or circuit type shall be segregated into groups and distinctively labeled.

Plant which has to be dismantled for maintenance shall have multicore cable terminations made of through glands onto an adaptable box. The box shall have terminal blocks, and connections shall be made to the equipment by single core wires and flexible waterproof plastic conduit. A separate earth core shall link the box to the equipment.

### Fiber Optic Cable Termination Boxes

In stations with data terminal equipment, fiber optic cables are terminated in optical termination boxes, because of cable testing, easier maintenance and reconnecting spare fibers to different directions. Phase one is cable introduction in the cabinet, arranging the fibers in connection points and cable jacket termination, and phase two is connection to pigtail.

### Joints

Through joints shall only be allowed on long cable runs outside buildings. Where such joints are necessary in thermoplastic and elastomeric cables, the cables shall be jointed with epoxy or acrylic resin cold setting compound, which has been premeasured and prepacked ready for use. The boxes shall be of split, moulded plastic type with filling vents for compound. Bonding straps shall be fitted with armour clamps across the joint and inspected by the Engineer prior to filling the box with compound. Wrapped pressure type joints will not be accepted.

Conductor cores shall be jointed number to number or colour to colour.

## Small Power and Lighting Installations

### Distribution Boards

Distribution boards shall be of folded sheet steel enclosed construction, braced to form a rigid structure. Doors shall be lockable, hinged and gasketted to give a damp and dust proof enclosure. The degree of protection shall be IP 43 (indoors) and IP 55 (outdoors).

The busbars shall be mounted on non-hygroscopic insulators, completely shrouded or PVC insulated, coloured to denote the appropriate phase. The current rating of the busbars shall be not less than the sum of the maximum current rating of all outgoing circuits. A neutral bar shall be provided with a separate terminal for each circuit.

A separate earth terminal block shall be provided with a separate terminal for each circuit. Distribution boards shall have a fault rating at least that of the system for one second. Removable top and bottom undrilled gland plates shall be provided with a brass earthing stud.

A switchfuse or isolator shall be connected on the incoming side of the board. The device shall be triple pole and neutral with overcurrent protection.

Each outgoing circuit including spare ways shall be protected by a HRC fuse or miniature circuit breaker (MCB). HRC fuse bases and carriers shall be of non-hygroscopic insulation.

Barriers shall be fitted over all live parts and spaces between phases. Each distribution board shall have a permanent circuit identification chart mounted on the inside of the front door.

Boards for use on dc systems shall be double pole types with fuses on the incomer.

### Bulk Switching Contactors

Bulk switching contactors (eg for large lighting or heating loads controlled from a single switch) shall be of the air break electromagnetic type. The contactors shall be continuously rated for the duty specified, shall have a utilisation category AC1, and an intermittent duty class 0.3 with the characteristic mechanical endurance of that class. The current ratings specified shall be eight hour rated duty.

Contactors shall be single or triple pole as required, each type with a neutral terminal. Contactors shall be fitted with a continuously rated operating coil having both terminals brought out.

Enclosures shall be similar to those of distribution boards and shall have a degree of protection not less than IP 52.

### Socket Outlets

Domestic pattern socket outlets shall be “Schucco type” and shall comply with the latest Standards. Industrial pattern socket outlets shall comply with the latest Standards.

In areas having plaster, tiled or other decorative finish, socket outlets shall be fitted flush with the finished area. In all other areas fittings shall, unless otherwise specified, be surface mounted.

### Lighting Switches

Internal lighting switches shall be supplied complete with box, cover plate and fixing screws. They shall be surface or walled in mounted.

At multi-switch positions, switches shall be contained in multi-gang boxes.

External lighting switches shall be of IP55 protection and surface mounted.

### Internal Lighting

Luminaries shall be complete with all supports, suspensions, flexible cables, pendants and plugs. They shall be connected to the main circuit wiring with heat resisting flexible cables of a minimum core size of 1,5mm2. Protective classification shall be IP 42.

The earthing of all luminaries shall be by a separate core in the connecting flex or cable, securely bonding the earth terminal on the fitting to that of the interconnecting cables.

Where adjacent luminaries are connected to different phases of the supply, a label shall be fitted internally, warning of the presence of the phase to phase voltage.

Luminaries shall not transmit load to suspended ceilings unless the ceiling and lighting is of integrated design with the appropriate supports.

Where high bay discharge luminaries are suspended from a structural ceiling, connections between the fitting and fixed wiring shall be by plug and socket.

Lamp holders for flexible pendants shall be of the all-insulated skirted pattern with cord grips.

The fixings, connection boxes and other parts of the luminaries shall be erected at times to suit the building programme. The glassware, diffusers, shades, lamps and tubes shall not be fitted until all building work is complete. Fittings shall be left clean inside and outside and ready for us.

## Types of Luminaries

### LED

It shall be applied at all places where permanent lighting is using, including external illumination, Central Control Room and other frequently used rooms

The luminaries shall comply with the latest Standards.

### External Luminaries

All external luminaries shall be of the totally enclosed fully weatherproof pattern with vandal-proof polycarbonate diffusers having a minimum degree of protection IP 55. Security lighting systems shall be designed to be inaccessible to intruders.

### Emergency Lighting

Emergency lighting luminaries shall be of the self-contained or slave type as specified. The luminaries shall be fully automatic in operation, providing instant illumination in the event of a mains failure. The battery capacity shall be sufficient to operate all luminaries connected to the emergency lighting system for a period of 3 hours.

## Lamps

All lamp holders shall be fitted with a lamp of a type and size specified by the manufacturer or as stated on the drawings.

### LED Lamps

LED lamps shall comply with the latest Standards. Unless otherwise specified, lamps shall be coloured 'white' for industrial use and 'warm white' for commercial and domestic lighting. The guaranteed minimum life shall be not less than 50.000 hours.

### Low and Extra Low Voltage Supply Transformers

Low and extra low voltage supply transformers shall comply with the latest Standards and shall, unless otherwise specified, be of the single phase type. Transformers shall be supplied complete with fixing bracket. The rated output voltage and VA shall be as specified.

### Electric Hand-lamps

Electric hand-lamps shall be suitable for 25V operational and shall be complete with specified length of TRS flexible cable, lamp and galvanised wire guard. Electric hand lamps shall comply with the latest Standards. The hand lamp cable shall, unless otherwise specified, be terminated in a plug complying with the latest Standards.

When used with a portable supply transformer, the cable may be permanently connected to the output terminals via a suitable compression gland.

The hand-lamp shall be complete with a reeling drum or wall brackets or both for the neat storage of the cable when not in use.

## Batteries and Chargers

Battery units shall comprise a floor standing or wall mounted front access type steel cabinet accommodating batteries, battery charger and distribution facilities.

### Batteries

Unless otherwise specified, batteries shall be of the high performance nickel-cadmium, or some similar, up to date technology type having cells housed in translucent, high impact plastic containers. The containers shall be fitted with vented filler plugs. High and low electrolyte levels shall be permanently marked on the container.

Cell terminals shall be of the bolted type. The terminal polarity shall be permanently marked.

Battery cells shall be arranged so that each is accessible for test and inspection. Cells shall be located in the lower section of the cabinet and shall be not less than 300mm above floor level.

Batteries shall be supplied complete with all necessary connections. The connections between tiers, and cells and disconnection links and fuses shall be of the multi-stranded plastic insulated type. The nominal battery voltage shall be 24V unless technical considerations otherwise dictate. The battery capacity shall be adequate to supply all connected loads for a minimum period of 8 hours. At the end of the 8 hour period the battery shall have sufficient capacity to complete the operations listed below, at the end of which the battery voltage shall not have fallen below 90% of nominal value with the standing loads connected:

- two closing operations on all automatic circuit breakers;

- two tripping operations on all circuit breakers;

- charging of one dc motor wound circuit breaker closing spring.

Detailed calculations and loading data used to determine the battery capacity shall be submitted to the Engineer at an early stage in the Contract.

### Battery Charger

The battery charger shall be of the solid state design incorporating 'Float' and 'Boost' charging facilities. In the 'Float' charge mode, the charger shall automatically maintain the battery in a fully charged condition whilst supplying its rated current. In the 'Boost' charge mode the charger shall be capable of fully charging the battery from a fully discharged state in a period not exceeding 7 hours.

Boost mode is not required for standby batteries for fire detection, emergency lighting or intruder alarm systems.

The charger output voltage regulation shall not exceed ±2 % for load variations of 0 to 100 % with ac supply voltage variations of ±6 %. The charging characteristics shall minimise battery water loss.

The charger shall be equipped with the following:

- Incoming supply On/Off switch;

- Supply On indication;

- Output voltmeter;

- Output ammeter;

- Float/Boost charge selector switch;  Charger Failed alarm relay;

- Charger Failed indication.

The minimum requirement for the 'Charger Failed' alarm shall be the detection of ac supply or dc output failure. The alarm relay shall not operate under a transient a.c. supply failure condition. An individual pair of volt-free contacts for 'Charger Failed' shall be provided. The contact shall be wired to terminals.

## Generator Sets

### Engine Control

An Engine Control Panel shall be provided, this should be either fitted on the skid frame with the diesel generator, or floor standing or located either in the Engine Room or in an adjacent room. When a Main Switchboard is to be provided, the Engine Control Panel shall be incorporated within the Switchboard. Alternatively, a remote monitoring facility may be provided in the LV Switchboard.

The Engine Control panel shall include all controls for starting/stopping and protection of the diesel generator set. A selector switch shall be provided to enable the set to be started either manually or automatically.

In Auto mode, the diesel generator shall start, if the mains voltage in any phase falls below an adjustable set value for more than an adjustable set time. Tripping of the Mains and closing of the Generator ACB's shall be automatic. On restoration of the mains, the diesel generator shall continue to run and supply the works for an adjustable set time to ensure reliability of the mains. The engine shall then continue to run, unloaded, for an adjustable set time before shutting down.

The engine starting circuit shall be designed for three starting attempts each comprising 10 second cranking followed by a 10 second rest period.

In Hand mode, the starting and stopping of the diesel generator, the tripping of the Mains and closing of the Generator ACB's shall be carried out manually.

The following shall be provided:

- Electronic Voltage Regulator (this may be mounted within an enclosure local to the alternator); - Frequency Meter;

- Generator Voltmeter and selector switch;

- Generator Ammeter and selector switch;

- Engine Hours Run Meter;

- Low oil pressure shutdown, and indicator;

- High water temperature shutdown and indicator;

- Low water level shutdown and indicator;

- Engine fail to start indicator (3 attempts then lockout);

- Charger Fail/Low Battery Volts indicator;

- Under speed shutdown and indicator;

- Over speed shutdown and indicator;

- Generator undervolts shutdown and indicator;

- Generator overvolts shutdown and indicator;

- Generator underfrequency shutdown and indicator;

- Generator overfrequency shutdown and indicator;

- Set Isolated indicator;

- Fire valve operated indicator;

- Day Tank Low/Low Fuel level;

- Day Tank High/High Fuel level;

- Emergency stop operated indicator;

- Hand/Off/Auto selector switch;

- Emergency Stop pushbutton;

- Engine heater switch and indicator;

- Engine Stop/Start pushbuttons;

- Fuel Line Failure alarm;

- Day Tank and Bulk Tank bund filling alarms.

Where the Bulk Tank(s) are below ground or where indication local to the tank is not possible, then unless specified otherwise, a Bulk Tank Contents Indicator shall be provided on the Engine Control Panel.

In addition to the Engine Protection detailed above, Overcurrent, Short Circuit and Earth Fault protection shall be provided local to the set.  If the cables from the set to the Switchboard are short in length are armoured, and run within a building, then the protection may be provided on the Incoming circuit breaker at the Switchboard. Where cables run through, ducts between buildings, or from an external generator to the switchboard then local protection must be provided at the generator. The contractor must ensure that local protection will discriminate with protection fitted down stream.

The following alarms shall be marshalled to the Plant SCADA system. These shall be output individually, or grouped, as detailed below:

| - Diesel Generator Running - Generator ACB Closed - Mains ACB Closed - Fire Shut Off Valve operated - Day Tank Bund Filling - Engine Bund Filling | - Individual - Individual - Individual - Individual - Individual - Individual |
| --- | --- |
| - Diesel Generator Fault - Diesel Generator Isolated - Day Tank Low Low level - Day Tank High High level - Fuel Transfer Pump Fault - Battery System Failure | - Group 1 - Group 1 - Group 1 - Group 1 - Group 1 - Group 1 |

A fire detector shall be provided over the engine, and a Fire Push located adjacent to each door entry to the Engine Room. When either of these devices is operated, the fire valve in the fuel line from the Day Tank to the engine shall close. Two volt free contacts, which close when the fire system is activated, shall be wired to the Engine Control Panel. One being for output to telemetry and the other for output to the works fire alarm system.

### Emergency Power Generation

Emergency Power generator sets shall be designed to operate as Mains Fail sets. It shall be designed to operate in a “Stand Alone” mode on full power capacity.

The set shall start up, synchronise with the mains, and run on load, when a signal is received from PLC (SCADA system). A “Test” switch shall be provided on the LV Switchboard or the change-over panel. This switch shall be connected in parallel with the signal from the PLC or telemetry, such that when the switch is closed the set operates as detailed above. When this switch is opened the set shall stop, unless the PLC or telemetry has not called the set to run in the meantime.

Unless specified otherwise, Reverse Power protection shall be provided to prevent returning power into the mains.  The Reverse Power Relay shall be compatible with and must discriminate with the protection.  When “Stand Alone” is selected the set shall take up load and operate independently of the mains. The set shall continue to run until the PLC or Test switch change state and trip the Generator ACB and shutdown the engine.

### Preliminary Check, Service and Test Running

All works to generators shall be carried out by specialist plant fitters with experience of the particular type of plant. This work shall include a basic check on serviceability of the cooling system, fuel system, engine lubrication, and starting systems, alternator and control panel.

Any necessary minor adjustments and repairs shall be carried out together with filling of cooling and lubrication systems and provision of fuel for test running.

Batteries shall be provided on a temporary basis for test starting. The diesel engine shall be started up if possible and shall be run for the minimum time necessary to make an appraisal of the operating condition. Following the preliminary check, the Contractor shall submit a report to the Engineer on the condition of the unit including:

- General observations;

- Noise level from main components;

- Starting equipment;

- Running temperature;

- Fuel injection system;

- Control and safety systems;

- Instrumentation;

- Engine oil condition;

- Turbo charging system;

- Cooling system;

- Main bearings;

- Compression;

- Exhaust system;

- Battery charging system;

- Alternator output;

- Alternator controls;

- Alternator instrumentation.

### Stripping Down Checking and Scheduling of Overhaul Works

Where the Contractor instructed by the Engineer shall dismantle and check the condition of all main wearing components of the generator and submit a Report including a schedule of works and detailed quotation for a complete overhaul.

The Engineer may use the information in the Report to obtain competitive quotations at his discretion, and may instruct the Contractor to have the work carried out by a nominated subcontractor.

### Reconditioning/Overhaul

The Contractor shall provide all necessary materials and carry out overhaul works to generators as instructed by the Engineer. Works shall be carried out in accordance with the manufacturers’ maintenance manuals and shall include commissioning and test running on completion.

Commissioning shall include provision of all consumables, and testing of protective cut out devices, and instrumentation. Test running shall be carried out for a continuous period of 12 hours under load during which the generator output and engine running characteristics shall be monitored and recorded.

## Power Factor Correction Capacitors

One common automatic compensation device for overall Plant power factor correction to not less then cosfi 0.98 shall be provided. It shall work with at least 9 steps of PF regulations.

All capacitor circuits shall have three separate protection fuses or three phase CB and contactors declared for "capacitor duty".

A label shall be fitted on all capacitors warning that discharge resistances are fitted.

The capacitors shall comply with relevant latest Standards. Capacitors containing polychlorinated biphenyls will not be accepted.

## Cathodic Protection

### General

The pipelines shall be protected against underground corrosion by the cathodic polarization with the minimum value of the protective potential of – 0.3V, calculated in relation to the spontaneous pipeline potential.  The cathodic protection stations connected to low-voltage power supply shall be used as a source of the protective cathodic current. The locations of the cathodic protection stations shall be selected in accordance with the estimate for the required distribution of the protective potential along the pipeline and the possibility of power-supply from the low-voltage network.

The control-measuring posts for monitoring the protective potential on the pipeline shall be arranged by the Contractor at all characteristic points of the pipeline, taking care to arrange them in such a way so that the proper operation of the entire cathodic protection system can be checked.

Applicable Standards:

- SRPS EN 62305-1:2013 	Protection against lightning, General Principles.

- DIN 50900: 	 	Metal Corrosion

All weldings of the cables and the pipeline: station-pipeline, measuring and junction points -pipeline shall be carried out by the alumino-thermic welding process. The welded points are to be insulated with the bitumen mass. While welding the junctions of the cables to an object, the appropriate personal protective means have to be used (protective gloves, welding apron and glasses).

Potential at the drain point, measured in relation to the reference Cu/CuSO4 electrode shall be not less – 1.5 V (except in exceptional cases).  The potential at the remotest point of the pipeline relating to the drain point from any side of it, as well as relating to the Cu/CuSO4 electrode, shall be at least – 0.85 V.

### Installation of Control-measuring Outputs

The control-measuring outputs shall be installed by the Contractor while carrying out the works on laying down the pipeline. The outputs shall be welded, in accordance with the specifications and drawings, on the already ditch laid pipeline just before filling in the ditch.

According to standards, the outputs shall be done by the alumino-thermic welding of the cable to the pipeline.  In the case the outputs are welded to the working pipeline, the attention shall be paid to welding the output to the non-corroded part of the pipe.

In both cases, either a contact screw or a cable fixed directly to a mould installed on the cleaned pipe,  the junction shall be cleaned from slag and insulate in order to prevent the development of the accelerated corrosion on the contact of two metals. The cables welded to the pipeline shall be, by the shortest way, led to the control-measuring poles and connected to the particular clamps according to the schemes for individual types of control-measuring poles.

The control-measuring poles shall be manufactured by the specialized Subcontractor in accordance with the design. According to standards, the poles shall be installed just above the pipeline.

It is required to make earth leads, for the control-measuring outputs that are installed on the pipelines under the coverage of the long distance power line, to which supervoltage arresters, mounted in the measuring box of the pole, shall be connected.

### Cathodic Protection Station

The cathodic protection station shall be mounted by the Contractor on the concrete.  The station shall be completed with all the necessary devices and equipment. All connections shall be cable made and carried out from the bottom side of the station.

The stations with the automatic regulation of the protective potential shall be applied. Control probe shall be installed along with the station.  The control probe shall be a non-polar copper-copper sulfate stationary electrode and built-in at a distance of about 1.0 m from the protected pipeline by the drain post at a depth of 0.8 m.

The control probe shall be put at the side opposite to the anode bearing. The probe shall be laid in the ditch and fixed to the copper electrode, connected to the appropriate clamp in the drain pole, wherefrom it shall be connected with the regulation input of the cathodic protection station by a control cable.

After the completion works of the cathodic protection station, all junctions shall be to tested, to check the efficiency of the protection against the dangerous contact voltage.

### Anode Bearing

The material used for the anode bearing shall be iron in the form of steel profiles or rails, that is, ferrosilicon or graphite.  The inert anodes shall be laid by the Contractor in the padding layer made of coke powder sized 40 x 40 cm.  The bearing shall be conducted by excavating the ditch of the sizes marked in the drawings for the anode bearing.  The ditch shall be filled in and stamped with the dust coke layer 20 cm thick.

The anode cable, of NYY type, shall be attached to each anode.  The junction of the cable itself with the anode must be carefully performed and insulated, since its destruction causes the inefficacy of the whole anode.  The cables of the individual anodes shall be pulled out above the padding layer whereupon the ditch will be covered with the excavated earth.

It is required to put a pole of the anode bearing- the anode pole in the middle or at the end of the anode bearing, at an accessible position, preferably near a road.  All the cables from the individual anodes and the anode cable from the cathodic protection station shall be led to the pole. The interconnecting of the anode cable with the anodes shall be carried out in the pole, on the clamps.  The control of each individual anode shall be enabled, without excavating, as well as the possibility of laying new anodes, if the resistance of the anode bearing increases and disturbs the voltage regulation scope of the cathodic protection station.

Upon the completion of the works, on the anode bearing, it shall be required to outline the exact position of the anodes in the bearing in relation to the anode pole, to designate the cables from the individual anodes in the anode pole in order to make it clear which cable belongs to each anode.

## Video Surveillance

### General

Video surveillance´s cameras shall be of outdoor construction, purpose made, for both, indoor and outdoor application, with two separate image sensors for day and night-time operation, automatic day/night switching and integrated video recording. Some of cameras must be with Ex protection.

They shall be with permanently fixed lenses at factory for extremely simple installation and digital continuous zoom, pan and tilt.

The cameras shall be robust, low-maintenance, with concealed cable duct, weatherproof from -30° to +60°C, without need for heating (IP65) and integrated microphone, speaker and PIR motion detector. It is necessary to integrate video surveillance with access control and fire alarm system.

### Technical Specification

Technical specification for camera

| Lenses | 22 to 135 mm format, horizontal angle 90° to 15° |
| --- | --- |
| Sensitivity | Day Color: 1 lux (t=1/60 s), 0,05 lux (t=1/1 s) Night B/W: 0,1 lux (t=1/60 s), 0,005 lux (t=1/1 s) |
| Max. image resolution | Color: 2048x1536 (3Mega), Black/White: 1280x960 (Mega) |
| Max. frame rate (M-JPEG) | VGA: 16 fps, TV-PAL: 12 fps, Mega: 6 fps, 3Mega: 4 fps |
| Internal DVR | SD card (up to 32 GB) |
| Image processing | Backlight compensation, automatic white balance, image distortion correction, video sensor (motion detection) |
| Alarm/Events | Triggering of events by integrated multiple-window motion detection, external signal, temperature sensor, notification over email, FTP, IPTelephony (VoIP, SIP), visual/acoustic alarm Pre- and post-alarm images |
| Interfaces | Ethernet 10/100, ISDN, RS232, 1 x In, 1 x Out (electrically separated from power supply) |
| Security | User-/Group management, HTTPS/SSL, IP address filter, IEEE 802.1x, Intrusion Detection |
| Power supply | Over Ethernet (IEE 802.3af; Class 0), Netpower-Adapter, typ. 4 W |
| Operating conditions | IP65 (DIN EN 60529), -30° to +60 °C |
| Video-Management-Software | available for Microsoft Windows, MacOS X, and Linux/UNIX operating systems, free download version |

Technical specification for Network Video Recorder (NVR)

- 64 NVR channel

- HDD (64TB) RAID 5 or RAID 6

- 8 MP resolution

- H.265/ H.264+/H.264 compression

- 2 USB port;

- alarm input/1 output; 1 audio input/ 1 output; 1Gbit LAN;

- Rackmount 19";

- HDMI/VGA.

## Fire Alarm System (FAS)

### General

The installation of fire alarm system shall cover all the premises of the object, depending on the level of fire danger it is provided manually reporting the occurrence of fire.

All detectors, individually addressable, tied in the loops, shall be connected to the fire alarm panel.

Distribution cabinet in object shall be connected to the fire control panel or console in gatehouse building.

Fire alarm panel in administration building shall be connected to the parallel fire alarm display in gatehouse building.

Fire alarm is signaling on fire alarm panel, which shall be provided in the administration building, and intervention measures are follow from there.

Fire alarm panel and parallel fire alarm display shall perform permanent control of situation and the correctness of electrical installations, receive and process alarms from lines, commands the corresponding signaling and the effects on other installations in accordance with the requirements of the project for fire protection

Fire alarm panel shall be powered by a 230V, 50Hz with a separate circuit from the power distribution cabinet.

In case of failure of the voltage it shall has back-up power - accumulator batteries which provide autonomy of 72 hours in steady mode and 30 min. in alarm mode.

Installation of fire alarm shall consist of  automatic optical fire detectors, automatic optical fire detectors in Ex protection, automatic heat fire detectors, automatic heat fire detectors in Ex protection, automatic optical-heat fire detectors, automatic optical-heat fire detectors in Ex protection, automatic optical-heat-CO fire detectors, automatic flame detectors, automatic flame detectors in Ex protection, automatic flame detectors for outdoor open space in Ex protection for distances at least 50m, automatic flame detectors for outdoor open space in Ex protection for coverage at least 50m distances, automatic flame detectors with analog camera for outdoor open space in Ex protection for coverage at least 50m distances, manual call points, manual call points in Ex protection, alarm sounders, alarm sounder in Ex protection, alarm horns in Ex protection, single input-output modules, single input-output modules in Ex protection, galvanic isolators, Zener barriers, linear optical detectors, linear heat detectors in Ex protection, fire alarm panel with 4 loops and fire parallel display.

All detectors shall be connected by the principle of input - output without continuing cables.

These models of automatic fire detectors are available:

- Addressable smoke detectors with base,

- Addressable smoke detectors with base in Ex protection,

- Addressable heat detectors with base,

- Addressable heat detectors with base in Ex protection,

- Addressable smoke-heat detectors with base,

- Addressable smoke-heat detectors with base in Ex protection,

- Addressable smoke-heat-CO detectors with base,

- Addressable flame detectors with base,

- Addressable flame detectors with base in Ex protection,

- Addressable flame detectors for outdoor open space in Ex protection,

- Addressable flame detectors with analog camera for outdoor open space in Ex protection,

- Conventional linear optical detectors,

- Conventional linear heat detectors in Ex protection.

Manual call point shall be provided on evacuation routes and near the exit from the buildings.

All manual call points, bases and input-output modules shall possess isolating switches which in the case of a short circuit or an open line ensures the smooth running of the system.

All alarm sounders and horns shall be conventional.

Fire alarm panel shall have maximal capacity for 4 loops for addressable devices with touch-screen display with possibility to use it with firefighter’s gloves, activation with key, password and RFID tag, possibility to connect through MODBUS and BACNET protocols with SCADA and history with 10000 events.

### Technical specification for Installations

Installation is performed with telephone "halogen free" cables, similar to the type

JH (St) H 2x2x0,8 mm,

JH (St) H 2x2x0,8 mm FE180 / E30,

NHXHX 3x2.5 mm2 FE180 / E30.

The cables are routed through a "halogen free" plastic pipes laid under plaster, by clamps, lay on the shelves.

In places changes of direction and branching installations shall be planned junction boxes 100x100 mm and Ø 78 mm.

Connection between distributions cabinets shall be carried out with similar type of cables TK 59GM 3x4x0,8 mm and PPOO-Y 3x2.5 mm2, that routed in the cable ducts.

Executive functions of fire alarm panel

Fire alarm panel formed the impulse for:

- Activating the alarm sounders, horns and modules.

  - Access Control System with Time Attendance System

    - General

The installation of access control system shall cover all the premises of the object, depending on the level of security it is provided.

All door controllers must be with keypad and card readers and need to be connected to the security switch in the administration building, where it is access controller server located. Door controllers shall be with user friendly touch-screen display. Communication between door controllers and security switch shall be through IP protocol. All door controller with card readers shall have PIR detector included.

Client computer shall be in gatehouse building and in the access control software shall be integrated video surveillance system and Fire Alarm System.

Separate door controllers with keypad and card readers shall be applied for the time attendance system and will have independent software.

Installation of access control shall consists of server, client computer, door controllers with keypad and card reader, magnetic cards with AES 128 encryption, electromagnetic locks with magnetic contacts, emergency exit buttons and software for integration access control with video surveillance and fire alarm.

In case of failure of the voltage it shall has back-up power - accumulator batteries which provide autonomy of 24 hours in steady mode and 30 min. in alarm mode.

    - Technical specification for Installations

Installation is performed with "halogen free" cables, similar to the type

JH (St) H 3x2x0,8 mm,

JH (St) H 2x2x0,8 mm,

JH (St) H 2x1,5 mm2,

STP cat 6

NHXHX 3x2.5 mm2 FE180 / E30,

The cables shall be routed through a "halogen free" plastic pipes laid under plaster, by clamps, lay on the shelves.

  - Public Address System

    - General

The installation of public address system shall cover complete area with PoE horns for activating alarm in critical situations in the landfill.

    - Technical specification for Installations

Installation is performed with "halogen free" cables, similar to the type

STP cat 6

The cables are routed through a "halogen free" plastic pipes laid under plaster, by clamps, lay on the shelves.

  - Intercom System

    - General

The installation of intercom system shall cover all the premises of the object, regarding harsh conditions in the landfill.

Industrial intercom stations for harsh environment with IP67 shall be placed around complete open area.

Intercom server shall be located in administration building and complete communication between intercom stations and dedicated switch shall be through IP protocol. Intercom server shall have SIP communication and possibility to communicate with phone system.

    - Technical specification for Installations

Installation is performed with "halogen free" cables, similar to the type

STP cat 6

NHXHX 3x2.5 mm2 FE180 / E30

The cables shall be routed through a "halogen free" plastic pipes laid under plaster, by clamps, lay on the shelves.

  - Gas Detection System

    - General

The installation of gas detection system shall cover all the premises of the object. Depending on the level of fire danger it shall be provided manually reporting the occurrence of explosive gas.

All detectors, individually addressable, tied in the loops, shall be connected to the gas detection panel.

Gas detection panel in administration building shall be connected to the parallel gas detection display in gatehouse building.

Gas detection shall be signaling on gas detection panel, which shall be provided in the administration building, and intervention measures shall follow from there.

Gas detection panel and parallel gas detection display shall perform permanent control of situation and the correctness of electrical installations, shall receive and process alarms from lines, shall command the corresponding signaling and the effects on other installations in accordance with the requirements of the project for gas explosion protection.

Gas detection panel shall be powered by a 230V, 50Hz with a separate circuit from the power distribution cabinet.

In case of failure of the voltage it shall has back-up power - accumulator batteries which provide autonomy of 72 hours in steady mode and 30 min. in alarm mode.

Installation of gas detection shall consist of automatic gas detectors, alarm sounders in Ex protection, alarm horns in Ex protection, gas detection panel (included input and output interface) with 2 loops and gas detection parallel display. Methane is most common gas in landfill. Gas detection panel must control dedicated ventilation in buildings.

All detectors shall be connected by the principle of in - out without continuing cables.

All alarm sounders and horns shall be conventional.

Gas detection panel shall have maximal capacity for 2 loops for addressable devices, possibility to connect through MODBUS protocol with SCADA.

    - Technical specification for Installations

Installation is performed with "halogen free" cables, similar to the type

JH (St) H 2x2x0,8 mm,

JH (St) H 2x2x0,8 mm FE180 / E30,

NHXHX 3x2.5 mm2 FE180 / E30.

The cables shall be routed through a "halogen free" plastic pipes laid under plaster, by clamps, lay on the shelves.

In places changes of direction and branching installations shall be planned junction boxes 100x100 mm and Ø 78 mm.

Connection between distributions cabinets shall be carried out with similar type of cables TK 59GM 3x4x0,8 mm and PPOO-Y 3x2.5 mm2, that routed in the cable ducts.

Executive functions of gas detection panel

Gas detection panel shall form the impulse for:

- Activating the alarm sounders, horns and ventilation.

## Structured Cable Network System

### General

The installation of structural cable network is planned in all administrative areas and key objects, and to connect computer socket to a local computer network.

The installation of structural cable networks shall be implemented as an integrated phone-computer installation.

It shall be planned two RJ-45 sockets at each position, first one shall be provided for connection to a computer and second one shall be provided for connection to a telephone.

A telephone-computer installations in the object, concentrates in distribution cabinet.

### Technical Specification for distribution cabinet

Distribution cabinet shall be designed as a metal 19" "rack "cabinet,  height 12U, for wall mount, complete with:

- RJ45 "patch" panel Cat 6,

- Cable system with clamps,

- Switches, 100/1000, with POE,

- Voice panels,

- Distribution panel with 6 sockets for 220V, 50Hz,

- Fan panel with 2 cooling fan,

- STP patch cables.

# GENERAL INSTRUMENTATION REQUIREMENTS

## Design

Signals from instruments to controllers shall be either electrical or pneumatic, with the following ranges:

- Electrical	: 4-20 mA dc (HART protocol recommended)

- Pneumatic	: 0.2-1.0 kg/cm²

### Central Control System

When instruments are to be used for process control, the PLC system will be used.

### Panel Mounted Instruments

Panel mounted instruments shall be controllers, indicators, manual loaders or monitor switches for interlocking, and shall be indicated or approved by the Engineer:

### Local Instruments and Controllers

Local instruments and controllers shall be of direct reading type, with local indication instrument (display) and shall be indicated or approved by the Engineer.

### Pressure and Differential Pressure Transmitters

Pressure and Differential Pressure transmitters shall be one or more of the following, and will be indicated or approved by the Engineer:

- Indicating type or non-indicating type with a separate output gauge;  With over-range protection;

- Intelligence or smart type.

Materials for pressure and Differential Pressure instrument will be:

- Body: Stainless Steel as manufacturer's standard;

- Elements: Stainless Steel as manufacturer's standard.

- have an electrical output of 0/4-20 mA or 0 - 10 V proportional to the differential pressure,

- be capable of withstanding a 100% overload (i.e. twice the differential pressure required for full output) without sustaining damage,

- have fully adequate static pressure rating to withstand all possible surge pressures,

- have independent span, zero and damping adjustments,

- have an accuracy within ± 0.5% of span, repeatability within ± 0.2% of span and a dead band not exceeding 0.2% of the span

Each installation shall be supplied and installed complete with:

- sensing lines of stainless steel, grade 316S31,

- a 3 or 5 valve manifold as required,

- test point(s) with separate isolating valve(s).

### Instrument Connections

Threaded connections shall be as follows, except those which require a flanged connection:

- For process: 15mm, NPT(F);

- For instrument air: 8mm, NPT(F);

- For wiring: 15mm, NPT(F), Compression fittings (packing connection type) with cable lamp.

### Instrument Protection

Instruments shall be resistant against tropical conditions, surge lightning, high humidity, and corrosive atmospheres.

### Safety Design

Fail-safe design of instruments and/or instrument systems shall be applied for the safety of personnel and equipment of the plant under the failure of instrument air and/or electric power. No process streams except air shall be brought into the control room.

### Marking / Labeling

Corrosion-proof metal or UV resistant plastic material name plates, engraved with the tag number shall permanently be affixed on the case or body, unless otherwise specified.

Model number, size, rating, materials, explosion proof grade, etc., shall be indicated on the instrument name palate.

### Water Meters

Water meters shall be of the propeller or helix driven type and shall be double-flanged.  The meter bonnet shall be injection moulded thermoplastic, O-ring sealed and attached to the meter head by a suitable fastening method.

The meter tube shall be fabricated steel or cast iron protected internally and externally to prevent corrosion.  The propeller or helix shall be the injection moulded plastic type.  The meter shall have a digital totaliser in cubic metres or a decimal multiplier thereof.  It shall, in addition, have a dial or dials registering decimal fractions of the totaliser.  The lowest reading unit shall be one litre up to nominal flow rates of up to 100 m³/hr; 10 litres from 100 up to 400 m³/hr and 100 litres from 400 up to 1500 m³/hr. The meter shall be capable of measuring flows between 5% and 200% of the nominal flow rate for the meter. The accuracy of the meter shall be within 5% for flows between 5% and 20% of the nominal flow and within 1% for flows in excess of this, up to twice the nominal flow rate.

The meter shall have a low head loss characteristic and installation shall be possible in a horizontal, vertical or inclined position without loss of accuracy. The working pressure rating of the meter shall be suitable for 120% of the maximum pressure that can be developed by the pump or 120% of the static gravity head in the pipe work system, whichever is the greater.

## Flow Instruments

### Electromagnetic Flowmeters

Electromagnetic flowmeters shall be in accordance with the following:

- meters shall be of the short form, having a modulated, direct current excitation and inherent total zero stability;

- power consumption shall not exceed 16 watts per 100 mm of diameter;

- output shall be 0/4-20 mA or 0 - 10 V and the system accuracy shall be within ± 0.5% of actual flow across the full range of the instrument;

- a test certificate shall be provided for each instrument;

- field coils shall be fully encapsulated;

- equipment shall be guaranteed suitable for the ambient and process liquid temperatures;

- each flowmeter primary shall be supplied with a neoprene liner and electrodes of the material best suited to the particular process fluid;

- primary units shall be suitable for accidental submergence to a depth of 3 metres;

- Contractor shall provide primary units having flanges in accordance with the relevant specification relating to pipes, flanges, fittings, etc.;

- Contractor shall ensure that all primary units are rated to withstand the maximum possible fluid pressure, including possible surge pressures;

- each primary unit shall be supplied and installed complete with a dismantling joint to permit removal for repair and inspection;

- flowmeter equipment shall be supplied complete with amplifier (converter), drive unit (if applicable) and all cable for connecting between the components. The termination box shall be sealed to IP68 minimum;

- amplifier/converter shall be fully screened to prevent interference from adjacent equipment and shall be remote from the electrodes;

- amplifier/converter shall incorporate voltage stabilisation to ensure maintenance of system accuracy with a supply variation of ± 10%;

- Contractor shall provide a length of pipe having the same length and being flanged as the flowmeter primary, to replace the meter should this have to be removed for repair;

- flowmeter primary shall incorporate an electrode (or electrodes) to detect when the pipe is not full. The detector output shall control circuits within the converter to open circuit the analogue signal and initiate an indication of the "pipe not full" condition.

- the instrument shall be equipped with a suitable fieldbus interface module (e.g. PROFINET) for connecting to the PLC system. If using fieldbus communication, current/voltage output might not be needed.

### Ultra-Sonic Clamp-On Flowmeter

Ultra-sonic flow measuring equipment shall operate on the phase difference technique employing 2 No. ultra-sonic probes displaced longitudinally and mounted on opposite sides of the pipe to detect the difference between the upstream and downstream flight times. The equipment shall include acoustic transducers and a transmitter, and shall be installed complete with all necessary fittings, cables and connectors.

The acoustic transducers shall be non-intrusive and arranged so that they may be removed without shutting down the process line.

All items of equipment attached to the pipe shall be of non-corrosive material, designed to withstand continuous submergence to a pressure of 3 m head and guaranteed suitable for the temperature and process pressures, including maximum possible surge pressures.

The transmitter shall process the signals from the acoustic transducers and shall: provide an output of 0/420 mA or 0 - 10 V proportional to flow; be suitable for direct or wall mounting with up to 30 m of cable; incorporate contacts to initiate an alarm in the event of mal-function; incorporate temperature compensation; include facilities for field checking and zero adjustment.

The complete system shall operate with a minimum accuracy of ± 1.5% of full scale deflection over the full ambient temperature range. A test certificate shall be provided for each set of equipment.

The instrument shall be equipped with a suitable fieldbus interface module (e.g. PROFINET) for connecting to the PLC system. If using fieldbus communication, current/voltage output might not be needed.

### Flow Switches

Flow switches shall be the thermal type. The flow shall be of robust design and comprise a switch having changeover contacts.

With the tilting action which occurs on rising flow, the contacts shall change over, but there shall be a dead band between opening one contact and closing the other, during which period both contacts shall be open.

Flow switches for installation in pipe lines shall:

- be suitable for the maximum possible flow rate,

- withstand reverse flow without sustaining damage,

- have the operating set point adjustable over the range 20% to 100% of the normal flow,

- have change-over contacts rated at 5 Amps 230 VAC (50 Hz) or 1 Amp at 24 volts DC,

- be complete with all fittings necessary to carry out installation in the pipeline, including cable gland,

- have a metal housing compatible with the pipe material and rated for the system temperature and pressure,

- be suitable for the application and process fluid in respect of the principle of operation and the material of the wetted parts.

## Level Instruments

### Type of Level Control

External displacement type level transmitters and/or controllers could be used for level measurement of liquids up to 2m. For greater length, D/P level instruments shall be used.

Process connections:  50mm flange with side-side connection;

Materials:   Body ; As per piping specification.

Displacer: 		316 SS

Torque tube:  	316 SS

Other requirements:  	20mm screwed plugs shall be used, unless otherwise specified.

Damping adjustment for indication and output signal;

Specific gravity adjustment if possible

### Pressure Transducer Level Measuring Equipment

Pressure transducer level measuring equipment shall comprise a strain gauge or differential transformer type pressure transducer, a controller/transmitter and be complete with all necessary cable, conduits, etc., as detailed below. Differential transformer transducers are to be preferred for very low ranges. Each pressure transducer shall be enclosed within an all welded, stainless steel case not less than 19.0 mm in diameter and shall:

- have a single moulded cable which is securely bonded to the stainless steel case and comprising electrical connections, venting tube, strain cord or wire within the cable to obtain the necessary strength, and an outer covering suitable for the application,

- be suitable for continuous immersion in all process fluids likely to be met in water applications including potable water, distillate, wastewater, raw sewage, primary sludge, secondary sludge, thickened sludge and final effluent,

- be constructed so that the sensor diaphragm is protected against damage by shock, debris, etc., without restricting the transference of pressure changes from the surrounding medium,

- incorporate automatic temperature compensation,

- withstand a continuous overpressure of up to 400% without sustaining permanent deformation or calibration change. The controller/transmitter shall:

- be suitable for mounting within a control panel,

- accept the signal from the transducer and provide a 0/4-20 mA or 0 - 10 V output proportional to level (gauge pressure), for indication and control,

- include independent zero and span adjustments,

- have a system checking module which will simulate the transducer output.

- the instrument shall be equipped with a suitable fieldbus interface module (e.g. PROFINET) for connecting to the PLC system. If using fieldbus communication, current/voltage output might not be needed.

The complete system shall provide an accuracy within ± 0.5% of span with a linearity better than ± 0.1%.

### Pressure Transducer Installation

For installations in sumps and for similar applications where the depth is in excess of 3 m or where the available headroom over the sump is limited, the pressure transducer shall be installed within a 100 mm dia. G.R.P. tube to provide protection against mechanical damage to both the transducer and the cable. The G.R.P. tubing shall have an adequate number of holes and/or slots to allow it to fill and drain as the level varies. The tubing shall be fixed to the sump wall at intervals not exceeding 2.5 m.

For installations where the sump depth does not exceed 3 m, the sensor shall be supplied and installed as a rigid assembly comprising a stainless steel tube, a tube holder (both as used for control electrodes) and the transducer, with the cable passing through the tube. The transducer shall be a close fit, located completely within the tube at the lower end. The assembly shall be fixed at not less than two places to the sump wall and installed with the bottom of the tube just clear of the sump invert.

For all installations the cable between the transducer and the controller/transmitter shall be a continuous length, and kept as short as is reasonably possible. This cable shall be run in conduit and installed well clear of all a.c. mains and power cables.

### Ultrasonic Level Measuring Equipment

Where ultra sonic level measuring equipment is specified in the relevant application clause, level measurement shall be accomplished by the use of non-contact, echo-time measuring equipment operating at ultra-sonic frequency. The equipment shall transmit pulses which are reflected back to the sensor from the surface of the liquid whose level is being measured.

The equipment shall consist of a sensor incorporating both transmitter and receiver, together with a separate control unit. The equipment shall be provided with automatic temperature compensation, shall be suitable for operation in the designated application under the specified climatic conditions.

The control units shall incorporate facilities for adjusting independently both zero and span, and shall have an output of 0/4–20 mA or 0–10 V proportional to level. The sensor shall be suitable for mounting in the open, or within an enclosed tank, and shall be totally enclosed to IP68. The connection between the sensor and control unit shall be via commercially available screened cable, and the equipment shall operate with up to 150 meters of such cable.

The overall accuracy of the level measurements shall be within ± 1.0% of the instrument span.

The Contractor shall ensure that the equipment is suitable for the application, particularly with regard to the blocking distance and transmitted beam angle or cone.

The instrument shall be equipped with a suitable fieldbus interface module (e.g. PROFINET) for connecting to the PLC system. If using fieldbus communication, current/voltage output might not be needed.

### Installation of Ultra–Sonic Level Equipment

Each ultra–sonic level sensor shall be installed on a robust and rigid structure provided for the purpose under this Contract. The structure shall include a means of leveling the sensor so that the transmitted beam is perpendicular to the liquid surface and shall provide a safe and easy access to the sensor for servicing and maintenance.

The Contractor shall provide, where applicable, a canopy above the sensor and/or the control unit to provide a protection from direct sunlight.

### Electrode Level Control Equipment

Electrode level control equipment shall consist of a control unit or units and a number of electrodes, together with all brackets and fixings as required for the complete installation.

For all applications, sufficient electrodes and associated controls shall be provided to prevent "hunting" between the two states.

The control unit shall:

- have all live parts at a voltage in excess of 55 volts to earth completely shrouded and fitted with warning labels,

- have an output relay with double pole changeover contacts of suitable material for the application,

- have a light emitting diode mounted on the front panel to indicate when the relay is energized,

- have a lockable sensitivity control potentiometer,

- be capable of operating at a distance of up to 100 m. from the electrodes.

- have a voltage on the electrodes not exceeding 25 volts.

- The electrode and holder shall comply with the following:

- the electrode holder shall be of the heavy duty type, fully weatherproof, constructed from die cast aluminium and provided with a mounting flange having a minimum of 4 No. fixing holes,

- the electrode holder shall be designed to allow a minimum of 75 mm adjustment of the electrode length,

- the electrodes shall be of stainless steel grade 316S31, having a minimum O.D. of 25 mm a wall thickness not less than 2.6 mm. The lower end of the electrode shall be sealed, and the upper end shall be locked to the insulator by a brass clamp,

- cable entry shall be via a standard screwed gland entry,

- each electrode shall be firmly secured to avoid any movement due to turbulences or flow velocity. The securing brackets shall be of the same material as the electrode and shall be installed above top water level,

- where the electrodes pass through securing brackets; they shall be protected by heat shrunk sleeving extending from 300 mm above the bracket to 300 mm below the bracket.

### Float Switches

Float switches shall be the pendant type with the float suspended on a flexible cable, such that with the float free of the liquid the float and cable hang vertically, but with a rising liquid level the float shall rise and tend to invert.

The float shall be of robust design and comprise a non mercury switch having changeover contacts encapsulated in hard plastic foam and connected to a 3 core cable. The whole assembly shall be covered and hermetically sealed in Hypalon or similar material.

With the tilting action which occurs on rising level, the contacts shall change over, but there shall be a dead band between opening one contact and closing the other, during which period both contacts shall be open. This dead band shall operate over an arc approximately 20° either side of the horizontal.

The contacts shall be rated for a minimum of 5 amps at 230 volts. The voltage on the contacts shall not exceed 55 volts (nominal) to earth.

In all applications the installation shall be complete with approved means of preventing the float (and lead) from movement due to wind or liquid turbulence.

Where float switches are to be used in applications under which they may be submerged during normal operation (e.g. pump control and/or low level alarm); they shall be attached to a weighted chain to minimise movement due to turbulence and also to provide a means of raising the units for maintenance and repair. All brackets, fixings etc. as necessary for the complete installation shall be provided. The chain/float assembly shall be installed such that the point of suspension is not less than 400 mm from any side wall.

## Pressure Instruments

### Pressure and Compound Gauges

Pressure gauges shall comply with the latest Standards and be of brass or black moulded phenol plastic construction with acrylic plastic or toughened glass windows. Dials shall be at least 100mm diameter. Internal gauge components shall be of stainless steel or other corrosion resistant material with an accuracy of at least ±1% for pressures between 10% and 90% of full scale and at least ±1.5% outside this range. All gauges shall operate about their mid-scale position and be calibrated in bar, and in meters head.

Gauges associated with pumps shall be of the compound type for suction branches and the pressure type for delivery branches.

All gauges shall be fitted with isolating valves and where measuring water pressure they shall be equipped with a combined isolating valve and air release vent. If mounted remotely from the tapping point an isolating valve shall be installed at the tapping point.

Diaphragms shall be fitted to all gauges subject to liquid containing suspended matter.

Snubbers shall be fitted to all gauges installed on pumps and whenever subject to fluctuating pressure pulses.

### Pressure Switches

Pressure switches shall be of either the bellows or bourdon type, and shall be rated to withstand the maximum possible surge pressures.

The switches shall have:

- signal pole change-over potential free contact, with the contact material and rating suitable for the application,

- calibrated setpoint adjustment which shall be lockable to prevent any movement due to vibration,

- switching differential adjustable between 5% and 25% of the setpoint adjustment range,

- all wetted parts compatible with the process fluid,

- be housed within an enclosure to IP55 or IP67 according to location.

The gauges could be also of compact not indicating type, with fixed alarm point, adapted to process controlled value.

## Temperature Instruments

### Thermowells

Thermowells for thermocouples shall be used according to the following specification:

- Construction according to manufacturer's standard

- Materials of Thermowells : 316 SS

- Connection flanges as piping specification.

### Thermocouples

Thermocouples shall normally be Magnesium Oxide (MgO) insulated and metal sheathed type and the hot junction shall be nongrounded to the sheath. The specification shall be K(CA) with a temperature limit of -200 to +1200°C, sheath diameter 4.8mm, 316 SS.

### Temperature Transmitter and Controller

Temperature shall be transmitted by EMF to current transducer.

## Process Analytic Instruments

Analytic instruments shall be applied under and in accordance with the process design requirements.  Generally, analytic measurements are:

- Field mounted, continuous output signal instruments

- Stationary water samplers for liquid media

### Field mounted instruments

Analytic field mounted instruments shall be, but not limited:

- Logically arranged menu structure

- Ultra simple calibrated with user samples and alarm signaling for calibration errors

- Over voltage (lightning) protected

- Directly accessed for manual contact control

- User-defined alarm configuration

- Automatic sensor self-recognition with calibration data transfer

- With display in customer units via table assignment

- Live check of sensor

- communication ability: MODBUS, HART® or PROFINET

### Samplers

Samplers shall have at least:

- Stainless steel cabinet with foamed insulation, for safe sample preservation

- Sample compartment with seamless inner shell and evaporator in foam - no freezing and no corrosion of cooling plates

- Menu-led operation with “Quick-Setup”, for quick commissioning

- Media-carrying parts easy to mount without tools, for easy cleaning and maintenance

- Separate bottle trays with grips, for easy sample transportation

- Parallel sampling, switching and event software for practical programming

- Modular installation of electrical components for extended functions

- Integrated data logger, for recording measured values and sample statistics, with RS232 interface for configuration, data transmission and read-outs

- Modbus or Profinet, for connection and control by the remote control systems

- Connection possibility for multi parameter sensor

## Control Valves

### Sizing Base

Cv (valve capacity) calculation according to ANSI, BS or DIN. When selecting valve sizes the following points shall be considered:

- The calculation is based on a flow rate of 1.5 x the normal flow rate, or 1.2 times the maximum flow rate; whichever is greater;

- Valve travel at minimum flow rate during normal operation shall be not less than 10%;

- Minimum body size is 25mm;

- Noise level should not exceed 85 dBA at normal operation.

### Body Material

The materials and rating of body shall generally conform to the general piping specifications Clause, but the rating shall be minimal 300 lbs for carbon steel line. The body shall be flanged

### Valve Types

Valve type shall be selected, taking into account the cost, operating and design conditions, fluid being handled, rangeability required, allowable leakage, noise. The following types shall be considered: Globe valve (single ported, double ported, cage guided); Butterfly valve; Pressure regulator (self-actuated).

### Valve Trim

Materials: 304 SS or 17-4 pH SS or stellited seat/face for erosive service; Seat leakage: Single ported valves shall be used unless specified otherwise.

### Packing Gland

Packing glands shall be made of Teflon for temperatures below 200°C. In case of higher temperatures Graphite will be used. Finned bonnets will be used if the temperature is higher than 231°C

### Valve Actuators

Valve actuators shall normally be of spring and diaphragm or piston type. Spring-less piston type, pneumatic, electric or hydraulic type may also be considered in. All actuators shall be adequate to fully stroke the valve under the maximum differential pressure specified by the process requirements. The following air pressure shall normally be used to determine the actuator spring and/or the size of the actuator:

- Without positioner 0.2-1.0 kg/cm² G;

- With positioner up to 4.0 kg/cm² G

### Handwheel

Handwheel shall be provided as per P&ID diagram.

### Valve Positioner

Valve positioners shall be provided for all control valves, except for on-off valves, 0.2-1.0 kg/cm² G spring range and having a good response time to the control signal. The type of positioner to be used in the remote control loop shall be as follows: pneumatic for local control and electro-pneumatic for remote control.

### Safety and Relief Valves

Sizing according to BS, ANSI or DIN. The valves shall normally be of direct spring loaded type, and provided with full nozzle type. The bonnet construction shall be: screw cap for all functions. Materials: Body as per pipe specification. Connections shall be flanged.

## Instrumentation Air Supply Piping and Tubes

### Air Supply

- Piping style: Branch piping;

- Air set for locally mounted instruments equipped with each instrument;

- Piping materials as per piping specification.

### Signal Tubing

- Signal tube: 8mm, PVC sheathed;

- Multi tube: conventional type, 304 SS.

# GENERAL SCADA REQUIREMENTS

## Functional Design Specification

The Contractor shall submit a Functional Design Specification (FDS) to be approved by The Engineer prior to manufacture and purchasing of equipment.

The FDS shall be submitted in English and the national language of the Purchaser on A4 size sheets numbered within each section and page within section, to include, but not limited to, the following for each Treatment Area and item of packaged plant: Contents List; Reference to supporting standards, manuals and specifications; Description of the design and design criteria; Relevant details of associated mechanical, electrical and instrumentation equipment; Control philosophy (functional description); Complete set of supporting drawings; Design Documentation (including: A description of each major element of the control scheme; A flow-chart or pseudo-code description of each sequential element of the control scheme; Analysis of failure modes and shutdown procedures.); Calculations; Quality control procedures and approvals; Outline of test procedures; Manufacturer’s literature for each item of equipment supplied.

All drawing shall be on A4 or A3 sized paper as appropriate to ensure legibility include a title block detailing: Purchaser’s Name; Contract Title; Contractors Name; Drawing Title; Drawing Number; Date; Author; Verification and Approval by the Contractor prior submission.

## System Overview

A control centre shall be established in a location to be agreed with the Engineer to accommodate the Dispatcher equipment and operator workstations.

The system implemented should be able to operate within the control strategy described but shall be flexible enough to be easily changed should the control philosophy change.

The proposed system shall provide:

- A centralised Dispatcher processing function, complete with standby facilities and local workstations.

- Distributed intelligence using microprocessor based Programmable Logic Controllers (PLC’s) for monitoring and data logging. Under normal operating conditions, the PLCs with associated Operator's panels (HMIs) shall monitor and control plant to given schedules and record the installation's operational/performance data e.g. pump start/stop, inlet flow, storm tank level etc.

The PLCs shall have programmable alarm limits for discrete and rate of change settings. This shall apply to both real and derived values. There shall be a facility for high and low priority alarms, e.g. low, very low, high and very high.

In order to cater for communications failures, the PLC shall be capable of holding 8 days worth of data as follows:

Analogue, totalised and derived signals - on significant change/15 minute intervals.

Digital signals on change of state.

Logging and archiving functionality shall be covered by the SCADA system, no need to implement it on the PLC level.

The data gathered from the PLCs shall be incorporated into the Dispatcher database and shall also be made available to applications programs written by the client.

Where PLCs are programmed to perform local control of plant it shall be possible for the programmes, schedules, set-points etc. to be downloaded from the Dispatcher. Subject to being assigned suitable privileges, system users shall have the facility to make short term alterations to PLC control schedules via the control centre, e.g. to implement remedial action when an alarm occurs.

SCADA Control shall be effected at two levels, these being:

- PLC local control via programs stored locally at the PLC, e.g. pump start, fallback control.

- Supervisory control from the control centre.

An authorised user at the control centre shall be able, via the communications network, to modify the control routines at any PLC by downloading new control (start/stop) schedules, new performance criteria e.g. increase/decrease flow/pressure or operating individual items of plant e.g. open/close valve, start/stop pump.

The preferred method of communication with site based PLC’s is via optic cable network and GPRS communication for remote sites. As future developments may require different forms of communication at specific sites, the equipment shall be capable of operating in all modes with minimal software changes. The system shall operate using "management by exception" techniques:

- When an alarm condition is detected the PLC will dial into the master station immediately to announce the alarm and forward any data collected.

- Where alarm conditions arise, individual alarm presentation with alarm lists, mimic and tabular diagrams, and help pages shall be available to assist the operator.

## Dispatcher System Hardware

A centralised SCADA Dispatcher shall be provided for the SCADA system unless otherwise specified within the particular specification. All equipment required to fulfil the requirements shall be industry standard proven computing equipment with a demonstrable long-term life cycle and support.

To permit other manufacturer’s equipment, e.g. PLCs, to be added to the SCADA system, all equipment shall, wherever possible, interface using industry standard communications protocols.

## System Availability

The strategic importance of the SCADA system requires a high level of system availability, i.e. not less than 99.9% availability for each calendar year. The SCADA system shall therefore be provided with the following.

### Uninterruptible Power Supply (UPS)

The system shall be provided with a UPS capable of supporting all the main computer equipment (central processing units, discs, communications processors etc.), operating consoles and the alarm/event printer for a period of not less than 60 minutes. The UPS shall be provided to cater for a 50% increase in load without the need for additional hardware.

Uninterruptible power supplies (UPS) shall be provided for equipment which does not have intrinsic back up when loss of power supply would cause an unacceptable level of corruption of important stored data, disruption of process control programmes or damage to electronic components.

Where standby generation has been provided to prevent loss of electronically stored data, disruption of process control programmes or damage to electronic components, such equipment shall be further protected by provision of an UPS between the generator and the equipment to absorb supply variations. UPS shall be supplied at 230V, and shall have an output voltage of 230V. One side of the output shall be connected to earth. The output shall be protected by fuses or MCB’s. There shall be a synchronous changeover from mains to the UPS in the event of a mains failure.

The UPS shall be housed in a wall mounted or floor standing enclosure and shall have a degree of protection to corresponding to the place of installation.

All battery terminals and wiring shall be fully protected and segregated from other wiring to prevent inadvertent short circuits. Lead acid batteries are not allowed.

Essential services, e.g. UPS, generator, security etc. shall be monitored by the SCADA system.

### Maintenance

The equipment shall be suitable for maintenance by the Employers staff. It shall be possible to maintain the in complete safety without shutting down the works.

## Communications Equipment

The Network equipment shall be provided with all necessary communications equipment to support:

- All (operator) workstations.

- All printing devices.

- Communications to all on-site PLCs.

- All remote equipment.

- Equipment as detailed in the particular specification.

## Data Storage

Each SCADA station shall be provided with the following storage media:

- Random Access Memory – to store the “real–time”/instantaneous database.

- Hard discs – to store the system configuration, mimics and local short–term (365 days)

## Workstations

The operator workstations shall be the main Human-Machine Interface (HMI) and shall consist of one or more min. 22" TFT Visual Display Units (VDUs) capable of displaying graphical and alphanumeric characters in at least sixty-four colours in all foreground/background combinations.

Each VDU shall have an associated separate keyboard consisting of a standard typewriter QWERTY alphanumeric set, with additional numeric and special function keys, augmented by a mouse.

## Printing Devices

The system shall be provided with two types of printing device:

### Colour Printer

To provide high quality printed output for report summaries, programme development, copies of mimic displays, historical trends etc., issued a high speed colour laser printer A3 format, shall be provided.

Remark: this requirement leads to environmental issues. All of the mentioned documents shall be in digital form, not printed on paper.

## Remote Data Transfer

The SCADA system shall be capable of processing the data received from operational sites e.g. into daily minimum, maximum and means, and forwarding the raw and processed data to off-line packages e.g. Microsoft Excel.

## System Features

A low risk system supplied with proven software shall be supplied.

### System Access

Users of the system shall be allocated individual passwords allowing each user an appropriate level of access commensurate with their requirements, responsibilities and areas of knowledge and interest. Three general categories of access have been identified:

- Data only.

- Data and Control.

- Data and System Management.

Data only shall be generally available to all system users.  Data and control shall be limited to those personnel with the knowledge and responsibility to take control actions.

## Colour Graphics Displays

The following display types shall be available on all colour graphics terminals:

- Mimic diagrams

- Help pages

- Graphs

- Bar charts

- Alarm and event log listings

- System configuration and maintenance displays

### Mimic Displays

Mimic diagrams are required to present a pictorial representation of the plant and its present status. All mimics shall be suitable for display all sizes of monitor supplied within the Contract and careful design of the mimic shall be used to this end.

The following requirements are required for all mimics:

- Display of fixed (background) diagrammatic plant information and text. The background colour for all mimics shall be subject to the approval of the Engineer.

- Display of variable information i.e. symbols or text displaying plant status. All flows shall be displayed in engineering units as specified in the I/O listing of the agreed Functional Design Specification.

- Each mimic shall have navigation 'pushbutton' to the process overview, the geographical overview and associated process mimics.

- The symbols used to describe the plant items shall be subject to the approval of the Engineer.

- Mimics shall display process lines as colour dynamic with arrow indication of flow direction.

- Alarms indication shall be animated within the relevant mimic.

- Trend pages (including historic and current information) and the alarm summary page shall be available from every mimic.

- The Contractor shall configure each on-site workstation such that a screen dump can be printed by a single keyboard/on-screen action.

- Control pages for all plant that can be controlled, overridden or plant data entered manually shall be available from every mimic.

- Easy picture creation, possibly using a CAD style package.

### Display of Variables

Variables can be considered as digital on/off parameters, analogue or totalisors.

Digitals may be either status (e.g., running/stopped) or alarm points, and shall be displayed by:

- Text changing

- Symbol colour changing

- Symbol shape changing

- Text or symbol flashing

It must be possible to associate more than one digital point with a symbol, so that more than two colours/shapes can have operational meaning. For example, a pump may be shown in four colours indicating running/stopped/failed/non-operational.

In addition, it shall be possible to associate any number of symbols within different mimics with a particular digital point.

Analogues and totalisors shall be displayed by: Numeric value; Bar chart; Graph.

It shall be possible to display all these three types of indication in mimic diagrams. Colour changes shall be used to indicate further information about a point, e.g. if an alarm limit has been exceeded.

### Display Attributes

Using the display facilities described above, the mimic diagrams shall indicate the following attributes for analogue, digital and totaliser points:

| Attribute |  | Point Type |
| --- | --- | --- |
| Status On/Off Alarm/Normal |  | Digital Status Digital Alarms |
| 1st Stage Alarm (High, Low) 2nd Stage Alarm (High-High, Low-Low) Out of Range |  | Analogues Analogues Analogues |
| Communications Failure Alarm Manually Suppressed (out of service) Alarm Automatically Suppressed |  | All All All |

### Picture Creation

It is essential that picture creation is a straightforward procedure, a CAD type package would be suitable. It must be possible to create symbols which may then be used in any orientation, size and colour and to create a symbol library, i.e. a part of a diagram which may then be used many times. It must be possible to display, on any single mimic diagram, information from anywhere within the system.

### Help Pages

Help pages shall be available within the system, to assist the operators in dealing with received alarm conditions. These pages will be compiled by the plant managers and will provide advice as to which staff shall be notified of which alarms.

Help pages may be presented as individual pages accessed from a mimic, or as a window superimposed on a mimic.

### Graphs

Graphical representation of historical data is required, with a selectable time base and the ability to put up to four graphs on display at once on the same axes, using different colours.

The system must be easy to use, with automatic default facilities so that only a minimum of instructions need be given to the system to obtain each plot.

Features that will be required are:

- Pre-configured and ad-hoc trend displays.

- Ability to compare graphs over different time spans, e.g. today's flow compared against yesterday's flow.

- Read-out of the actual value of a graph at a given time point.

- Ability to roll a graph forward and backwards in time.

- Ability to set the scale for each graph.

- Trend graphs giving a plot of the selected variable up to the last scan, updating when a new value is received.

- Ability to incorporate a trend graph as a feature on a mimic diagram.

- Graphical output of both analogue and digital signals (real and derived). Digital signals will produce a square wave type plot indicating for instance when a pump started and stopped.

- Auto ranging scale unless manually overridden.

- Ability to display data from different sites within the same trend display

### Bar Charts

A bar chart type representation of analogue variables is required. This is required on mimic diagrams, and must be capable of horizontal or vertical orientation, with selectable scaling. Width of bars must be selectable so that the feature can also be used for such items as tank level pictorial representations.

### Alarm and Event Log Listings

All alarms and changes of status (i.e. digital events) in the system shall be logged to disc. It shall be possible to recall this information to the screen via a select and sort programme. This programme shall sort and display information on at least the following bases:

- Process Area

- Site type

- Site name

- Time period

- Signal identification numbers

- Signal state (on/off)

- Alarm status i.e. cleared, accepted and unaccepted.

- Alarms or status occurrences required

Any sort parameters not entered shall default to "all".

### System Set-up and Maintenance Displays

Suitable displays of information shall be provided to display all set-up features of the system. These displays will be closely associated with the SCADA system set-up facilities.

### Logging On/Off

Every user of the SCADA system shall be required to log on (i.e. activate) his terminal when he wishes to operate on it. The system will be aware of which terminals are logged on and the access rights of the user and will therefore be aware of where to send certain information.

## Alarm Facilities

Digital points within the system shall be capable of operating as either status (e.g. running/stopped) or alarm points (e.g. normal/failed). A digital alarm point shall enter the Alarm State when it is either a logical ‘1’ or logical ‘0’ as designated in the system set-up for each point, the opposite state being the normal condition.

Analogue points shall be provided with two high alarm limits (high and high–high), and two low alarm limits (low and low–low). Should an analogue value either rise or fall from a value considered to be normal, a first stage high or low alarm limit will be encountered resulting in a new alarm condition. Should the value continue to rise (or fall) it will then encounter the second stage high–high or low–low alarm limit again resulting in a new alarm condition.

### Alarm Priorities

Every alarm generated within the system shall be allocated an alarm priority to indicate the importance of the alarm. Whereas a digital point will have only one alarm priority, an analogue point will have three. This will allow the relative importance of the first and second stage high and high–high (low and low– low) alarms to be set. The alarm priority is used in conjunction with the ‘area of interest’ of the users logged onto the system to determine where and when a new alarm is enunciated. The priority of an alarm shall change if required depending on the time and date.

### Alarm Annunciation

Alarms are to be enunciated on the appropriate operator workstations both visually and audibly, and have clear and unambiguous acceptance procedures. High priority alarms shall be presented for acceptance before low priority ones.

### Alarms Filtering

The SCADA system shall have a “tool–kit” of facilities that may be applied to individual points in the system in order to prevent unnecessary annunciation of alarms. These shall typically include:

- Analogues: dead-band; delays before initial alarm; minimum alarm repeat interval; logical suppression of new alarm if other conditions are; present; averaging values in PLC.

- Digitals: delay before initial alarm; minimum alarm repeat interval; logical suppression of new alarm if other conditions are present.

Users, subject to authorisation (i.e. correct level of access), shall be able to manually suppress an alarm, e.g., if a transducer is faulty and is being particularly troublesome. The suppression of alarms shall be logged to the event list.

### Derived Alarms

A combinational and sequential logic package is required within the SCADA system, allowing signals to be combined to form derived alarms. These may be combinations of analogue and digital information obtained from different sites (e.g., a pump may be running at a pumping station but no flow entering the associated inlet works resulting in a derived alarm indicating a potential burst).

## Historic Information

### PLCs

Logging&archiving functionality will be completely implemented on the SCADA level. Loss of communication btw PLC and SCADA system must not be an issue.

### Master station

In addition to the raw operational data, a long-term archive of analogue max/min/mean values, pump hours run etc. will be maintained. Values stored will be as detailed within the Particular Specification.

## Controls

### Manual Control

It shall be possible to perform control operations (e.g. remote start/stop of pump) from any of the operator consoles. Access to controls will be limited by the access rights assigned to the individual passwords for various operatives (see System Access).

The issuing of control instructions shall take precedence over the scanning for alarms. A well organised select check and execute system is required.

### Automatic Controls

Automatic control features shall be available within the SCADA system, and fall into two categories:

- Profile type controls where a working pattern (e.g. of reservoir level) is downloaded to a PLC for use by a local control system. New profiles may be sent for each day or week etc., as required.

- Combinational and sequential control: There are circumstances where the only practicable way of closing a control loop is via the SCADA system, although this should be avoided whenever possible.

- The package used for alarm derivation will also fulfil the automatic control requirements.

- The following facilities shall be provided as a minimum:

- Logical AND/OR/NOT/EXOR/EQUALS

- IF-THEN-ELSE Constructions

- Arithmetic operations including >, $, >, #, =, +, -, H, ), /.

- Logical constructions including time and data

- Look-up tables, with interpolating facilities

- Input to functions from any system point including digital, analogues, totalisors, controls from a keyboard, set-point input from a keyboard.

- Output from functions to be available as digital, analogue or totaliser points, or transmitted to any PLC as a control or set point.

- Access to point attributes in addition to present value, including:

- Suppressed, telemetry failed, in alarm (and for analogues, which alarm level).

### Terminal Time-out

When a terminal is used for control purposes, it shall have to be logged on specifically for that function. If it is not used for a user configurable period of time (e.g. 5 minutes) in this mode, it shall automatically revert to a display only mode. A warning should be provided one minute prior to the auto log off.

## System Record

A record shall be kept on disc within the system of all operator actions, such as alarm acceptance or control actions performed on the system. The record shall include:

- Time and date;

- Action;

- Operator.

This record shall be retrievable from the system using a similar select and sort routine to that specified for status and alarm logs.

## Report Generation

The system shall be capable of generating both regular and individual reports. Reports must be easily configured and altered in order to maintain their relevance.

An example of a regular report which may be produced from the system is the following, designed to be made available to the works manager each morning:

Service reservoirs: levels (%)

Treatment works: previous day's output

Flows: at points where flows have to be maintained for abstraction purposes Alarms that have occurred during the night

## System Time

The system shall support: Greenwich Mean Time (GMT/UCT); Daylight Saving Time (DST); Leap Years.

All data shall be logged at GMT/UCT + 1 hours, but automatically displayed in the appropriate local time adjusted for daylight saving.

## System Database Configuration

The system shall be provided with privileged and secure on-line database building utilities i.e. it shall not be necessary to stop the scanning and alarm presentation facilities. Any configuration shall not be installed into the active database until completed, verified and authorised by the user. A reliable verification procedure shall be required to prevent the creation on invalid files and the deletion of in-use files.

It shall be possible to define process point files, calculated/derived point files, remote PLC files, to include: Meaningful point identification and description; Allocation of points to groups/locations; Range of analogue values in Engineering Units; Alarm limits/categories; Scan control/frequency; Report control (whether change of state is to be logged to the alarm/event printer); Save control (whether values are to be archived); MIS control (whether values may be transferred to other systems)

## PLC Equipment

- Programmable logic control devices (PLC's), where specified, shall be used to affect the monitoring and control of the plant or process.

- They shall be capable of operating as either a standalone unit providing local HMI interface information or as form part of a supervised system complete with communications facilities.

- The PLC shall be a modular unit capable of expansion with associated HMI. It shall support a minimum of 32 input/outputs but shall minimally be capable of expansion up to 1024 I/O.

- The PLC shall operate from a nominal power source of either 230Vac, 50 Hz, and incorporate its own integral 24Vdc power supply for driving auxiliary modules.

- The programmable controller shall have adequate memory and I/O ports to receive all control and sequencing signals and drive all indicator lamps, relays or solenoids as may be required to accurately control all the necessary functions of the control system.

- The controller shall indicate the operating state of the inputs / outputs by means of LED diods and sets of LED.'s to indicate the controller status and to notify of any internal faults.

- An integral means of turning all outputs off and ceasing the processor operation shall be fitted.

- The PLC shall perform the majority of sequential functions and shall drive, either directly or by interposing relays, all the necessary outputs as detailed elsewhere.

- Where the output load exceeds the rated capacity of an output port of the controller, suitably rated, DIN rail mounted interposing relays shall be installed in the cabinet to amplify output controls signals.

- DIN rail mounted terminals shall be fitted in the bottom of the cabinet to allow the termination of all control and sequencing cabling. The terminals shall accept up to 4mm2 stranded conductors.

- All output ports from the controller shall be correctly fused in order to protect the controller (by means of fused terminals).

- The PLC shall be capable of supporting the following component parts either inherently or via expansion when required and shall support all the required process I/O (+20% spare) as detailed elsewhere:

- Power supply

- Central Processor

- Digital inputs and outputs

- Analogue inputs and outputs

- Communications

- High speed pulse counter

- RTD inputs

### Power Supply Requirements

The equipment shall be designed to operate from one of the following power supplies:

- Mains power supplies shall be 230Vac, 50 Hz. The mains operating voltage range shall be user selectable by a switch or selection link.

- Mains power supplies as defined in sub-clause (a) above, but having an additional facility for operation directly from a 24Vdc standby supply.

- 24Vdc supply with full protection against accidental reversal of the supply polarity.

- The system circuitry shall be fully isolated from its power supply, using isolating barriers having resistances of not less than 2 megohms, measured at 500Vdc to the requirements of BS 4743.

- Depression of the mains supply voltage by 25% for a period of 5 seconds or interruption of the supply for 25 cycles shall not cause the system alarms to operate.

- Mains borne transients of up to 1000V with energy levels of 1 joule shall not initiate system alarms or cause the system to operate outside the performance requirements of this specification after the occurrence of the transient.

- Distortion of the AC mains supply waveform as defined in BS 6438 Clause 5.4.3 for a rated range of use III (B = 0.10) shall not cause system malfunction.

- System cable terminations shall be made in a discrete termination section, housing terminal blocks sized, barriered and uniquely identified, to suit the voltage and current demands of the circuitry. Pinch screw type terminals are not acceptable.

- Within the following ranges variation of the power supply to any system shall not cause it to operate outside the performance requirements of this specification as required under BS 6438.

-12% to +10% of the nominal 230Vac and a variation of the frequency within 45 to 55 Hz.

-12% to +10% of the nominal 24Vdc supply.

### Input/Output Requirements

#### Digital Input Requirements

Two classes of input are acceptable:

- Nominal 24V DC input rating, opto-isolated, reverse polarity protected.

- Nominal 230V AC input rating, opto-isolated.

Mixing input ports in any given single installation shall not be acceptable.

Field contact inputs shall be debounced such that status changes will not be recognised unless the contact condition is maintained for at least 25 milliseconds.

#### Digital Output Requirements

- Digital output shall be of the volt-free contact type.

- Each output shall be electrically isolated from other outputs, the rest of the circuitry and earth. It shall have an insulation resistance to the rest of the circuitry and earth of greater than 2 megohms, when tested for 1 minute with 500V DC insulation tester.

- System functionality shall be maintained when each output terminal is earthed in turn.

#### Analogue Input Requirements

The preferred input signal is 4-20mA; continuous; linear supporting a fully floating max 250 ohm input impedance load. Analogue/Digital conversion shall have a minimum 8 bit resolution, linear to ±1%, accepting signals in the range 0-10mA and 0-20mA and voltages 1-5V, 0-1V and 0-100mV as required. Input moduls shall be able to accept and supply HART instruments loops.

#### Analogue Output Requirements

Analogue output shall be 4 to 20mA DC electrical signal with a linearly increasing output for increasing measuring value. When the load resistance across the output terminals is varied from 0 to 1000 ohms the output signal current shall not change by greater than 0.1% of span, over the full output range.

### Communication Ports

Communication ports will only be necessary on the PLC when its use is specified as part of an overall networked system. When required they shall provide the communication link between the PLC and other PLC's or PC based system.

### Protocols

Provision of the communication required to satisfy this Specification shall include all necessary protocols for its successful operation.

A serial RS 232 or other applicable port shall be available to enable interfacing a local PC's for HMI purposes to allow local database and control sequence loading, interrogation or modification. The port shall cater for communication with a suitable encoding device.

### High Speed Pulse Counter

This input module shall accept voltage level input signals of 5, 12, or 24 volt and have counting speeds up to 50 kHz. Encoded count signals of 16 or 32 bit, bidirectional, shall be selectable and a minimum of 2, source or sink, independently configurable outputs shall be provided.

## Communications

The Contractor shall supply install and commission all necessary communications equipment and software to provide a complete integrated communications network for the SCADA system.

### Scan Times

The Contractor shall prepare a detailed assessment of the PLC scan times for his system and submit this to the Engineer for approval.

### Transmission and Protocol

The Contractor shall use an industry standard open transmission protocol.

### Electronic Equipment

All communications equipment used in the communications system shall be of high reliability and shall comply with the most recent edition of appropriate National and International Standards

## Testing

The Contractor shall provide for system testing as detailed. The Engineer shall approve all acceptance procedures for inclusion within the system specification.

### Factory Acceptance Test

The Contractor shall provide for full Factory Acceptance Test of the fully configured system, to include:

- The complete system network

- Support for all PLCs with all points over an integrated network, simulated to include all types of communications units and interfaces

- Mimic display pages on the system as defined within the particular specification

- Test 1 Simultaneous occurrence of: The control centre polling outstations in normal (i.e. daytime) operational mode receiving 50% of data from each PLC with 10% of points in alarm conditions. Two operator workstations performing: Simultaneous access; Access staggered by 2 seconds.

- Test 2 as test 1 performing daily system archive.

- Test 3 as test 1 performing archive data recovery; Full daily archive recovery; Four data points for one week (15 minute intervals)

- Test 4 as test 1 performing screen dump; Printing daily report

- System Start-up and Shut-down Procedures, These tests shall exercise the system start-up and shutdown commands including: System start-up commands; Operator log-in and log-out commands; Password verification; Any special function command keys; Orderly system shut-down.

- System Back-up and Recovery Test: These tests shall exercise the system back-up and recovery procedures, including: System back-up to archive media; System re-build from system archive media; Synchronisation of the Master Station and outstations.

The simulation package shall use the SCADA system to demonstrate proper performance under full utilisation conditions.

#### SCADA Database Configuration

These tests shall exercise the database commands including:

- Password and level of access maintenance.

- The creation and amendment of PLCs.

- The maintenance of PLC communications parameters, e.g. telephone numbers, radio characteristics, change of media, scanning intervals, on/off telemetry scan.

- Regions of interest.

- Creation and amendment of SCADA points: Name; Type, e.g. status, analogue, derived; Alarm limits; Historic data recording and characteristics; Re-transmission of value to associated points; Scaling factors; Calculation formulae maintenance; Set output control parameters for digital, analogue and derived controls.

#### Picture Configuration

The tests shall exercise the picture configuration commands available to the privileged operators, including:

- The creation of picture pages, to include foreground/dynamic and background/static picture elements.

- The modification of picture pages, to include foreground/dynamic and background/static picture elements.

- The deletion, copying and renaming of pictures.

- Any function control key usage.

- Examples of all picture types, e.g.: Static information pages (e.g. indices); Mimic pictures for information display and control monitoring; Alarm list pages; Statistical pictures (e.g. trends, histograms); Help/text pages; The display and printing of pictures.

#### Data Collection

These tests shall exercise the data collection commands available to the privileged operators, including:

- The collection of digital, analogue and derived parameters.

- The collection of all data from outstations at frequencies defined by the privileged operator.

- The manual entry of data.

- The inhibition of data collection from a PLC.

- The inhibition of data collection from an individual point.

- The editing of stored data (subject to correct level of access)

#### Supervisory Control

These tests shall exercise the supervisory control commands, including:

- The creation and downline loading of control sequences.

- Digital, e.g. open/close, and analogue, e.g. set point, controls of individual control points.

- Preventive checks to ensure the correct control point is addressed.

#### Alarm/Event Handling

These tests shall exercise the alarm and event reporting procedures, including:

- Digital and analogue alarms: Reported on the alarm/event printer; Logged to disc; Reported to the appropriate operator consoles;

- Events, e.g. issue remedial control command, are only issued from appropriate operator consoles; logged to the alarm/event printer; logged to disc; are subject to correct level of access and regions of interest.

- Alarm acceptance/acknowledgement procedures.

- Alarm list interrogation procedures.

- Alarm list printing.

- Alarm inhibit for an individual point.

#### Data Logging

These tests shall exercise the data logging and archiving procedures including:

- Tests to ensure all data/alarms collected are logged to the on-line archive storage.

- Tests to ensure data can be archived to and recalled from long term archive media.

#### PLC Programming

These tests shall exercise the PLC sequence programming procedures, including:

- Sequence program editing, compilation and loading.

- The ability to load new sequences on demand by a privileged operator.

#### Management Information System Development

These tests shall demonstrate the use of the enquiry package and the applications programs development tool kit, including:

- The editing and compilation of programs.

- The abstracting of data from the SCADA database.

- The automatic scheduling of programs as a result of time of day queues and as a result of a SCADA event/alarm.

The Contractor shall substantiate the validity of the simulation to the Engineer and shall confirm by what means such simulation will be carried out.

- The PLC to demonstrate: All control and failure recovery sequences, simulating all digital and analogue inputs and outputs on each system.

- The communications system to demonstrate: Full simulation utilising all interface nodes, with PLCs connected, in order to prove the performance over the network. Communications failures shall be simulated in order to prove the automatic re-routing of communications to SCADA system.

#### Factory Acceptance Test - Witnessing

The Factory Acceptance Test shall be conducted in the presence of witnesses, who shall be nominated, in writing, by the Employer and the Contractor respectively. The witnesses shall be empowered to act during the Factory Acceptance Test, on behalf of the parties they represent, to judge the success or failure of a particular test. Either party as necessary, in writing may appoint nominated Deputies.

The Contractor shall provide evidence that the tests (FAT/SAT) have been successfully performed prior to the witnessing by the Engineer.

#### Factory Acceptance Test Procedures

The testing procedures shall be designed such that each separate testable entity (e.g. hardware configuration, picture building) consists of a well-defined series of tests.

Each test shall be documented to include:

- The purpose of the test;

- Any pre-requisites required allowing the test to be completed successfully; Any hardware required allowing the test to be performed successfully; A detailed schedule of activities to be performed within the test.

#### Factory Acceptance Test – Records

A log shall be maintained during the Factory Acceptance Test. This log shall record for each test performed:

- The test results;

- Any faults which occur;

- Any remedial action taken; Re-test results; Decisions taken by the witnesses which may affect the test results.

The witnesses of both parties shall initial all entries within the log. Copies of the log shall be provided to the Employer on completion of the Factory Acceptance Test.

The Contractor shall record the following:

- DISPLAY RESPONSE: This shall be no greater than as specified;

- PERCENTAGE CPU UTILISATION;

- SCAN TIME: This shall be no greater than 5 seconds for full system scanning;

- TIME TO CLEAR BACKLOG: The Contractor shall also record any adverse conditions that become apparent.

#### Failure and Re-test

The success or failure shall be determined as follows:

- If the system performs as laid down in the Functional Design Specification the test shall be deemed successful.

- The tests shall not be failed due to external conditions, e.g. power fail, provided the system fulfils the resilience criteria detailed within this tender document and any subsequent project specification.

- The tests shall not be failed through incorrect operation provided the fault can be corrected by normal operating procedures and provided the test performed satisfactorily in all other aspects (e.g. printer ribbon failure).

Any test that is deemed unsuccessful may be retried following any remedial action that may be necessary. If the system should fail any test and it is apparent that the fault may have affected the result of tests previously regarded as successful any or all of the tests affected may be re-tested.

To allow all participants to fully understand all aspects of the Factory Acceptance Test, the Factory Acceptance Test Specification as agreed between all parties shall be issued with the Contractor's Project Specification (CPS).

### Site Acceptance Tests

The Contractor shall provide for full site acceptance tests for each item of plant to be provided under the Contract. This shall include the interface to the marshalling unit, the communication system, the earthing system and full functionality as demonstrated at the Factory Acceptance Test.

### Systems Acceptance Tests

The Contractor shall provide for full system test on completion to include tests as stated above.

All special test equipment relevant to the Contractor supplied equipment shall become the property of the Employer on completion.

## Training

The Contractor shall at time of tender state any minimum levels of training/experience required for participants, prior to attending the appropriate course.

The Contractor shall provide training for the Purchaser's staff as detailed. The Tenderer may offer training courses structured to meet his technical offering. These courses shall be subject to the approval of the Engineer.

In general training courses shall be provided at Purchaser’s offices as detailed within the particular specification. However some courses may be held at the manufacturer’s works as agreed by the Purchaser.

The Contractor shall provide all course materials and equipment needed.

The training shall be organised such that the Purchaser shall be able to operate and maintain the SCADA scheme following completion of all training courses.

#### System Operators

The Contractor shall provide a course for all system operators with 4 no. operators attending each course. This purpose-designed course is to be held at the Works Control Centre. Training must be provided in advance of commissioning to enable the Purchaser’s user staff to participate in the full process commissioning of the system and safely operate the plant and maintain the SCADA system.

System take-over shall not take place until satisfactory training has been provided.

This course shall be designed to familiarise the participants with the general running of the standard operating system and the SCADA package to include but not limited to:

- Loading and starting up the Operating System;

- System Operators interface;

- Operator control of program/task execution;

- Operator control of disc files;

- File transfer tasks - archiving, retrieval;

- Operator response to system failure, on-line/off-line diagnostics, transfer of control between the computers synchronisation of the system database;

- SCADA system interrogation facilities - alarm lists, log printouts select mimic and trend displays etc;

- Alarm acknowledge accept/delete;

- Control actions, e.g. start pump, close valve; All functions associated with each access level of the SCADA system;

- System Supervisor Personnel;

### Systems Administrators /Programmers/Engineers

The Contractor shall provide a five-day course for the system administrator. The course shall be held at the Works Control Centre prior to the systems hand-over and shall consist of all of the above tasks plus:

- Basic systems design overview;

- The use of computers to perform diagnostics and to tune other parts of the system;

- Changing passwords and access control; Sequence verification;

- Preventative maintenance.

This course shall be designed to cover all configuration and advanced facilities of the SCADA package. To include, but not be limited to:

- The system database structure;

- System database building/configuration;

- Mimic building;

- Applications program interface to the system database;

- Management information system interface;

- Downtime loading of control programs/sequences to PLCs;

- Advanced operating features.

### Site Training

The Contractor shall liaise with the Engineer and the Purchaser on site as new areas of plant are to be changed over to the new system, to establish the following:

- What training is required for operating and maintenance staff?;

- Who is to be trained?;

- Who will provide the training and when?

The Contractor shall supply O & M documentation prior to training. A section of the plant shall not be handed to the Purchaser for operation until training on the control systems has been completed. Should defects occur prior to Take-over of the whole scheme the Contractor shall be responsible for rectifying the fault prior to any other phased hand-over of the scheme.

This training course/workshop shall be designed as a "reference" course rather than a formal educational course, i.e. the Contractor's personnel shall be present to assist the Purchaser's personnel, as necessary, with any technical difficulties.

## Operations & Maintenance Documentation

This contract shall include full documentation for all equipment and software provided under this contract. The documentation shall be written in a clear and concise manner which is fully formatted and indexed to provide documentation that is easy to understand and friendly to use.  It shall be capable of incorporating upgrades and amendments to information in an efficient and effective manner. Generally the documentation shall be compiled in A4 ring binders. Liaison will be required with the Engineer regarding the contents of the individual manuals.

All documentation shall also be provided in electronic form, on disk in the Employer standard format current at the letting of the contract. The Employer shall hold the copyright for these documents. All drawings, unless within word-processing documents, shall also be provided in AutoCAD format on disk, or other media agreed with the Purchaser. All documentation shall conform to ISO 6592 Code of Practice for Documentation of Computer Based Systems. The Contractor may offer manuals structured to meet his technical offering. These manuals shall be subject to the approval of the Engineer and shall be detailed at the time of Tender. The documentation shall be submitted to the Engineer for approval and shall include, but not limited to:

### Full System Operating Procedures (six Copies)

The Contractor shall provide full operating procedures detailing how to use the SCADA system, to include but not limited to: Loading and starting up the Operating System; System Operators interface (including: System mimic navigation; SCADA system interrogation facilities - alarm lists, event log printouts and trend displays etc; Alarm acknowledge accept/delete; Control actions, e.g. start pump, close valve; All functions associated with each access level of the SCADA system.); Operator control of program/task execution; Operator control of disc files; File transfer tasks - archiving, retrieval; Operator response to system failure, on-line/off-line diagnostics, transfer of control between the computers synchronization of the system database.

### Full Software Documentation (six Copies)

The complete software specification shall be provided and shall include the system design specification, flowcharts, logic diagrams, system software definitions, program index, system build definition, and system data for each system and module. The information shall not be disclosed to any third party without the author’s consent.

Hardware Manuals (two Copies)

The Contractor shall provide documentation for all equipment supplied within the Contract.

### PLC Programming Documentation (one Copy)

The Contractor shall provide a copy of all necessary PLC programming documentation as supplied by the PLC manufacturer.

## System Recovery

The Contractor shall supply a full backup set of the supplied software, on suitable archival media (e.g., CD, DVD, etc.). The Contractor shall also himself keep a full backup of the supplied software for the life cycle of the supplied equipment.

## Consumables

The Contractor shall supply all consumables for the SCADA equipment for the duration of the contract, including, but not limited to: Printer paper; Printer ribbons/ink cartridges; Storage media; Cleaning materials.

## Spares and Test Equipment

The Contractor shall provide a list of recommended list of spares and test equipment required to the SCADA system.

To minimise the spares holding, the Contractor’s design should consider the benefits of standardisation.

# GENERAL TESTING REQUIREMENTS

## Testing and Inspection

The Contractor shall arrange for the Electricity Authorityto undertake any testing and inspection necessary for the electricity supplies to be connected when required. On completion of the tests and inspections, not less than two weeks prior to the power supply being required, the Contractor shall supply to the Engineer a copy of his Electrical Installation Completion Certificate and of the test certificates.

## Electrical design meetings

The Contractor will be invited for Electrical Design Meetings by the Engineer to provide information and attune planning of activities with the other contractors, if necessary. The Contractor shall be represented by an electrical engineering specialist and the Contractor representative or personnel equally authorised.

## Tests Generally

Test personnel shall be fully conversant with the particular manufacturer’s plant, which is being tested, and shall be fully competent in the required test procedures.

The Contractor shall submit a programme of tests, structured to facilitate attendance by the Engineer, and to economise on time and travel/accommodation expenses.

The Engineer shall be given two weeks notice in writing to attend works tests. The Engineer may, at his discretion, forego the witnessing of any tests. In such instances, the Contractor shall have the required tests carried out, and shall supply independently certified test certificates to the Engineer.  The Engineer’s approval is required before shipment to site. Formal test certificates are required in triplicate in all cases. The Engineer will give at least twenty-four hour written notice of his intention to attend the tests.

The testing shall ensure that all plant functions correctly, performs and is supplied to Specification. Specific ‘works’ tests’ are detailed in the relevant parts of this specification.

A provisional sum should be included in the schedule of prices for expenses by the Engineer for attendance at the Contractor’s or Manufacturer’s premises.

In general, testing shall be to the following requirements:

## Testing for the equipment and materials

The entire scope of supply shall consist of new manufactured materials only.

The Engineer shall be entitled, at all reasonable times during manufacture, to inspect, examine and test on the Contractor's premises the materials, workmanship and performance of all plant to be supplied under the Contract.  If the plant or any part thereof is being manufactured at a plant other than the Contractor's, he shall obtain, for the Engineer, permission to inspect, examine and test such plant as is required. Any such examination, inspection or testing does not relieve the Contractor of his obligations under the Contract. The results of any testing shall not prejudice the Engineer’s rights to reject the Plant if it fails to comply with the Specification when installed, or to give complete satisfaction in service.

The Contractor shall provide at his own expense all labour, materials, electricity, fuel, water, stores, apparatus and instruments as may be required and reasonably demanded for the carrying out of the tests. The Contractor shall submit to the Engineer fully detailed documentation of his inspection and test procedures for approval.  Testing shall not commence until the Engineer has formally approved the procedures.

If after inspecting, examining or testing any plant, the Engineer should decide that such plant or any part thereof is defective or not in accordance with the Contract, he may reject the said plant or part thereof by giving the Contractor, within a reasonable time, written notice of such rejection, stating therein the reason for rejection.

Full witness testing by the Engineer at the manufacturer’s works of the following may be required:

- Mixers

- Blowers

- Automatic valves

- Pumps

- Dosage equipment

- Electrical Switchgear and Motor Control Panels

Other items as may be required from time to time

All major items of plant shall be offered for inspection prior to their being dispatched from the Manufacturer's or his Sub-Contractor's works. Inspection may also be required during preparation and manufacture. A provisional sum is included in the schedule of prices for expenses by the Engineer and PIU for attendance at the Contractor’s or Manufacturer’s premises.

### Electrical Switchgear and M.C.C.’s

Works tests on electrical switchgear and motor control panels shall include complete functional testing of all components, insulation, phasing and high voltage testing according to international standards. Complete checking of mechanical and electrical interlocks and sequential operation of motor control equipment using simulated signals shall also be carried out. Primary and secondary injection current tests shall be carried out to prove the operation of circuit breakers, current transformers, relays and instrumentation.

### Inspection on Delivery and During Installation

All Plant shall be visually inspected before installation to ensure that no damage has occurred during transit or storage. Labeling etc. shall also be checked.

During installation, the Engineer will visually inspect all works to ensure:

- That it complies with the requirements of the Specification.

- That installation workmanship is acceptable and in compliance with the Manufacturer’s requirements.

## Tests on Completion

As the various parts of the plant are installed and tested by the Contractor under working conditions they shall be offered to the Engineer for initial inspection and testing in accordance with this Specification. However, the Tests on Completion shall not commence until the particular section of the installation is complete and ready for testing. Before successful test, the expenses for consumables shall be borne by the Contractor.

If any portion of the Works fails to pass the tests, further tests of the said portion shall be repeated within a reasonable time upon the same terms and conditions. All reasonable expense to which the Engineer/Employer’s Representative may be put by the repetition of the tests shall be deducted from the Contract Price.

The following tests generally shall be carried out:

- All plant shall be tested mechanically and electrically to prove that each item of plant or equipment functions as designed. Greasing and lubrication systems shall be tested for all plant.

- All electrical installations shall be tested, and the rotation direction and insulation resistance of all motors shall be checked.

- Calibration tests shall be carried out on all instrumentation.

- The capacity and electrical performance of all pumping installations shall be fully tested. In addition, all pipework, valves, penstocks etc. shall be pressure tested, to a head of not less than 1.5 times the designed working pressure.

- The process control systems shall be fully tested to demonstrate that the sequence of operation of the plant is correct, and that the plant generally performs in the manner and to the parameters specified. This shall encompass the SCADA system.

Tests on Completion shall be carried out on each unit of each process stage to verify that each unit complies with Employers Requirements in terms of throughput and water quality.

Successful tests on Completion shall be carried out on each unit or, if it is not possible to isolate a single unit, on the completed process stage, before it is included as part of the on-line water treatment plant.

### Damages for Failure to pass Tests on Completion

The contractor shall, at his expense, adequately rectify faults to the satisfaction of the Engineer.

## Test Instruments

The manufacturer shall satisfy the Engineer as to the accuracy of all the instruments used for the tests and if required shall produce recent calibration tests, or otherwise have them calibrated at his own expense by an independent authority.

## Control/Switchgear Panels

### Low Voltage Devices

Low voltage circuit breakers shall be delivered with CE-marking in accordance with low voltage directives.

Miniature circuit breakers shall be delivered with CE-marking in accordance with low voltage directives. Low- and moulded case air-break switches and fuse combination units shall be delivered with CEmarking in accordance with low voltage directives.

Low voltage contactors shall be delivered with CE-marking in accordance with low voltage directives.

All other electrical equipment shall be delivered with CE-marking in accordance with relevant directives. All low voltage switching devices of current rating 100 A or greater shall be subjected to measurement and recording of circuit resistance. The test shall comprise measurement, at the main terminals of each pole with the contacts fully closed, of D.C. voltage and current (at 100 A or greater). The values of resistance for any two similar examples from a particular manufacturer's range shall not differ by more than 20%.

### High Voltage Devices, if needed

High voltage circuit breakers shall be tested in accordance with BS EN 62271-100:2009+A1:2012. High voltage switches shall be tested in accordance with BS EN 62271-103:2011. High voltage contactors shall be tested in accordance with BS EN 62271-106:2011.

High voltage direct-on-line starters shall be tested in accordance with BS EN 62271-106:2011.

All high voltage switching devices of current rating 100 A or greater shall be subject to measurement, at the main terminals of each pole with the contacts fully closed, of D.C. voltage and current (at 100 A or greater).

The values of resistance for any two similar examples from a particular manufacturer's range, shall not differ by more than 20%.

### Switchboards and Motor Control Centers

Factory built assemblies of low voltage switchgear and control gear shall be tested in accordance with EN60204-1

If needed. High voltage metal enclosed switchgear and control gear shall be tested in accordance with BS EN 62271-200:2012.

Additionally, low voltage and high voltage switchgear and control gear assemblies shall be tested for the following:

Measurement of main circuit resistance: The resistance of each pole of each main circuit from the cable terminal to bushes (with all intervening switch contacts fully closed) shall be measured and recorded. A similar measurement and record shall be taken along the length of each busbar (with bus-section switch contacts fully closed). The tests shall comprise the measurement of D.C. voltage and current (at 100 A or greater) and calculation of resistance.

Interchangeability; All components of the same rating and construction, designated as drawout or plug-in shall be demonstrated as being interchangeable.

Protection and control circuits; For all forms of current transformer protection the following information shall be made available to the Engineer before the time of inspection:

- Current transformer magnetising curve.

- Recommended relay setting;

- Calculated primary operating current at this setting;

- Calculated through-fault stability values where applicable;

- Values of any stabilising and setting resistors employed in the systems;

As far as possible, based on the completeness of the circuits, in the final manufactured form within manufacturer's premises, the satisfactory operation of associated control and protection circuits shall be proved by the following tests:

To ensure the correct operation of all current operated protection relays and direct acting coils at the recommended setting by primary current injection.

To ensure the correct polarity between current and voltage elements of power relays, meters and instruments.

To ensure the correct operation of D.C. operated auxiliary protection relays, such as Buchholz protection relays at normal operating voltage by stimulated operation of associated remote relays.

To ensure the correct operation of control circuits at normal operating voltage by operation of local control switches and simulation of operation from remote control positions.

Note: Checking the operation of all protection relays and control circuits shall be carried out with all closing and tripping circuits energized at their normal rated voltage.

### Instrument and metering equipment

Indicating ammeters shall be checked for calibration at 0.25, 0.5 and full-scale deflection by primary current injection testing.

Indicating voltmeters shall be checked for normal voltage readings by secondary voltage application. Where possible, integrating kWh- and kVar meters shall be tested for correct operation. Tests shall be carried out to ensure that the meter is inoperative with voltage alone, with the secondaries of current transformers connected and the primary current interrupted.

All instruments shall be subject to the manufacturer's normal work tests and shall be certified.

Supervisory and control equipment;

In order that any control scheme can be tested in its entirety, the Contractor shall provide a test assembly comprising an adequate number of switches and lamps as a means of simulating external signals and loads.

## Transformers

If it is decided to supply transformers they shall be routine tested at the manufacturer's works in accordance with IEC 60076.

If the manufacturer can provide evidence covering impulse voltage withstand tests for transformers of similar type and design, Type Test certificates will be acceptable

## Cable Tests during Installation

During the period of site installation, the Engineer will carry out inspection of the works to ensure the standards of workmanship meet the Specification and are to his satisfaction. In the event of any part of the cabling installation failing to meet these requirements, the Contractor will be informed immediately and shall remedy the deficiency to the satisfaction of the Engineer.

The Contractor shall:

- Inform the Engineer prior to the testing of the cables and shall be responsible for liaising with any other contractor to whose equipment the cables may be terminated to ensure that all parties concerned are aware of the impending tests, to guarantees the safety of personnel and that the isolation of any equipment has been completed. Any special isolation or preparation required to be carried out before cable testing can be completed, will be carried out by the Contractor responsible for that equipment. All tests shall be carried out by the Contractor but shall be supervised by the Engineer.

- Provide D.C. test equipment and apply (after isolation) in the presence of the Engineer, the following D.C. test voltages on all cables between cores, cores and sheath and cores and armour.

### High voltage cables if needed

XLPESWA PVC 20,000/35,000 Volt grade cable between cores and between any core and screen/armour 76,000 Volt

XLPESWA PVC 5,800/10,000 Volt grade cable between cores and between any core and screen/armour 25,000 Volt

XLPESWA PVC 3,500/ 6,000 Volt grade cable between cores and between any core and screen/armour 15,000 Volt

### LV cables 600/1000 V

Polyvinyl chloride (PVC) or cross-linked polythene (XLPE) 600/1,000 Volt grade cable between cores and between core and armour 3,500 Volt

Demonstrate correct phasing out of cores in all cables throughout the works and test the insulation of all the cables, both between the cores and between the cores and earth, during installation with a "Megger" 500 Volt hand generator.

Conduct soil resistivity tests in the presence of the Engineer to obtain the most suitable location for the earth electrode system.

Demonstrate to the Engineer that the resistance of the earth electrodes to earth conductor continuity and earth installation is in accordance with the specified requirements.

Tests shall be performed from each major item of plant, by using an "Earth Megger" and auxiliary return conductor.

If any portion of the works fails to pass the tests, another test of the failed portion shall be repeated within a reasonable time upon the same terms and conditions.

Certificates of all testes carried out shall be provided giving full details and description of each test.

## Electrical Measuring Instruments and Meters

Tests to ensure accurate operation of all meters, voltmeters and kilowatt- and kiloVar hour meters shall be undertaken in accordance with relevant EN/IEC standards.

## Programmable Logical Controller (PLC)

The Contractor shall be responsible for testing all items of equipment comprised in the PLC system for correct operation.

## Test Period

After installation of the total system including submission of test reports, the Contractor shall report ready for the beginning of a test period of one month.

All units shall be activated and in operation. Furthermore, all Control Boards and switchboard as well as SCADA system with software shall be operational simultaneously for a minimum of 99% of the time in the test period. During the test period, a minimum of 95% of the system point shall be at any time operative.  In corporation with the Recipient, all test points shall be tested during the period.

In case the system is not operational according to the above, the test period shall be cancelled.  After correction of errors, a new test period shall be commenced.

The Contractor may ask for final commissioning after satisfactory execution of the test period.